## Sheet1
Action Closed by Name | Action Closed Date | Action Completed by Name | Action Completed Date | Action Taken Current Status | Audit Desc. | Audit End Date | Audit Number | Audit Start Date | Audit Status | Audit Status Code | Audit Type | CAPA Desc. | CAPA Number | CAPA Status | Last Change by Name | Last Changed Date | Observation Comment | Part Code | Part Details | Planning Plant | Plant Desc. | Recommendation | SBU | SBU Group | SBU Zone | Target Date | Root Cause Analysis | Risk Score | Risk Category | Severity Code | Frequency Code | Revised Target Date | Unique CAPA | State Code | Tags | Fire Safety | Electrical Safety | Permit To Work (PTW) | Housekeeping | Training & Awareness | PPE Compliance | Equipment Safety | SOP / Policy / Documentation | Emergency Preparedness | Signage & Marking | Year | FIscalYear | Pending >1yr Flag | Audit Type Corrected | UniqCAPA | Last Audited Date | Days Since Last Audit | DateDiff | Weeks | UNIQUE_IDENTIFIER | AUDIT_COUNT_OVER_WEEKS_OPEN | AUDIT_COUNT_OVER_WEEKS_CLOSED | Weeks_int | AUDIT_COUNT_OVER_WEEKS_CLOSED_VIS | ageing_date_diff | AGEING_DAYS | Audit Year | Pending >2yr Flag | CURR_WEEK | Risk | OpenRecomms | ClosedRecomms | TotalRecomms | TARG_WEEK | ACTL_WEEK | AuditYear2 | FixLocations | CumNotLocations | MnthNotLocations | DateDiff_Target_Date | DateDiff_Action_Closed_Date
[5 empty] | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121499 | Open |  |  |  | 3.16 | Earth pits / boundary / vegetation control checked | 1308 | SITARGANJ DEPOT | XX | SOD | Marketing | NUZ | 2026-03-31 |  | 1 |  | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121499 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121499 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121499 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-02-2000010854ACN-2026-02-4000121499 |  | AUD-2026-02-2000010854ACN-2026-02-4000121499 | 21 |  | 26 | 80 | 0 | 0 | 31
|  |  |  | Route correction by 28.2.26 | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122152 | Open | VIPIN TOTLA | 2026-02-25 | Individual performace are reviewed and encouraged for their best performance area. Training requirements discussed | 1.2 | Performance review conducted | 1797 | GULBARGA NEW IRD | Route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-03-15 |  | 4 |  | S2 | F2 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122152 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122152 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122152 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | LOW | AUD-2026-02-2000010815ACN-2026-02-4000122152 |  | AUD-2026-02-2000010815ACN-2026-02-4000122152 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Coordinate with CPO | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122153 | Open | VIPIN TOTLA | 2026-02-25 | TT induction.Railway payment 53 lakhs pending. (total 93 l, paid 40 L, 53 lakhs more needed) | 1.3 | Pending issues reviewed | 1797 | GULBARGA NEW IRD | Coordinate with CPO | SOD | Marketing | SWZ | 2026-03-15 |  | 8 |  | S2 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122153 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122153 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122153 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122153 |  | AUD-2026-02-2000010815ACN-2026-02-4000122153 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Funds for railway payment, TT allotment from CPO. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122154 | Open | VIPIN TOTLA | 2026-02-25 | Railway payment to IOC pending, TT allotment of 35 TTs from CPO. | 1.5 | HQO / Zonal support required identified | 1797 | GULBARGA NEW IRD | Funds for railway payment, TT allotment from CPO. | SOD | Marketing | SWZ | 2026-03-15 |  | 8 |  | S2 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122154 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122154 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122154 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122154 |  | AUD-2026-02-2000010815ACN-2026-02-4000122154 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | DCT LOIs to be send for cancellation bt 20.2.26. Accident spot review and route correction by 28.2.26 | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122155 | Open | VIPIN TOTLA | 2026-02-25 | Induction of DCT LOIs pending, Route correction pending to be completed by 28.02.26, Accident spots review for relevance | 1.6 | Expectations clearly communicated to officers | 1797 | GULBARGA NEW IRD | DCT LOIs to be send for cancellation bt 20.2.26. Accident spot review and route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-03-15 |  | 6 |  | S3 | F2 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122155 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122155 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122155 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122155 |  | AUD-2026-02-2000010815ACN-2026-02-4000122155 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Records to be submitted by 28.2.26 to SWZ | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122156 | Open | VIPIN TOTLA | 2026-02-25 | Discussed trainings to be imparted to new officers | 1.8 | Improvement plans discussed | 1797 | GULBARGA NEW IRD | Records to be submitted by 28.2.26 to SWZ | SOD | Marketing | SWZ | 2026-03-15 |  | 4 |  | S1 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122156 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122156 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122156 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | LOW | AUD-2026-02-2000010815ACN-2026-02-4000122156 |  | AUD-2026-02-2000010815ACN-2026-02-4000122156 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Not done in Q3, Shall comply in Q4 | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122157 | Open | VIPIN TOTLA | 2026-02-25 | Surprise Fire drill done 21/Aug, 2025 | 2.1 | Fire drill conducted in last 6 months (surprise) | 1797 | GULBARGA NEW IRD | Not done in Q3, Shall comply in Q4 | SOD | Marketing | SWZ | 2026-03-15 |  | 8 |  | S2 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122157 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122157 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122157 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122157 |  | AUD-2026-02-2000010815ACN-2026-02-4000122157 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | To be done in all ERDMP scenarios, Not done in TT gantry in 25-26. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122158 | Open | VIPIN TOTLA | 2026-02-25 | Single contingency location | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1797 | GULBARGA NEW IRD | To be done in all ERDMP scenarios, Not done in TT gantry in 25-26. | SOD | Marketing | SWZ | 2026-03-15 |  | 8 |  | S2 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122158 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122158 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122158 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122158 |  | AUD-2026-02-2000010815ACN-2026-02-4000122158 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | 2 Non-working cameras are to be corrected. Response from SIS very poor | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122159 | Open | VIPIN TOTLA | 2026-02-25 | 46 out of 48 CCTV Cameras are working. | 2.6 | CCTV functioning checked | 1797 | GULBARGA NEW IRD | 2 Non-working cameras are to be corrected. Response from SIS very poor | SOD | Marketing | SWZ | 2026-03-15 |  | 12 |  | S3 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122159 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122159 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122159 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122159 |  | AUD-2026-02-2000010815ACN-2026-02-4000122159 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Balance 8 Cameras are to be made active. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122160 | Open | VIPIN TOTLA | 2026-02-25 | 32 Cameras out of 40 are active under VA, Balance Cameras are to be made active. | 2.7 | VA alerts checked / analysed | 1797 | GULBARGA NEW IRD | Balance 8 Cameras are to be made active. | SOD | Marketing | SWZ | 2026-03-15 |  | 12 |  | S3 | F4 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122160 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122160 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122160 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122160 |  | AUD-2026-02-2000010815ACN-2026-02-4000122160 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | 1 kl AR AFFF is needed in case of UG tanks, location to access AR AFFF requirement | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122161 | Open | VIPIN TOTLA | 2026-02-25 | AFFF - 11 KL, AR-AFFF – 3.7 KL are available. | 2.9 | Foam inventory verified | 1797 | GULBARGA NEW IRD | 1 kl AR AFFF is needed in case of UG tanks, location to access AR AFFF requirement | SOD | Marketing | SWZ | 2026-03-15 |  | 9 |  | S3 | F3 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122161 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122161 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122161 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122161 |  | AUD-2026-02-2000010815ACN-2026-02-4000122161 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | PO for PLC for HVLR panel placed on 9/2/26 | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122162 | Open | VIPIN TOTLA | 2026-02-25 | HVLR No.-3 for HSD dyke is not working due to Panel Issue. ,The same needs to be corrected. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1797 | GULBARGA NEW IRD | PO for PLC for HVLR panel placed on 9/2/26 | SOD | Marketing | SWZ | 2026-03-15 |  | 4 |  | S2 | F2 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122162 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122162 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122162 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | LOW | AUD-2026-02-2000010815ACN-2026-02-4000122162 |  | AUD-2026-02-2000010815ACN-2026-02-4000122162 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Route correction by 28.2.26 | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122163 | Open | VIPIN TOTLA | 2026-02-25 | Carried out | 3.3 | VTS deviations reviewed | 1797 | GULBARGA NEW IRD | Route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-03-15 |  | 6 |  | S3 | F2 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122163 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122163 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122163 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122163 |  | AUD-2026-02-2000010815ACN-2026-02-4000122163 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Improvements near primary and secondary roads, UG tank farm surounding. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122164 | Open | VIPIN TOTLA | 2026-02-25 | House keeping is good. | 3.15 | Housekeeping & PPE usage checked | 1797 | GULBARGA NEW IRD | Improvements near primary and secondary roads, UG tank farm surounding. | SOD | Marketing | SWZ | 2026-03-15 |  | 1 |  | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122164 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122164 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122164 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | LOW | AUD-2026-02-2000010815ACN-2026-02-4000122164 |  | AUD-2026-02-2000010815ACN-2026-02-4000122164 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | Vegetation is removed, still requires dedicated cleaning. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122165 | Open | VIPIN TOTLA | 2026-02-25 | Good, still improvemnts required. | 3.16 | Earth pits / boundary / vegetation control checked | 1797 | GULBARGA NEW IRD | Vegetation is removed, still requires dedicated cleaning. | SOD | Marketing | SWZ | 2026-03-15 |  | 5 |  | S1 | F5 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122165 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122165 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122165 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | LOW | AUD-2026-02-2000010815ACN-2026-02-4000122165 |  | AUD-2026-02-2000010815ACN-2026-02-4000122165 | 21 |  | 25 | 80 | 5 | 5 | 28
|  |  |  | LPS point of tank TK4 to be attended by checking . New system for Al dome to be devised | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122166 | Open | VIPIN TOTLA | 2026-02-25 | OISD - Zero, MDSA 24-25 7 /33 pending, 25-26 8/59 pending, SSA 11/67 pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1797 | GULBARGA NEW IRD | LPS point of tank TK4 to be attended by checking . New system for Al dome to be devised | SOD | Marketing | SWZ | 2026-03-20 |  | 6 |  | S3 | F2 | 2026-03-20 | AUD-2026-02-2000010815ACN-2026-02-4000122166 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122166 | 2026-08-19 18:00 | 61.0038 | 200 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122166 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122166 |  | AUD-2026-02-2000010815ACN-2026-02-4000122166 | 21 |  | 25 | 80 | 5 | 5 | 29
|  |  |  | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122167 | Open | VIPIN TOTLA | 2026-02-25 | As on date location has completed and verified the Supply and Installation of FMP JB and Gulbarga_S&I of Lights. Bottom loading project is under execution | 4.3 | Project progress reviewed | 1797 | GULBARGA NEW IRD | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | SOD | Marketing | SWZ | 2026-03-30 |  | 6 |  | S3 | F2 | 2026-03-30 | AUD-2026-02-2000010815ACN-2026-02-4000122167 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122167 | 2026-08-19 18:00 | 61.0038 | 210 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122167 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122167 |  | AUD-2026-02-2000010815ACN-2026-02-4000122167 | 21 |  | 25 | 80 | 5 | 5 | 30
|  |  |  | Close monitoring and compliance is required. | SENIOR MANAGEMENT INSPECTION - GULBARGA | 2025-02-18 21:20 | AUD-2026-02-2000010815 | 2025-02-18 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122168 | Open | VIPIN TOTLA | 2026-02-25 | 9 numbers of RFDs has been sent for Accution on 09/02/2026. One RFD penfing for approval. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1797 | GULBARGA NEW IRD | Close monitoring and compliance is required. | SOD | Marketing | SWZ | 2026-03-15 |  | 6 |  | S3 | F2 | 2026-03-15 | AUD-2026-02-2000010815ACN-2026-02-4000122168 | KA | [11 empty] | 2025 | 24-25 | 1 | Senior Management Inspection | AUD-2026-02-2000010815ACN-2026-02-4000122168 | 2026-08-19 18:00 | 61.0038 | 195 | >20 | AUD-2026-02-2000010815 - ACN-2026-02-4000122168 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2024-25 | 0 | 21 | MEDIUM | AUD-2026-02-2000010815ACN-2026-02-4000122168 |  | AUD-2026-02-2000010815ACN-2026-02-4000122168 | 21 |  | 25 | 80 | 5 | 5 | 28
[5 empty] | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122513 | Open |  |  | A Bomb Threat drill was conducted on 08/01/2026 in the presence of the Bomb Squad, Fire Brigade, local police, District Medical Team, and Mutual Aid Partners. Observations: 1 Quick identification of suspicious item 2 Effective coordination between Depot personnel, mutual aid partners and district administration 3 Evacuation procedure was followed as per emergency plan ERDMP document was also checked for the emergency scenarios considered for the location and it was found that a scenario of tilting of floating roof was also considered in it whereas the location is having only UG product tanks. Further, all the relevant emergency scenarios have not been so far covered in mock drills conducted in this Financial Year. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1308 | SITARGANJ DEPOT | 1 Need for Regular training to prevent panic is to be done 2 Before arrival of bomb Squad premises should be evacuated by the depot personnels 3. ERDMP to be modified with correct information. 4. All the relevant emergency scenarious covered in the ERDMP document to be covered during this FY. | SOD | Marketing | NUZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011209ACN-2026-03-4000122513 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122513 | 2026-08-26 17:00 | 54.0455 | 302 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122513 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011209ACN-2026-03-4000122513 |  | AUD-2026-03-2000011209ACN-2026-03-4000122513 | 21 |  | 26 | 80 | 0 | 0 | 44
[5 empty] | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122531 | Open |  |  | 1. OISD Status: N/A 2. PCSA Status: Audit was conducted on 3rd Jan 2023, total observations were 43. All observations were complied in time bound manner. 3. Comphrensive/MDSA Status: Audit was conducted from 7th Oct -10 oct 2025, total observations were 90 out of which 14 observations are pending. 4. SSA Status: Audit was conducted from 3rd sep - 10 th Sep 2025, Total observations were 53,out of which 2 observations are pending. 5. T4S Audit Status: Audit was conducted from 4th - 6th Aug 2023, Total observations were17 and all observations were complied in time bound manner. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1308 | SITARGANJ DEPOT | Audit observations must be complied with in a time-bound manner, and their closure should be supported with adequate documentation and proof of compliance. | SOD | Marketing | NUZ | 2026-07-31 |  | 2 |  | S2 | F1 | 2026-07-31 | AUD-2026-03-2000011209ACN-2026-03-4000122531 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122531 | 2026-08-26 17:00 | 54.0455 | 333 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122531 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011209ACN-2026-03-4000122531 |  | AUD-2026-03-2000011209ACN-2026-03-4000122531 | 21 |  | 26 | 80 | 0 | 0 | 48
[5 empty] | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122764 | Open |  |  | All points of OISD audit are complied, two points of SSA are to be complied,MDSA 2025-26: 18 out of total 32 points pending) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1775 | BENGALURU TERMINAL | To be complied by 31/3/26 | SOD | Marketing | SWZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 6 | PROCESS SAFETY | S2 | F3 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122764 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122764 | 2026-09-24 17:00 | 25.0455 | 211 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122764 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010965ACN-2026-03-4000122764 |  | AUD-2026-03-2000010965ACN-2026-03-4000122764 | 21 |  | 26 | 80 | 0 | 0 | 31
|  |  |  | The agreement copies of 2 DCT are pending rest all has been collected, dealer and transporter meeting are conducted | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122283 | Open | JOSVIN SUNNY | 2026-05-23 | Replacement of One officer required from April. Discussed on Transport Contract and Present TT availablity. NOVEX ITDG Module SOP was discussed in detail. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1892 | KOZHIKODE DEPOT | Advised location to procure agreement copies of all transporters and DCT's and confirm that all SD are accounted properly. Conduct trainings of DCT (Sales area vice ) & Transporters. | SOD | Marketing | CZR | 2026-03-31 |  | 1 |  | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122283 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122283 | 2026-09-17 16:00 | 32.0872 | 211 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122283 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-02-2000010911ACN-2026-03-4000122283 |  | AUD-2026-02-2000010911ACN-2026-03-4000122283 | 21 |  | 26 | 80 | 2 | -4 | 31
|  |  |  | Compliance activities are in progress | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122851 | Open | G RAMADOSS | 2026-03-03 | SSA - 6 pending, MDSA 25-26 - 22 Pending, MDSA 24-25 - 6 pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1871 | MADURAI DEPOT | All pending 6-SSA, 6-MDSA 24-25 and 22-MDSA 25-26 to be complied as per timelines | SOD | Marketing | SZ | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-03-2000010767ACN-2026-03-4000122851 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122851 | 2026-07-03 | 108.7538 | 302 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122851 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010767ACN-2026-03-4000122851 |  | AUD-2026-03-2000010767ACN-2026-03-4000122851 | 21 |  | 26 | 80 | 2 | 2 | 44
|  |  |  | Identified the land(1.2 acres) behind the existing TT parking. Taken up with land owners for submission of documents for preparation of proposal. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-03-4000122852 | Open | G RAMADOSS | 2026-03-03 | Full field round completed. Infrastructure augmentation data communicated to HQO. In regards to additional parking land, met the land owners along with LIC. Land owners shall provide the data in short time, post same proposal shall be sent. | 4 |  | 1871 | MADURAI DEPOT | Additional TT parking including land purchase & other development need to be done | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010767ACN-2026-03-4000122852 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122852 | 2026-07-03 | 108.7538 | 394 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122852 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010767ACN-2026-03-4000122852 |  | AUD-2026-03-2000010767ACN-2026-03-4000122852 | 21 |  | 26 | 80 | 2 | 2 | 57
|  |  |  | construction of Additional bay and tankages will be taken up after board approval for shifting of tirunelveli markets. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122853 | Open | G RAMADOSS | 2026-03-03 | Full field round completed. Infrastructure augmentation data communicated to HQO. In regards to additional parking land, met the land owners along with LIC. Land owners shall provide the data in short time, post same proposal shall be sent. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1871 | MADURAI DEPOT | Additional bay and tankages due to shifting of tirunelveli. | SOD | Marketing | SZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-03-2000010767ACN-2026-03-4000122853 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122853 | 2026-07-03 | 108.7538 | 485 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122853 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010767ACN-2026-03-4000122853 |  | AUD-2026-03-2000010767ACN-2026-03-4000122853 | 21 |  | 26 | 80 | 2 | 2 | 70
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | The ethanol Sample was just taken from the Ethanol TT which was waiting for decantation as per IQCM guidelines, further The contract workman and officers have been counselled to be proactive and conduct job as per IQCM norms | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122314 | Closed | SHIVESH TRIPATHI | 2026-03-05 | One untagged ethanol sample found to be kept in TLFPH. | 6.12 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122314 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122314 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122314 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122314 | AUD-2026-02-2000010710ACN-2026-02-4000122314 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Work was being carried out by the contractor for the gate installation job by Engineering and Projects team, A show cause has been issued to the contractor and the indisciplined workers have been barred for two weeks from premises, furhter the importance of Work permit system is being disseminated via tool box talks and other meetings | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122305 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Hot work was found be going on at TT parking area, without work permit and welder found in slippers and without any PPEs. | 6.3 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122305 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122305 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122305 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122305 | AUD-2026-02-2000010710ACN-2026-02-4000122305 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Planning officers have been advised to write Name/Initials on the sample tag furhter, Specimen signature document of all authorisedofficers have been taken and pasted on Security cabin and notice board for display | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122306 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Name of officers not mentioned on many sample tags. | 6.4 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122306 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122306 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122306 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122306 | AUD-2026-02-2000010710ACN-2026-02-4000122306 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Hose boxes and DHs have been provided as per OISD norms, the subject DH was installed for coverage of emergency scenario just outside the exit gate for TTs further, area was cleared of debries to ensure that seamless movement of hose pipe and efficient utilisation of DH | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122308 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Location to review positioning of hose boxes and easiness of utilisation of DH post in TT parking area. One was found blocked by fencing. | 6.6 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122308 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122308 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122308 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122308 | AUD-2026-02-2000010710ACN-2026-02-4000122308 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Testing dates were earlier mentioned on the hose boxes of the hoses, Now we have started mentioning the date as per the advise on the hose pipes itself | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122309 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Hose pipe deployed in TT parking were found without last testing date written over it. | 6.7 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122309 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122309 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122309 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122309 | AUD-2026-02-2000010710ACN-2026-02-4000122309 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Hoses in Hose boxes installed in TT parking area are kept under seal arrangement to ensure effectiveness and availability in time of need, The keys are kept at Securiy cabin, now proper tagging of keys have been insured for timely and effective response | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122310 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Key for opening hose box is not available for hoses in TT parking area. | 6.8 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | HARSH WORKING CONDITIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122310 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122310 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122310 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122310 | AUD-2026-02-2000010710ACN-2026-02-4000122310 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
RAHA ROY SUBRAJYOTI | 2026-03-05 | SHIVESH TRIPATHI | 2026-03-05 | Licenses were already up to the date, in a few place in display board the dates were schduled to be updated and have now been updated | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122311 | Closed | SHIVESH TRIPATHI | 2026-03-05 | Various statutory display at main gate are required to be updated in term of validity date. | 6.9 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122311 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122311 | 2026-09-02 17:30 | 47.0247 | 185 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122311 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122311 | AUD-2026-02-2000010710ACN-2026-02-4000122311 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 27
|  |  |  | followup being done with VA vendor | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123404 | Open | GAKHAR NAVEEN | 2026-08-11 | yes | 2.7 | VA alerts checked / analysed | 1588 | VASHI WHITE OIL TERMINAL | FEW ALERTS WRONG GETTING RECEIVED | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123404 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123404 | 2026-10-14 | 5.7538 | 241 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123404 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011165ACN-2026-03-4000123404 |  | AUD-2026-03-2000011165ACN-2026-03-4000123404 | 21 |  | 26 | 80 | 15 | 11 | 35
|  |  |  | ACESS control being correted from visitor to via vendor a request(under process) | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123405 | Open | GAKHAR NAVEEN | 2026-08-11 | yes | 2.8 | Access control systems checked | 1588 | VASHI WHITE OIL TERMINAL | ACESS control being correted from visitor to via vendor a request | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123405 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123405 | 2026-10-14 | 5.7538 | 241 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123405 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011165ACN-2026-03-4000123405 |  | AUD-2026-03-2000011165ACN-2026-03-4000123405 | 21 |  | 26 | 80 | 15 | 11 | 35
|  |  |  | Email Sent to HQO along with Digital Inititaive dept | ZONAL VISIT REPORT 17.02.2026 VASHI BOT | 2026-02-17 | AUD-2026-03-2000011166 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123409 | Open | SUKHWANT SINGH KAHLON | 2026-03-05 | Location is not having VA. Advised to follow up with HQO for installating VA at the locaiton | 2.7 | VA alerts checked / analysed | 3562 | VASHI BO TML | Location to follow up for installation of VA at the location . | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-03-2000011166ACN-2026-03-4000123409 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011166ACN-2026-03-4000123409 | 2026-09-15 | 34.7538 | 302 | >20 | AUD-2026-03-2000011166 - ACN-2026-03-4000123409 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011166ACN-2026-03-4000123409 |  | AUD-2026-03-2000011166ACN-2026-03-4000123409 | 21 |  | 26 | 80 | 9 | 9 | 44
|  |  |  | PO placed on vendor M/s Times Project. Job shall commence in the first week of March | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123414 | Open | SUKHWANT SINGH KAHLON | 2026-03-06 | Interacted with officers handling tank revamp project and deliberated on the timelines for completing the actvities on urgent basis | 1.1 | Interaction with all officers (1–1.5 hrs) | 1584 | LONI TERMINAL | Project jobs to be carried out with utmost safety and completed in a time bound manner | SOD | Marketing | WZ | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-03-2000011168ACN-2026-03-4000123414 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123414 | 2026-10-15 | 4.7538 | 394 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123414 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011168ACN-2026-03-4000123414 |  | AUD-2026-03-2000011168ACN-2026-03-4000123414 | 21 |  | 26 | 80 | 18 | 18 | 57
|  |  |  | Requires design change, Works are in progress. | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123419 | Open | JERRY JOSEPH | 2026-05-18 | VRU pipe was not placed in the wagon during loading due to design flaw. Location advised to rectify the same and start VRU at siding on priority | 6.2 | At Railwagon loading gantry | 1584 | LONI TERMINAL | XX | SOD | Marketing | WZ | 2026-06-30 |  | 3 |  | S1 | F3 | 2026-06-30 | AUD-2026-03-2000011168ACN-2026-03-4000123419 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123419 | 2026-10-15 | 4.7538 | 302 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123419 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011168ACN-2026-03-4000123419 |  | AUD-2026-03-2000011168ACN-2026-03-4000123419 | 21 |  | 26 | 80 | 18 | 18 | 44
|  |  |  | Discussed with WZ as advised payment to be processed. | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122768 | Open | SUKHWANT SINGH KAHLON | 2026-03-06 | YES | 1.3 | Pending issues reviewed | 1551 | VASCO BLACK OIL TERMINAL | Pending payments to IOC on way leave charge/ Common Jetty line maintenance Charges | SOD | Marketing | WZ | 2026-07-31 |  | 3 |  | S1 | F3 | 2026-07-31 | AUD-2026-03-2000010967ACN-2026-03-4000122768 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122768 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122768 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122768 |  | AUD-2026-03-2000010967ACN-2026-03-4000122768 | 21 |  | 26 | 80 | 31 | 31 | 48
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122769 | Open |  |  | YES | 2.1 | Fire drill conducted in last 6 months (surprise) | 1551 | VASCO BLACK OIL TERMINAL | To be conducted level-2 drill | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010967ACN-2026-03-4000122769 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122769 | 2026-09-04 | 45.7538 | 302 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122769 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122769 |  | AUD-2026-03-2000010967ACN-2026-03-4000122769 | 21 |  | 26 | 80 | 31 | 31 | 44
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122770 | Open |  |  | YES | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1551 | VASCO BLACK OIL TERMINAL | Few Lights required to be replaced by LED lights | SOD | Marketing | WZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010967ACN-2026-03-4000122770 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122770 | 2026-09-04 | 45.7538 | 241 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122770 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122770 |  | AUD-2026-03-2000010967ACN-2026-03-4000122770 | 21 |  | 26 | 80 | 31 | 31 | 35
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122771 | Open |  |  | YES | 2.5 | Emergency response preparedness reviewed | 1551 | VASCO BLACK OIL TERMINAL | All three Fire enginers are operating (FE3 smoke leakge from axhaust manifold observed) | SOD | Marketing | WZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010967ACN-2026-03-4000122771 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122771 | 2026-09-04 | 45.7538 | 241 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122771 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122771 |  | AUD-2026-03-2000010967ACN-2026-03-4000122771 | 21 |  | 26 | 80 | 31 | 31 | 35
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122772 | Open |  |  | NA | 2.8 | Access control systems checked | 1551 | VASCO BLACK OIL TERMINAL | one security guard at gate for excess control DFMD to be made working | SOD | Marketing | WZ | 2026-05-31 |  | 1 |  | S1 | F1 | 2026-05-31 | AUD-2026-03-2000010967ACN-2026-03-4000122772 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122772 | 2026-09-04 | 45.7538 | 272 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122772 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122772 |  | AUD-2026-03-2000010967ACN-2026-03-4000122772 | 21 |  | 26 | 80 | 31 | 31 | 39
|  |  |  | Contractor is lined up to carry out the primer coating of both the tanks roof. | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122773 | Open | SUKHWANT SINGH KAHLON | 2026-03-06 | YES | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1551 | VASCO BLACK OIL TERMINAL | TK5,TK8 & PH/TT gantry/FP/MCC inspected.Advised locn to apply TK5&TK8 roof with applicable primer coat . | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010967ACN-2026-03-4000122773 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122773 | 2026-09-04 | 45.7538 | 302 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122773 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122773 |  | AUD-2026-03-2000010967ACN-2026-03-4000122773 | 21 |  | 26 | 80 | 31 | 31 | 44
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122774 | Open |  |  | YES | 4.3 | Project progress reviewed | 1551 | VASCO BLACK OIL TERMINAL | Compound wall construction to be completed by 20.03.2026 | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010967ACN-2026-03-4000122774 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122774 | 2026-09-04 | 45.7538 | 302 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122774 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122774 |  | AUD-2026-03-2000010967ACN-2026-03-4000122774 | 21 |  | 26 | 80 | 31 | 31 | 44
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122775 | Open |  |  | YES | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1551 | VASCO BLACK OIL TERMINAL | 40% Scrap is still lying. Advised to make scrap free by 30.04.2026 | SOD | Marketing | WZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010967ACN-2026-03-4000122775 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122775 | 2026-09-04 | 45.7538 | 241 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122775 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122775 |  | AUD-2026-03-2000010967ACN-2026-03-4000122775 | 21 |  | 26 | 80 | 31 | 31 | 35
[5 empty] | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122776 | Open |  |  | YES | 6.1 | Fire Engine cooling water circulation system | 1551 | VASCO BLACK OIL TERMINAL | Suggested slight modification and to install Pressure gauge in all 3 engine cooling water line. Cooling water outlet to take it to Water storage tanks. | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010967ACN-2026-03-4000122776 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122776 | 2026-09-04 | 45.7538 | 302 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122776 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122776 |  | AUD-2026-03-2000010967ACN-2026-03-4000122776 | 21 |  | 26 | 80 | 31 | 31 | 44
|  |  |  | Location has lined up for the work / would be completed before March 31st | ZONAL VISIT REPORT 28.02&02.03.26VACOBOT | 2026-03-03 | AUD-2026-03-2000010967 | 2026-02-28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122777 | Open | SUKHWANT SINGH KAHLON | 2026-03-06 | YES | 6.3 | Transformer Yard Inspection | 1551 | VASCO BLACK OIL TERMINAL | Suggested location to do painting of Transformer and Structure. | SOD | Marketing | WZ | 2027-04-30 |  | 1 |  | S1 | F1 | 2027-04-30 | AUD-2026-03-2000010967ACN-2026-03-4000122777 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010967ACN-2026-03-4000122777 | 2026-09-04 | 45.7538 | 606 | >20 | AUD-2026-03-2000010967 - ACN-2026-03-4000122777 | 532 | 8294 | 21 | 8294 | -192 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010967ACN-2026-03-4000122777 |  | AUD-2026-03-2000010967ACN-2026-03-4000122777 | 21 |  | 26 | 80 | 31 | 31 | 87
|  |  |  | Lux levels TK 3B manifold found to be less due to malfunctionng of the lights. Replacement of faulty lights is taken up. The lux level in the secondary road near slop tank found to be less due to tree shades. Cutting of tree branches carried out. The illuminationis found OK. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123582 | Open | LOMESH KUMAR PATRE | 2026-08-09 | Lux levels checked . TT Gantry - 250 , Product Pump House 270, Fire Pump House - 128, TK 3B manifold - 32 , Secondary road near slop tank - 5 , Admin - 280 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1979 | VIJAYAWADA TERMINAL | Lux levels to be improved to meet OISD STD 244 requirements | SOD | Marketing | SCR | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011121ACN-2026-03-4000123582 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123582 | 2026-08-21 16:00 | 59.0872 | 272 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123582 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011121ACN-2026-03-4000123582 |  | AUD-2026-03-2000011121ACN-2026-03-4000123582 | 21 |  | 26 | 80 | 12 | 12 | 39
|  |  |  | 2 cameras sent for repair and expected to put back into the operation by 10.06.2026. CCTV cameras are realigned for Bay No 6, nearemergency exit gate, railway wagon siding, scrap yard and TT locking shed. Camera angle for Cable cellar area has been readjusted. camera of Lube godown area was made functional. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123584 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | CCTV functioning checked . 48 out 48 cameras are active in VA. Out of the total 65 CCTV cameras , two cameras sent for repair. CCTVcameras to be cleaned / realigned at Bay no 6 , near emergency exit gate , Railway wagon siding , scrap yard , TT locking shed , TK1B PTZ camera showing blank , cable cellar camera angle to be adjusted, Lube godown area camera not working. | 2.6 | CCTV functioning checked | 1979 | VIJAYAWADA TERMINAL | CCTV cameras to be realigned / cleaned . | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011121ACN-2026-03-4000123584 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123584 | 2026-08-21 16:00 | 59.0872 | 211 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123584 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011121ACN-2026-03-4000123584 |  | AUD-2026-03-2000011121ACN-2026-03-4000123584 | 21 |  | 26 | 80 | 12 | 12 | 31
|  |  |  | Noted. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123588 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Not available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1979 | VIJAYAWADA TERMINAL | Security Guards with HVD available. HZA endorsement to be taken | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011121ACN-2026-03-4000123588 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123588 | 2026-08-21 16:00 | 59.0872 | 241 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123588 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011121ACN-2026-03-4000123588 |  | AUD-2026-03-2000011121ACN-2026-03-4000123588 | 21 |  | 26 | 80 | 12 | 12 | 35
|  |  |  | Noted. Pending points are perrtains to the tank repair works. Rest all the points are closed. The repairs requires the budget are taken up on priority . | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123592 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Pending MDSA and SSA points to be complied as per given target dates | 3.18 | OISD/MDSA/SSA compliance reviewed | 1979 | VIJAYAWADA TERMINAL | Pending SSA 19 points and Pending MDSA points to be completed as per given target dates | SOD | Marketing | SCR | 2027-05-31 |  | 8 |  | S2 | F4 | 2027-05-31 | AUD-2026-03-2000011121ACN-2026-03-4000123592 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123592 | 2026-08-21 16:00 | 59.0872 | 637 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123592 | 532 | 8294 | 21 | 8294 | -223 | 10 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011121ACN-2026-03-4000123592 |  | AUD-2026-03-2000011121ACN-2026-03-4000123592 | 21 |  | 26 | 80 | 12 | 12 | 91
|  |  |  | The requirements of SOP display boards have been identified, PO placed. The replacement of SOPs is expected to be completed by 30.06.2026. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123597 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | SOP boards faded / torn to be replaced. | 6.1 |  | 1979 | VIJAYAWADA TERMINAL | PO placed , SOP boards to be replaced at the earliest | SOD | Marketing | SCR | 2026-05-31 | HARSH WORKING CONDITIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011121ACN-2026-03-4000123597 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123597 | 2026-08-21 16:00 | 59.0872 | 272 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123597 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011121ACN-2026-03-4000123597 |  | AUD-2026-03-2000011121ACN-2026-03-4000123597 | 21 |  | 26 | 80 | 12 | 12 | 39
|  |  |  | The CBACS provision for access control between Pipelines and Terminal will be taken up under NPCB 2026-27. Meanwhile, frsiking of personal is being carried out by Pipeline team. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123603 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Gate near Pipeline area separating licenced / delicenced area access control to be provided. | 6.9 |  | 1979 | VIJAYAWADA TERMINAL | Gates available for segragation. Controlling shall be maintained | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2027-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123603 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123603 | 2026-08-21 16:00 | 59.0872 | 211 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123603 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011121ACN-2026-03-4000123603 |  | AUD-2026-03-2000011121ACN-2026-03-4000123603 | 21 |  | 26 | 80 | 12 | 12 | 31
|  |  |  | approx 1500 SQM of checquered plates are rusted. The replacement of these sheets will be taken up on priority. Budget request is being made for the same. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123604 | Open | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Wagon Gantry rusted sheets to be rectified. Heavy leak in Tank wagon sprinkler line section valve 8. | 6.10 |  | 1979 | VIJAYAWADA TERMINAL | To be rectified. | SOD | Marketing | SCR | 2026-03-07 | HARSH WORKING CONDITIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2027-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123604 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123604 | 2026-08-21 16:00 | 59.0872 | 187 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123604 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011121ACN-2026-03-4000123604 |  | AUD-2026-03-2000011121ACN-2026-03-4000123604 | 21 |  | 26 | 80 | 12 | 12 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | Direction board has been provided on Boundary wall near entrace of HVLR Panel pathway with arrow mark about position of Panel near Meter Room. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122654 | Closed | ARYA VIPIN KUMAR | 2026-03-07 | 1. HVLR no 4 operated by Ms. Neha & Preeti. Both officers operated satisfactory. Direction board to be provided for HVLR Panel nearMeter Room. 2. MEFG operated by contract workmen. Operated satisfactory. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122654 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122654 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122654 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122654 | AUD-2026-03-2000011009ACN-2026-03-4000122654 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | Awareness has been reinforced through gate meetings and monthly training sessions. During these sessions, the TT crews were specifically briefed on the instances when the panic button should be pressed and also shown the exact location of the panic button inside the TT cabin to ensure proper understanding and prompt use during emergencies. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122655 | Closed | DAS DARSHAN | 2026-03-06 | 2. Roadside emergency procedure awareness check carried out with TT crew of UP44BT3622 & UP32LN3535. TT crew was found aware of emergency procedure however not aware instances when Panic button to be presses given in TT cabin. | 2.15 | TT crew roadside emergency procedures checked | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122655 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122655 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122655 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122655 | AUD-2026-03-2000011009ACN-2026-03-4000122655 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | colour-blindness book provided in Medical Room | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122656 | Closed | DAS DARSHAN | 2026-03-06 | Facility not available | 2.16 | Eyesight / colour-blindness awareness checked | 1292 | LUCKNOW DEPOT | facility shall be developed. | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122656 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122656 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122656 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122656 | AUD-2026-03-2000011009ACN-2026-03-4000122656 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | Whenever an alert is closed, necessary corrective actions are taken such as blocking of the TT or restricting the concerned worker from work for a few days as a disciplinary measure by issuing a letter to the contractor. All such actions are communicated and recorded through email correspondence with the concerned parties. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122651 | Closed | DAS DARSHAN | 2026-03-06 | 3. VA alerts are being closed by location in time. 3.1 Review of alert Wheel choke noncompliance (TT Unloading) TAS_1292_SOP040_020126_000022 dated 02.01.2026. Alert closed with comment TT crew advised to adhere to TT loading SOP. Supporting document in line with alert closure not available with location. 3.2 Review of alert Non-compliance of Fire Extinguisher (TT Unloading) TAS_1292_SOP033_020126_000030 dated 02.01.2026. Alert closed with comment TT crew advised to adhere to TT loading SOP. Supporting document in line with alert closure not available with location. | 2.7 | VA alerts checked / analysed | 1292 | LUCKNOW DEPOT | Location to maintain supporting document related to SOP deviation in VA alerts. | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122651 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122651 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122651 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122651 | AUD-2026-03-2000011009ACN-2026-03-4000122651 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | In gate turnstile is repaired and is working properly. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122652 | Closed | DAS DARSHAN | 2026-03-06 | Access control system: In gate turnstile not working. | 2.8 | Access control systems checked | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011009ACN-2026-03-4000122652 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122652 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122652 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122652 | AUD-2026-03-2000011009ACN-2026-03-4000122652 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | Corrective actions have been taken for both the TTs to rectify the identified deficiencies. Further, it has been ensured that all TTs are covered under quarterly safety checks, during which the condition and functionality of all safety fittings are verified to ensure compliance and safe operations. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122657 | Closed | DAS DARSHAN | 2026-03-06 | 1. TT fitting check was carried for following TT and observation recorded 1.a. UP73A5022: Improper battery terminal wiring, Non-functional/inadequate spark arrestor 1.b. UP78HN1570: Improper battery terminal insulation and wiring. | 3.1 | TT fittings & discipline checked | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122657 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122657 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122657 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122657 | AUD-2026-03-2000011009ACN-2026-03-4000122657 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | Training on usage of PPE is given to Nayara TT crews by both HPCL and Nayara Officers | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122660 | Closed | DAS DARSHAN | 2026-03-06 | Housekeeping practice is found satisfactory. PPE (safety harness) usage by Nayara TT crew - UP53LT5171 & CG04LN4358 is found improper | 3.15 | Housekeeping & PPE usage checked | 1292 | LUCKNOW DEPOT | Location to ensure PPE usage by TT crew. | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122660 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122660 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122660 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122660 | AUD-2026-03-2000011009ACN-2026-03-4000122660 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | The observations made during inspection has been taken care in the fire drill conducted in 24.02.26. Also the alternate WCFM available near Training Hall with raised platform can be used for better reach of water and Foam to handle any emergency. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121399 | Closed | ARYA VIPIN KUMAR | 2026-03-07 | 1. Date 30.01.2026 & Time: 10:25 AM 2. Area of drill conducted: TT parking 3. Scenario covered: Fire in TT 4. Double/single Contingency: Single contingency 5. Observations: 5.1 Team leaders to ensure effective communication and reporting to fire chief during drills 5.2 Location to check reach of fire monitors in TT parking area. 5.3 Location to conduct training to contract workmen andofficers on usage of firefighting equipment specially fire hoses. 5.4 Location to conduct frequent drills in TT parking area and post drill sessions with TT crew ensure effective TT evacuation during emergency 5.5 Location to conduct training session with TT crew on type of fire extinguisher and their usage. 5.6 During drill, delay in operation of different equipment was observed. Same is required to reviewed. 5.7 Location to impart training to security personnel for crowd management in TT parking area. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1292 | LUCKNOW DEPOT | Corrective action shall be taken to improve in mock drills. | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000121399 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000121399 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000121399 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000121399 | AUD-2026-03-2000011009ACN-2026-03-4000121399 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-06 | As a corrective action, the concerned TT crew were denied entry into the plant for two weeks. The mobile phone was deposited in thelocker at Lucknow IRD for 20 days. In addition, security checking at the in-gate has been made more stringent to prevent recurrenceof such incidents. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122680 | Closed | DAS DARSHAN | 2026-03-06 | During TT cabin inspection, Mobile phone and match box found inside TT UP78HN1570 & UP73A5022. | 6.13 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122680 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122680 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122680 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122680 | AUD-2026-03-2000011009ACN-2026-03-4000122680 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | The identified deficiencies were rectified through rework. The vendor was also cautioned and instructed to ensure proper workmanship and adherence to quality standards in future works. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122681 | Closed | DAS DARSHAN | 2026-03-07 | Poor workmanship observed during review of work carried out by M/s Jai Bajarang under supervision of Sh. Vivek Singh. | 6.14 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122681 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122681 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122681 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122681 | AUD-2026-03-2000011009ACN-2026-03-4000122681 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | The concerned TT crew were called for verification and their identity and signatures were revalidated. They were counselled to maintain consistency in signatures across all official documents. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122670 | Closed | DAS DARSHAN | 2026-03-07 | Training records of TT Crew of UP78HN1570 Driver Sh. Ajai Kumar and Sh. Sarvajeet was checked. Last Training as per OISD 154 attended on date 05.12.2025. Signature not matching in ID card and training record. | 6.3 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122670 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122670 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122670 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122670 | AUD-2026-03-2000011009ACN-2026-03-4000122670 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | The officer was able to explain the working and operational procedure of the Phytoremediation Plant as per SOP. However, he could not point out the exact location of the sump at that moment, as the sump is an underground structure and not visibly identifiable on the surface. The officer is now fully familiarized with the exact location of the sump | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122671 | Closed | DAS DARSHAN | 2026-03-07 | Officer found not to be familiarised with facility available. Sh. Darshan was not aware of SOP of operation of Phytoremediation plant. | 6.4 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122671 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122671 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122671 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122671 | AUD-2026-03-2000011009ACN-2026-03-4000122671 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | The screw has been provided in JB117 | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122672 | Closed | DAS DARSHAN | 2026-03-07 | One screw of JB 117 found missing. | 6.5 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122672 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122672 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122672 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122672 | AUD-2026-03-2000011009ACN-2026-03-4000122672 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | Unwanted material has been shifted to scrap yard. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122674 | Closed | DAS DARSHAN | 2026-03-07 | Unwanted material found near pipe line - to be shifted to scrap yard. | 6.7 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122674 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122674 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122674 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122674 | AUD-2026-03-2000011009ACN-2026-03-4000122674 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
ARYA VIPIN KUMAR | 2026-03-07 | DAS DARSHAN | 2026-03-07 | Height restriction boarda are displayed near siding barrier so that same may be visible in movement from either side with Photo forbetter understanding. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122676 | Closed | ARYA VIPIN KUMAR | 2026-03-07 | Height restriction board to be displayed at siding barrier. | 6.9 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122676 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122676 | 2026-09-03 | 46.7538 | 187 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122676 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122676 | AUD-2026-03-2000011009ACN-2026-03-4000122676 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 27
|  |  |  | in progress | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123651 | Open | PANDEY AKHIL | 2026-03-07 | Pending observations are as below | 3.18 | OISD/MDSA/SSA compliance reviewed | 1937 | SURYAPET TERMINAL | All the points under SAFE 100 and MDSA 24-25 are closed SAFE 100-46/46 MDSA 24-25-14/14 MDSA 25-26 -19/18 | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123651 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123651 | 2026-08-04 18:45 | 75.9726 | 211 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123651 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011061ACN-2026-03-4000123651 |  | AUD-2026-03-2000011061ACN-2026-03-4000123651 | 21 |  | 26 | 80 | 0 | 0 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124076 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Follow up to be made with railways on monthly basis for pending land lease issue | 1.3 | Pending issues reviewed | 1777 | Hassan Terminal | Coordinate with Railways | SOD | Marketing | SWZ | 2026-03-31 |  | 6 |  | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124076 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124076 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124076 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124076 |  | AUD-2026-03-2000011172ACN-2026-03-4000124076 | 21 |  | 26 | 80 | 1 | 2 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124077 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Pending Railway land lease payment | 1.5 | HQO / Zonal support required identified | 1777 | Hassan Terminal | Follow up with railways and meeting to be conducted with SWZ railway officials | SOD | Marketing | SWZ | 2026-03-31 |  | 6 |  | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124077 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124077 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124077 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124077 |  | AUD-2026-03-2000011172ACN-2026-03-4000124077 | 21 |  | 26 | 80 | 1 | 2 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124079 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Interacted with security and their awareness on emergency preparedness found to be satisfactory.Checked PA system found to be functional except pump house | 2.4 | Security alertness checked (night-halt / surprise checks) | 1777 | Hassan Terminal | PA system near pump house to be made functional | SOD | Marketing | SWZ | 2026-03-31 |  | 9 |  | S3 | F3 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124079 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124079 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124079 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124079 |  | AUD-2026-03-2000011172ACN-2026-03-4000124079 | 21 |  | 26 | 80 | 1 | 2 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124084 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Location needs to have one security guard with HVD | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1777 | Hassan Terminal | Location to take action | SOD | Marketing | SWZ | 2026-03-31 |  | 6 |  | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124084 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124084 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124084 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124084 |  | AUD-2026-03-2000011172ACN-2026-03-4000124084 | 21 |  | 26 | 80 | 1 | 2 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124087 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Water level variation is observed which needs to be rectified | 3.7 | Inventory physical dip of minimum two tanks taken | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-03-31 |  | 8 |  | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124087 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124087 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124087 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124087 |  | AUD-2026-03-2000011172ACN-2026-03-4000124087 | 21 |  | 26 | 80 | 1 | 2 | 31
|  |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124089 | Open | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | All points of OISD audit are complied, two points of SSA are to be complied,MDSA audit compliance under progress(MDSA 2023-24: one point pending; MDSA 2024-25: two points are pending and MDSA 2025-26: 19 points pending) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1777 | Hassan Terminal | To be complied at the earliest | SOD | Marketing | SWZ | 2026-03-31 |  | 9 |  | S3 | F3 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124089 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124089 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124089 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011172ACN-2026-03-4000124089 |  | AUD-2026-03-2000011172ACN-2026-03-4000124089 | 21 |  | 26 | 80 | 1 | 2 | 31
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122712 | Open |  |  | It was observed that TT reporting in the starting of the office hours is very less. Advised location to follow up and ensure improved TT reporting | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011215ACN-2026-03-4000122712 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122712 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122712 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011215ACN-2026-03-4000122712 |  | AUD-2026-03-2000011215ACN-2026-03-4000122712 | 21 |  | 26 | 80 | 2 | 2 | 57
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122713 | Open |  |  | The efficacy of present available transport TT fleet was discussed in detail and advised location for ensuring 100% indent execution at all times. At present location is facing occasional TT shortage due to WZ DS indents. Location has been advised to induct additional TTs as per tender terms and conditions by local notification. Draft local notification has been reviewed, corrected and finalized to release to transporters as per tender provisions. | 1.8 | Improvement plans discussed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-03-2000011215ACN-2026-03-4000122713 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122713 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122713 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011215ACN-2026-03-4000122713 |  | AUD-2026-03-2000011215ACN-2026-03-4000122713 | 21 |  | 26 | 80 | 2 | 2 | 57
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122718 | Open |  |  | The following Tank Trucks were inspected at TT Gantry area for safety fittings and post load EM lock checks for any suspected abusecase and observations are as follows- Sr. No. TT No. Carrier Name Capacity Lock No. 1 Remarks Lock No. 2 Remarks 1 GJ21Y8426 LOTUS PETROLEUM 20 KL 18907 Verification with intelligent key- Suspected abused lock. 18908 Verification with intelligent key- OK. 2 GJ26T5166 DHEERAJ PETROLEUM 14 KL 16370 Verification with intelligent key- OK. 16369 Verification with intelligent key- OK. 3 GJ30T6185 VEDRAJ PETROLEUM 12 KL 18897 Verification with intelligent key- OK. 18898 Verification with intelligent key- OK. 4 DD01P9543 ADITYA ROADLINES 20 KL 2973 Verification with intelligent key- Suspected abused lock. 12614 Verification with intelligent key- OK. 5 CG10BN5144 BHARAT ROADWAYS 14 KL 5956 Verification with intelligent key- Suspected abused lock. 5965 Verification with intelligent key- OK. | 3.1 | TT fittings & discipline checked | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-03-2000011215ACN-2026-03-4000122718 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122718 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122718 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011215ACN-2026-03-4000122718 |  | AUD-2026-03-2000011215ACN-2026-03-4000122718 | 21 |  | 26 | 80 | 2 | 2 | 57
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122719 | Open |  |  | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 |  | 4 |  | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122719 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122719 | 2026-08-06 | 74.7538 | 241 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122719 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011215ACN-2026-03-4000122719 |  | AUD-2026-03-2000011215ACN-2026-03-4000122719 | 21 |  | 26 | 80 | 2 | 2 | 35
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122720 | Open |  |  | Yes reviewed | 3.5 | EM Lock SOP compliance verified | 1412 | HAZIRA IRD (STP 1044) | Location to ensure correction action in line with circular for verification within 15 days | SOD | Marketing | NWR | 2026-04-30 |  | 4 |  | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122720 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122720 | 2026-08-06 | 74.7538 | 241 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122720 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011215ACN-2026-03-4000122720 |  | AUD-2026-03-2000011215ACN-2026-03-4000122720 | 21 |  | 26 | 80 | 2 | 2 | 35
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122721 | Open |  |  | Current compliance status of SSA has been discussed with Hazira team with action plan for ensuring time bound closure of pending 3 Nos recommendations. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011215ACN-2026-03-4000122721 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122721 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122721 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011215ACN-2026-03-4000122721 |  | AUD-2026-03-2000011215ACN-2026-03-4000122721 | 21 |  | 26 | 80 | 2 | 2 | 57
MAJUMDER BIRAJ | 2026-05-30 | BUDHI VEERAIAH | 2026-05-26 | Hosekeeping improved by removing all the project surplus materials that were lying in fire pumphouse and at nearby fire water tanksof Kolkata Terminal 1 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127507 | Closed | BUDHI VEERAIAH | 2026-05-29 | Housekeeping practice is found satisfactory. Location is advised to remove the project surplus near fire engine and Water tank. It was observed that the project work is being undertaken b/w admin building and water tank area. Plastic bucket was found inside the pump house area | 3.15 | Housekeeping & PPE usage checked | 1644 | KOLKATA-I TERMINAL | The area to be cleared/ housekeeping to be improved and project work to be shifted to other safe place. Contractor material in pump house area to be removed on priority. | SOD | Marketing | EZ | 2026-03-30 | INADEQUATE SAFETY CULTURE | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-04-04 | AUD-2026-03-2000010730ACN-2026-03-4000127507 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127507 | 2026-09-18 | 31.7538 | 271 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127507 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127507 | AUD-2026-03-2000010730ACN-2026-03-4000127507 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 39
ARYA VIPIN KUMAR | 2026-06-01 | KUMAR NITISH | 2026-03-28 | Complied. Blending percentage being monitored regularyat TT gantry. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122078 | Closed | KUMAR NITISH | 2026-03-28 | Ethanol blending checked for TT WB19K7947 Bay no 3. Blending % is found 16%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1128 | MATHURA TERMINAL | Location to check and verify ethanol % blending . | SOD | Marketing | NUZ | 2026-02-27 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-27 | AUD-2026-02-2000010909ACN-2026-02-4000122078 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122078 | 2026-09-18 | 31.7538 | 273 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122078 | 532 | 8294 | 21 | 8294 | 234 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122078 | AUD-2026-02-2000010909ACN-2026-02-4000122078 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 39
SINGWAL DEEPAK | 2026-06-02 | CHAHAR ALKESH KUMAR | 2026-05-15 | Additional budget request was submitted on portal and all pendig invoices and accruals have been processed. | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127195 | Closed | CHAHAR ALKESH KUMAR | 2026-05-15 | Nil pending. Requirement of budget at location. Location was advised to get the same from other location within Zone. | 1.3 | Pending issues reviewed | 1435 | GWALIOR DEPOT | Location is advised to get the same from other location within Zone. | SOD | Marketing | CEN | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011237ACN-2026-03-4000127195 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127195 | 2026-08-22 19:00 | 57.9622 | 274 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127195 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011237ACN-2026-03-4000127195 | AUD-2026-03-2000011237ACN-2026-03-4000127195 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 40
SINGWAL DEEPAK | 2026-06-02 | CHAHAR ALKESH KUMAR | 2026-05-15 | New Camera has been installed near TLF. | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127196 | Closed | CHAHAR ALKESH KUMAR | 2026-05-15 | Out of 65 only 01 CCTVs were found faulty for which tender evaluation is in process and expected to restore by 30.04.2026. | 2.6 | CCTV functioning checked | 1435 | GWALIOR DEPOT | Location is advised restoration of 1 nos. faulty cameras by 30.04.26. | SOD | Marketing | CEN | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 3 | PROCESS SAFETY | S1 | F3 | 2026-04-30 | AUD-2026-03-2000011237ACN-2026-03-4000127196 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127196 | 2026-08-22 19:00 | 57.9622 | 274 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127196 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011237ACN-2026-03-4000127196 | AUD-2026-03-2000011237ACN-2026-03-4000127196 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 40
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000134145 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. TTLF Gantry efficiency to be improved 2. All officers to be rotated and should know all jobs in terminal 3. SOP for pipelinereceipt to be made with OMC members | 1.8 | Improvement plans discussed | 1630 | PARADEEP TERMINAL | 1. TTLF loading performance to meet SBU target 2. Officer rotations , particularly in ethanol handling 3. SOP with OMC for PLT receipt to avoid losses | SOD | Marketing | ECZ | 2026-07-15 |  | 6 |  | S3 | F2 | 2026-07-15 | AUD-2026-06-2000012424ACN-2026-06-4000134145 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134145 | 2026-08-20 17:50 | 60.0108 | 317 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134145 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000134145 |  | AUD-2026-06-2000012424ACN-2026-06-4000134145 | 21 |  | 27 | 80 | 11 | 11 | 46
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000134147 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1630 | PARADEEP TERMINAL | Location advised to inform security DGR owner to carry out inspection in night & have record of the same . Also advised to carry out mock drill in night | SOD | Marketing | ECZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134147 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134147 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134147 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000134147 |  | AUD-2026-06-2000012424ACN-2026-06-4000134147 | 21 |  | 27 | 80 | 11 | 11 | 44
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135301 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | TK 4 -HSD : Phy-537.2, T-33'c / TAS - 536.7, T-33.4 TK 14 -MS : Phy - 190.8 ,W-2.6, T-32.3/TAS - 190.4, T-32.49, W- 2.0 cm TK-6-Ethanol : Phy- 292.2, T-33/ TAS- 291.5, T- 33.62 | 3.7 | Inventory physical dip of minimum two tanks taken | 1630 | PARADEEP TERMINAL | Minor variation found in Ref.height of Tank 6 (3mm) TO BE CORRECTED | SOD | Marketing | ECZ | 2026-07-30 |  | 6 |  | S3 | F2 | 2026-07-30 | AUD-2026-06-2000012424ACN-2026-06-4000135301 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135301 | 2026-08-20 17:50 | 60.0108 | 332 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135301 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135301 |  | AUD-2026-06-2000012424ACN-2026-06-4000135301 | 21 |  | 27 | 80 | 11 | 11 | 48
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135303 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. SKO dye mixing equipement surplus after location made SKO free 2. RIM seal protection system one old panel is lying idle at first floor of planning room, to be removed and disposed | 3.9 | Abnormal variations / unused assets reviewed | 1630 | PARADEEP TERMINAL | 1. this facility to be offered to HQO for utilization at other locations 2. disposal to be done | SOD | Marketing | ECZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012424ACN-2026-06-4000135303 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135303 | 2026-08-20 17:50 | 60.0108 | 333 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135303 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135303 |  | AUD-2026-06-2000012424ACN-2026-06-4000135303 | 21 |  | 27 | 80 | 11 | 11 | 48
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135306 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | Compliance status reviewed . OISD compliances of 2 points AND 6 NOS. FOR SSA pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1630 | PARADEEP TERMINAL | advised to comply by 30.6.2026 | SOD | Marketing | ECZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135306 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135306 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135306 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135306 |  | AUD-2026-06-2000012424ACN-2026-06-4000135306 | 21 |  | 27 | 80 | 11 | 11 | 44
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000135311 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | scrap disposal of pending sprinkler material & other misc. fixed assets items valuation done. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1630 | PARADEEP TERMINAL | RFD to be made & disposal to be done . Also some other fixed asset items not in usable condition like RIM SEAL panel in planning room , valves , found to be included in RFD | SOD | Marketing | ECZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012424ACN-2026-06-4000135311 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135311 | 2026-08-20 17:50 | 60.0108 | 333 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135311 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135311 |  | AUD-2026-06-2000012424ACN-2026-06-4000135311 | 21 |  | 27 | 80 | 11 | 11 | 48
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135314 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | HSD Expressway ( 2 nos.) found to be idling most of the time | 6.3 | Gantry Infrastructure | 1630 | PARADEEP TERMINAL | suggested that SKO loading arms and MFM can be used to provide MS loading points to utilize 2 bays fully | SOD | Marketing | ECZ | 2026-12-31 |  | 6 |  | S3 | F2 | 2026-12-31 | AUD-2026-06-2000012424ACN-2026-06-4000135314 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135314 | 2026-08-20 17:50 | 60.0108 | 486 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135314 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135314 |  | AUD-2026-06-2000012424ACN-2026-06-4000135314 | 21 |  | 27 | 80 | 11 | 11 | 70
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135315 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. LOTO for control switches of non-operating equipment 2. 2 nos. addl. Exhaust to be provided 3. Entry of MCC room shall be from De-licensed area | 6.4 | MCC room | 1630 | PARADEEP TERMINAL | as per comments | SOD | Marketing | ECZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135315 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135315 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135315 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135315 |  | AUD-2026-06-2000012424ACN-2026-06-4000135315 | 21 |  | 27 | 80 | 11 | 11 | 44
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135316 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | Near FPH , HSD line found to be burried in PCC with flange | 6.5 | Product pipeline | 1630 | PARADEEP TERMINAL | to be made free | SOD | Marketing | ECZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135316 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135316 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135316 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135316 |  | AUD-2026-06-2000012424ACN-2026-06-4000135316 | 21 |  | 27 | 80 | 11 | 11 | 44
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135317 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. Out Barrier not working 2. IN/OUT Tablet not working 3. RMU - Overfill sensor not being used by TTs , not checked also 4. Tank 1 & 2 , Remote working od MOV not doing , AUMA make 5. Tk 21 Radar Gauge card damage 6. Power dosing - not working 7. VRU- not working from last 2 months 8. Ethanol VFD - commissioning not done 9. VMS not working 10. Public address system not working | 6.6 | TAS observations | 1630 | PARADEEP TERMINAL | All these issues to be resolved | SOD | Marketing | ECZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012424ACN-2026-06-4000135317 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135317 | 2026-08-20 17:50 | 60.0108 | 333 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135317 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135317 |  | AUD-2026-06-2000012424ACN-2026-06-4000135317 | 21 |  | 27 | 80 | 11 | 11 | 48
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135318 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. Proper painting and Tagging of R1, R2 & R3 , KEY BOX to be done for identification and visibility. 2. Planning Room needs to be properly organised and also the acess needs to be review to avoid unwanted acess . | 6.7 | Gate entrance area | 1630 | PARADEEP TERMINAL | as per the Observation comments | SOD | Marketing | ECZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012424ACN-2026-06-4000135318 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135318 | 2026-08-20 17:50 | 60.0108 | 333 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135318 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135318 |  | AUD-2026-06-2000012424ACN-2026-06-4000135318 | 21 |  | 27 | 80 | 11 | 11 | 48
|  |  |  | OPEN | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135319 | Open | KHADE RAKESH GANPATRAO | 2026-06-03 | 1. AFFF &AR-AFFF foam tank area to be maitained properly . 2. Tank naming /marking to be done correctly as per std . Pipe line direction to be provided in the Foam Tank area . | 6.8 | Foam Tank Area | 1630 | PARADEEP TERMINAL | as per the Observation comments | SOD | Marketing | ECZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012424ACN-2026-06-4000135319 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135319 | 2026-08-20 17:50 | 60.0108 | 333 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135319 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135319 |  | AUD-2026-06-2000012424ACN-2026-06-4000135319 | 21 |  | 27 | 80 | 11 | 11 | 48
DANTHAMALLA SATISH KUMAR | 2026-06-04 | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | Tank Wagon Pump House HCD Made Functional | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123024 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | HVLR, HCD, Sprinklers operation checked. Found Ok. Wagon pump house HCD found not working. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1940 | KADAPA DEPOT | HCD at TW pumphouse to be made functional | SOD | Marketing | SCR | 2026-02-25 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123024 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123024 | 2026-08-20 11:30 | 60.2747 | 276 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123024 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123024 | AUD-2026-03-2000010862ACN-2026-03-4000123024 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 40
DANTHAMALLA SATISH KUMAR | 2026-06-04 | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | CCTV installed in place of non working cameras. For 2 existing cameras focussing and adjustment done. | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123022 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | Yes. 5 CCTVs are under outage. Same to be repaired at the earliest. Focus of 2 cameras to be corrected. | 2.6 | CCTV functioning checked | 1940 | KADAPA DEPOT | New CCTV to be installed in place of non working cameras. For 2 existing cameras focussing to be adjusted. | SOD | Marketing | SCR | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010862ACN-2026-03-4000123022 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123022 | 2026-08-20 11:30 | 60.2747 | 276 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123022 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123022 | AUD-2026-03-2000010862ACN-2026-03-4000123022 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 40
DANTHAMALLA SATISH KUMAR | 2026-06-04 | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | projects works are in progress. as per schedule targets projects will be completed | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123039 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-06-04 | New AG Tank - PCSA to be conducted, LT supply from VDPL - 31.03.2026, Ethanol unloading gantry - 20.02.3036 & Fire engine panels - 30.03.2026 | 4.3 | Project progress reviewed | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000010862ACN-2026-03-4000123039 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123039 | 2026-08-20 11:30 | 60.2747 | 276 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123039 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123039 | AUD-2026-03-2000010862ACN-2026-03-4000123039 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 40
MANDAL PRATAPKUMAR | 2026-06-07 | NILABH | 2026-05-23 | New CCTV Camera installation completed at location. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127431 | Closed | NILABH | 2026-05-23 | 10 numbers of cameras are not working. CCTV recording of 92 days available. MOC approval not available with location. | 2.6 | CCTV functioning checked | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-10 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127431 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127431 | 2026-08-26 17:00 | 54.0455 | 279 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127431 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127431 | AUD-2026-04-2000011243ACN-2026-04-4000127431 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 40
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | 1) Clean Agent System is TT loading Control Room is not mandarory as per Clause 5.1.2.33 of Petroleum and Natural Gas Regulatory Board (Technical Standards and Specifications including Safety Standards for Petroleum Installations) Regulations, 2020. 2 Nos of 2 Kg Clean Agent extinguishers have been provided in Control Room. 2) ERDMP prepared, Audit for additional 8000 KL HSD Tank (TK-15) was conducted on 28-30 May 2026. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125384 | Closed | SHETTY ANURANJAN | 2026-06-09 | Two points of T4S audit are still pending to be complied: 1. Clean agent system in control room 2. ERDMP approval of new tank constructed | 1.3 | Pending issues reviewed | 1242 | JAIPUR TERMINAL | Pls ensure compliance of both the points. | SOD | Marketing | NWF | 2026-04-15 | OUTDATED OR COMPLEX SOPS | 9 | PROCESS SAFETY | S3 | F3 | 2026-04-15 | AUD-2026-03-2000011022ACN-2026-03-4000125384 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125384 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125384 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125384 | AUD-2026-03-2000011022ACN-2026-03-4000125384 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Tank TK4 was converted from MS to Gasohol on 28/03/2026. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125386 | Closed | SHETTY ANURANJAN | 2026-06-09 | Tank TK4 is to be converted from MS to gasohol. This is a last year project with scheduled completion date of 30.09.2025. SOP was developed by location. Location needs to finalyse SOP and prepare MOC. This tank needs to be converted to gasohol by 31st march 2026.For any support from pipeline SBU, Zone/HQO will extend support. | 1.5 | HQO / Zonal support required identified | 1242 | JAIPUR TERMINAL | Pls ensure conversion of TK4 into gasohol | SOD | Marketing | NWF | 2026-03-31 | HARSH WORKING CONDITIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125386 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125386 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125386 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125386 | AUD-2026-03-2000011022ACN-2026-03-4000125386 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Security Co-ordination Meeting was conducted on 15/04/2025. Report available. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125387 | Closed | SHETTY ANURANJAN | 2026-06-09 | Yes. Location conducted MARG members meeting frecently in presence of Sr. Police Offiials. | 1.8 | Improvement plans discussed | 1242 | JAIPUR TERMINAL | Location is required to conduct security co-ordination committee meeting. Pls make report on this meeting with signatures of all officials present. | SOD | Marketing | NWF | 2026-04-15 | OUTDATED OR COMPLEX SOPS | 8 | EMERGENCY | S2 | F4 | 2026-04-15 | AUD-2026-03-2000011022ACN-2026-03-4000125387 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125387 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125387 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125387 | AUD-2026-03-2000011022ACN-2026-03-4000125387 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Noted. Necessary improvement was observed in response of participants in subsequent mock drills. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125388 | Closed | SHETTY ANURANJAN | 2026-06-09 | Yes. Double contingency scenarion was developed. LIC was made as an observer. Fire drill conducted on 11th March at 14.45 hr. Positive points: 1. All equipment operated satisfactorily. 2. Location followed the process of extinguishing the fire as per SOP. 3. Location officers including contract manpower were involved Area of improvements: 1. Communication can be improvised. 2. Seurity guards to be trained to guide tank trucks for smooth evacuation 3. Fire hoses with foam branch pipe should be used for to the point fire fighting. Even if, it is not used, auxiliary team can make it in ready condition. | 2.2 | Double contingency scenario simulated; observations recorded | 1242 | JAIPUR TERMINAL | This is continuous process of improvments. Location to improve upon in every fire drill | SOD | Marketing | NWF | 2026-03-31 | HARSH WORKING CONDITIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125388 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125388 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125388 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125388 | AUD-2026-03-2000011022ACN-2026-03-4000125388 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Location has conducted surprise inspection during night (29/03/26) and on Sunday (17/05/26 & 07/06/26) to access alertness of security. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125390 | Closed | SHETTY ANURANJAN | 2026-06-09 | Checked through CCTV footage of 2 AM to 3 AM, 10th March 2026 for visitor room and locking platform area. No security was observed sitting at visitor room or doing patrolling. Two securities were nlot aware of display screen (TAS screen). They were not knowing about safety briefing. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1242 | JAIPUR TERMINAL | Location needs to make surprise night inspection. Whether securities are really reporting at office? Are they sleeping inside Terminal in one room? This needs to be verified. Traiuning of security personnel to be enhanced. | SOD | Marketing | NWF | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125390 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125390 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125390 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125390 | AUD-2026-03-2000011022ACN-2026-03-4000125390 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Ethanol TTs are being checked by officers for emptiness. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125391 | Closed | SHETTY ANURANJAN | 2026-06-09 | Check for three different periods: 1. 31.12.2025, 17.00 hr to 17.30 hr (TT gantry area) 2. 15.12.2025, 09.00 hr to 09.30 hr (TT gantry area) 3. 09.03.2026, 14.00 hr to 15.00 hr (TT gantry and Securiry locking platform) 1. TT crews were wearing PPE. Fire ext. were kept at required place. 2. Ethanol TT no. GJTA3297 was cheked at TT gantry for unloading of product and checking of emptyness by officer. It is observed that emptyness of TT was checked by TT driver only at Gantry. It was further cross checked whether anyofficer checks the emptyness of tank truck at security locking platform. It was observed that ine security was found standing on sliding platform of locking area. He was checking the emptyness from distance. No officer checked the emptyness. 3. It was checked toascertain whether location is keeping 92 days back up or not. It is okay | 2.6 | CCTV functioning checked | 1242 | JAIPUR TERMINAL | As per SOP, minimum two officer needs to check empty tank truck. Even a single officer didn't check the emptyness of ethanol TT. This is a serious concern. Location to follow SOP. | SOD | Marketing | NWF | 2026-03-31 | HARSH WORKING CONDITIONS | 20 | PROCESS SAFETY | S4 | F5 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125391 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125391 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125391 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | HIGH |  | AUD-2026-03-2000011022ACN-2026-03-4000125391 | AUD-2026-03-2000011022ACN-2026-03-4000125391 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Visitor register is being filled by concerned visitor only. The same has been implemented. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125392 | Closed | SHETTY ANURANJAN | 2026-06-09 | Access control system checked. Securities were aware of SOP for visitor entries. It is observed that visitor register is filed by security staffs only. This is not correct. Visitor register is to be filled by concerned visitor only. | 2.8 | Access control systems checked | 1242 | JAIPUR TERMINAL | Pls ensure. | SOD | Marketing | NWF | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125392 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125392 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125392 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011022ACN-2026-03-4000125392 | AUD-2026-03-2000011022ACN-2026-03-4000125392 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Foam Tank has been filled upto available quantity. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125393 | Closed | SHETTY ANURANJAN | 2026-06-09 | 1. 8.5 Kl x 2 tanks: Only one tank was having foam. It was having 2 KL foam. 2nd tank was empty. 2. Location informed that they requre 10 KL of foam as per OISD 244 requirement. There were approx 5 KL of foam inside barrels kept near central foam shed. Locationwas advised to fill foam tanks. | 2.9 | Foam inventory verified | 1242 | JAIPUR TERMINAL | Pls top up foam tanks with required level as early as possible. | SOD | Marketing | NWF | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125393 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125393 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125393 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125393 | AUD-2026-03-2000011022ACN-2026-03-4000125393 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Displacement Water Tank handed over by MDPL to Terminal on 01/06/26. The observed water level in the tank is 13.686 m, corresponding to an available water quantity of approximately 6,700 KL. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125394 | Closed | SHETTY ANURANJAN | 2026-06-09 | Displacement water tank, under custody of Pipeline SBU, is empty. This tank is a part of total water storage requirement of location. Location is operating with approx 55 to 60% water requirement. Location sent MOC and requested for 2 months time to bring displacement water tank in operation. It was returned with remark that water needs to be replenished latest by 30.04.2026. Pls take up withPipeline SBU. | 2.10 | Fire water levels verified | 1242 | JAIPUR TERMINAL | Location needs to take up with pipeline department. They should extend support to them if needed. | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | ASSET INTEGRITY | S3 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125394 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125394 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125394 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125394 | AUD-2026-03-2000011022ACN-2026-03-4000125394 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | SOP has been displayed in Gantry for actions to be taken by TT crew in case of emergency (both inside terminal as well as outside terminal. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125396 | Closed | SHETTY ANURANJAN | 2026-06-09 | Emergency preparedness checked. It require further training. | 2.15 | TT crew roadside emergency procedures checked | 1242 | JAIPUR TERMINAL | Zone has shared SOP in Hindi for actions to be taken by TT crew in case of emergency (both inside terminal as well as outside termnal. It needs to be displayed at prominent place and training to be given to all TT crew | SOD | Marketing | NWF | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125396 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125396 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125396 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125396 | AUD-2026-03-2000011022ACN-2026-03-4000125396 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-05-19 | The close monitoring of VTS violations are being maintained and action also taken as per iTDG. Necessary explanation from transporters/TT crew also obtained. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125398 | Closed | SHETTY ANURANJAN | 2026-06-09 | List of VTS deviations for the period 05.01.2026 to 22.02.2026 shared with locations by Zone. There are cases where route corrections may be required. Multiple loaded Tts are stopping at one place. Location is required to take explanation from transporter. If explanation is not satisfactory, location needs to take up with Administration, including SP. If concerned DCT or transporter is not giving reply of our letter and their TT is still stopping at that place, then TT loading has to be stopped. | 3.3 | VTS deviations reviewed | 1242 | JAIPUR TERMINAL | Location to take corrective action and revert. | SOD | Marketing | NWF | 2026-04-30 | HARSH WORKING CONDITIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125398 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125398 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125398 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125398 | AUD-2026-03-2000011022ACN-2026-03-4000125398 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | 5 % Surprise Check is being conducted for TTs to access correctness of dips. Records maintained. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125397 | Closed | SHETTY ANURANJAN | 2026-06-09 | Checked for 7 TTs. Following variations observed compartment wise: 1. RJ14GQ8297, 20 KL HSD, Bay 3: +2 mm/+1 mm/+2 mm/+2 mm 2. RJ23GC9474, 4 MS + 8 HSD, Tpt TT, Bay 4: +5 mm/+2 mm/+2 mm 3. RJ25GA6305, 10 KL MS +10 Kl HSD, Bay 7: +3 mm/+3 mm/+1 mm/+1 mm 4. RJ23GD1241, 4 MS + 10 HSD, bay 6: OK/+2 mm/OK 5. RJ14GT3479, 4 ms + 8 HSD, Bay 5: +3 mm/ok/ok 6. RJ14GK7482, 10 MS +10 HSD, Bay 11: OK/-5 mm/+5 mm/+6 mm 7. RJ29GA6353, Bay-3, 10 MS +4 HSD: OK/+2 mm/ok Dip rod checked for TT no.RJ14GK7482. Initially variation of2 mm was observed in DL and PL of each compartment. Location changed the meter tape. With new meter tape, there were nil variations. Dip rod was checked for TT no. RJ29GA6353. Found okay. | 3.2 | Post-loading dip checks verified | 1242 | JAIPUR TERMINAL | Variation observed in two trasnport Tts. DCT Tts performed well. It is advised to check dip of all transport Tts and share the result. If any transport TT is consistently showing variation equal to or greater than +3 mm, pls go for recalibration of that TT. | SOD | Marketing | NWF | 2026-04-30 | OUTDATED OR COMPLEX SOPS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125397 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125397 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125397 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125397 | AUD-2026-03-2000011022ACN-2026-03-4000125397 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | As per TAS BCU Recipe logic, loading stops with 'No Flow Timeout Error' when Ethanol percentage in current batch falls below 17% oris greater than 23% of the total quantity loaded at that instant. Ethanol content at that particular instant is taken based on the recipe number assigned at the time of load building. Same has been observed during several instances happened during the months of May'26 and June'26 when Ethanol quantity loaded was not as per the recipe blend percentage. For those instances, loading stopped successfully with No Flow Timeout Error. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125399 | Closed | SHETTY ANURANJAN | 2026-06-09 | Checked following three TTs loaded with EBMS: 1. RJ26GA2139, Bay 12 2. RJ26GA7799, Bay 8, Rajasthan Auto Service 3. RJ14GH9717, Bay 9, MF Bulk Carrier, Destined to Kesar Filling Stn. Pls find the observations: 1) No. of alarm (1% to 3% variation): Nil No. of alarm >3% variation: Nil 2) MS vs Ethanol qty was in the ratio of 4:1 in the starting up to 800 to 1000 liter MS injection. It changed into 5:1 in between 1000 liter to 3600 Litre MS. After that MS and ethanol injection reduced to almost 2:1. 3) Ethanol loading completed when 100 to 150 litre MS remained. Despite above variations in MS and HSD injection, there were no alarms. Checked bottom and top sample of following three TTs: 1. RJ26GA2139, Bay 12: Comp 1: Top sample density: 750.6, Bottom sample: 751.1, Invoicedensity: 751.9. This is okay 2. RJ26GA7799 Bay 8: Comp 1: Top sample density: 751.1, Bottom sample: 754.5, Comp 2: Top Sample: 749.2, Bottom Sample: 760.6 Comp 3: Top sample: 749.2, Bottom Sample: 757.1 Comp 4: Top sample: 748.7, Bottom sample: 765, Invoice density: 751.9 officer was asked to churn the product of TT no. RJ26GA7799. After churning the result is as follows: Comp 1:Top sample: 750.9, Bottom sample: 754.1 Comp 2: Top Sample: 749.6, Bottom Sample: 757.0 Comp 3: Top Sample: 749.6, Bottom Sample: 755.2 Comp 4: Top Sample: 749.2, Bottom Sample: 755.7 | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1242 | JAIPUR TERMINAL | There is considerable variation in the density of top and bottom samples. This is also not matching with invoice density. There is variation more than +/- 3 kg/cum. This is not acceptable. System was also not generating any alarms. It should have stopped loading of MS and ethanol when ration of MS/ethanol injection came down to 2:1. However, it didn't happen. This shows that TAS logic is byepassed. Location needs to check the same through TAS service provider and revert immediately. | SOD | Marketing | NWF | 2026-04-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 15 | ASSET INTEGRITY | S3 | F5 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125399 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125399 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125399 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125399 | AUD-2026-03-2000011022ACN-2026-03-4000125399 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 | SHETTY ANURANJAN | 2026-06-09 | Housekeeping contract workers have been provided frequency schedule for area/facility wise cleaning. The same is verified by supervisor and M&I Officer. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125401 | Closed | SHETTY ANURANJAN | 2026-06-09 | Overal Housekeeping was good. Drain surrounding the gantry not clean. One contract workman should regularly clean pipeline, TAS equipment, structures through detergent and wet cloth. | 3.15 | Housekeeping & PPE usage checked | 1242 | JAIPUR TERMINAL | Location to ensure | SOD | Marketing | NWF | 2026-03-31 | HARSH WORKING CONDITIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125401 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125401 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125401 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125401 | AUD-2026-03-2000011022ACN-2026-03-4000125401 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | The tanks dip are being taken manually and same are verified with TAS on daily basis. The are within allowable limits. Records maintained. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125400 | Closed | SHETTY ANURANJAN | 2026-06-09 | Dip checked for all 4 MS tanks. There are 3 AG MS tanks and 1UG MS tank. Pls find observations Gross dip/Water/Temp. 1. TK5 (MS): As per TAS: 393.6 cm/0/27.3 As per manual dip: 393.9 cm/Trace/27.5 2.TK4 (MS) As per TAS: 144.8 cm /0/26.6 As per manual dip:144.4/0/26.5 3. TK11 (MS) As per TAS: 1180.0 cm/0/25.2 As per manual dip: 1180.2 cm/0/25.5 4. TS3 (MS): As per TAS: 24.8 cm/0/28.2 As per manual dip: 12.0 cm/2 mm/28.0 | 3.7 | Inventory physical dip of minimum two tanks taken | 1242 | JAIPUR TERMINAL | 1. There is difference of 4 mm in gross dip of TK4. To be reviewed. 2. Considerable difference in gross dip of TS3. There is difference of 12.8 cm. Needs to be checked. Therre is difference of 1941 liter. It also showed 2 mm water. However, as per TAS, water dip is nil. | SOD | Marketing | NWF | 2026-04-30 | OUTDATED OR COMPLEX SOPS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125400 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125400 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125400 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125400 | AUD-2026-03-2000011022ACN-2026-03-4000125400 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | Show Cause Notice was issued to Shri Katyani Fuels for non supply of ethanol on 16/04/26. Reminder letters were also issued on 16/03/26 and 27/03/26 prior issuance of SCN. Joint sampling was conducted and report was obtained on 15/04/26. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125404 | Closed | SHETTY ANURANJAN | 2026-06-09 | Katyani Fuel is not supplying Bio Fuel. 3 letters to be issued before issuing PO cancellation. File note approval to be taken. Sample failed thrice for supplier M/s Vinayak Fuel. Joint sampling to be done as per procedure for commencement of supply from this supplier. | 6.4 | Consumption of Bio Diesel quantity | 1242 | JAIPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-04-15 | OUTDATED OR COMPLEX SOPS | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-15 | AUD-2026-03-2000011022ACN-2026-03-4000125404 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125404 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125404 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011022ACN-2026-03-4000125404 | AUD-2026-03-2000011022ACN-2026-03-4000125404 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | Location has maintained clamp and nipple arrangement for taking care of any leak in product pipeline. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125405 | Closed | SHETTY ANURANJAN | 2026-06-09 | To handle sudden leakage from product pipeline, location should have safety kit. | 6.5 | Handling emergency | 1242 | JAIPUR TERMINAL | Pls make clamp and nipple arrangement for taking care of any leak in product pipeline. Make different sizes of clamps. | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125405 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125405 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125405 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011022ACN-2026-03-4000125405 | AUD-2026-03-2000011022ACN-2026-03-4000125405 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | Necessary records are being maintained in History Cards for safety equipments. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125406 | Closed | SHETTY ANURANJAN | 2026-06-09 | It is observed that RSFPS is in CAMC, few HVLR is in AMC and few are in CAMC. HCD is in AMC. Fire engines and DG are in AMC. History card of CCTV, HVLR, RSFPS, Pumps, Tanks, VRU should be updated properly. Location should update all visit details in History card.If any parts are replaced (even if cost is not borne by HPCL), pls mention that in history card. | 6.6 | History card | 1242 | JAIPUR TERMINAL | Pls update all details including visit of OEM, any servicing done, any filter changed. Even if material changed is under the scope of CAMC vendor, pls write name of material changed and associated cost | SOD | Marketing | NWF | 2026-04-30 | HARSH WORKING CONDITIONS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125406 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125406 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125406 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125406 | AUD-2026-03-2000011022ACN-2026-03-4000125406 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | Monthly monitoring of RTGP is being maintained. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125407 | Closed | SHETTY ANURANJAN | 2026-06-09 | Pending RTGP record (month wise) to be parepared on RTGP register itself. List of open RTGP as per security vs list of open RTGP asper online gate pass portal to be mentioned. It is observed that confirm despatch not done for 8 cases of RTGP. Pls ensure to carryout Confirm Despatch after approving RTGPs. | 6.8 | RTGP monitoring | 1242 | JAIPUR TERMINAL | Monthly monitoring of RTGP by security to be done. Confirm despatch to be done after approving RTGP. | SOD | Marketing | NWF | 2026-04-30 | OUTDATED OR COMPLEX SOPS | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125407 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125407 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125407 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125407 | AUD-2026-03-2000011022ACN-2026-03-4000125407 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | Physical records and SPPI are matching for additive stocks. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125408 | Closed | SHETTY ANURANJAN | 2026-06-09 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.9 | Additive stock monitoring | 1242 | JAIPUR TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-04-30 | OUTDATED OR COMPLEX SOPS | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125408 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125408 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125408 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125408 | AUD-2026-03-2000011022ACN-2026-03-4000125408 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
SHETTY ANURANJAN | 2026-06-09 |  |  | EM Locks are being checked on monthly basis. Records maintained. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125411 | Closed | SHETTY ANURANJAN | 2026-06-09 | Intelligent Key was used to check EM lock conditions of Tts. Two transport Tt and three DCT Tts were checked and found okay. LIC also checked from his own key. | 6.12 | Checking of lock by Intelligent key | 1242 | JAIPUR TERMINAL | Pls check locks by using Intelligent key on weekly basis. 5 Tts per week. Revert with result. 1005 locks to be checked. | SOD | Marketing | NWF | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011022ACN-2026-03-4000125411 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125411 | 2026-09-30 | 19.7538 | 281 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125411 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125411 | AUD-2026-03-2000011022ACN-2026-03-4000125411 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 41
DINESH KUMAR | 2026-06-10 |  |  | Corrective action taken against contamineted Ethanol by reprocessing from local Plant. Point is complied. | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129950 | Closed | DINESH KUMAR | 2026-06-10 | Pending issue of Contaminated ethanol reprocessing was reviewed and discussed. Advised location to expedite and take help from HQO and zone to sensitize vendor. | 1.3 | Pending issues reviewed | 1254 | JALANDHAR DEPOT | XX | SOD | Marketing | NFZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-05-2000011851ACN-2026-05-4000129950 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129950 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129950 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129950 | AUD-2026-05-2000011851ACN-2026-05-4000129950 | 21 | 21 | 27 | 80 | 0 | -21 | 44 | 41
DINESH KUMAR | 2026-06-10 |  |  | Corrective action taken for mentioned HCD and same has been rectified. | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129952 | Closed | DINESH KUMAR | 2026-06-10 | Two nos. HVLR operated. one nos. open path type HCD installed at MS dyke dispatch side is not functioning, Request raised with OMC vendor under AMC for rectification | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1254 | JALANDHAR DEPOT | Location to follow up for HCD repair | SOD | Marketing | NFZ | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-05-31 | AUD-2026-05-2000011851ACN-2026-05-4000129952 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129952 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129952 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129952 | AUD-2026-05-2000011851ACN-2026-05-4000129952 | 21 | 21 | 27 | 80 | 0 | -21 | 39 | 41
DINESH KUMAR | 2026-06-10 |  |  | Corrective action taken and grasscutting done | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129955 | Closed | DINESH KUMAR | 2026-06-10 | Grass & Vegetation observed in parking and near ETP, Grass and vegetation observed in Miyawaki forest area | 3.15 | Housekeeping & PPE usage checked | 1254 | JALANDHAR DEPOT | Grasscutting to ensured in all the operating areas | SOD | Marketing | NFZ | 2026-05-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-10 | AUD-2026-05-2000011851ACN-2026-05-4000129955 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129955 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129955 | 532 | 8294 | 21 | 8294 | 162 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129955 | AUD-2026-05-2000011851ACN-2026-05-4000129955 | 21 | 21 | 27 | 80 | 0 | -21 | 36 | 41
DINESH KUMAR | 2026-06-10 |  |  | New earthpit stickers changed as per actual dates | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129956 | Closed | DINESH KUMAR | 2026-06-10 | No unwanted vegetation is seen in depot. Earth pit condition is checked and found in proper condition. Earthpit testing has been completed but old stickers found on many earthpits | 3.16 | Earth pits / boundary / vegetation control checked | 1254 | JALANDHAR DEPOT | Earthpit testing dates and updated values to be mentioned on all earth pits | SOD | Marketing | NFZ | 2026-05-10 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-10 | AUD-2026-05-2000011851ACN-2026-05-4000129956 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129956 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129956 | 532 | 8294 | 21 | 8294 | 162 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129956 | AUD-2026-05-2000011851ACN-2026-05-4000129956 | 21 | 21 | 27 | 80 | 0 | -21 | 36 | 41
DINESH KUMAR | 2026-06-10 |  |  | all closed | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129957 | Closed | DINESH KUMAR | 2026-06-10 | 8 MOCs in closed status, one MOC in approved status, needs to be closed | 3.17 | MOC status reviewed | 1254 | JALANDHAR DEPOT | approved MOC to be closed in system after the execution of change | SOD | Marketing | NFZ | 2026-05-10 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-10 | AUD-2026-05-2000011851ACN-2026-05-4000129957 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129957 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129957 | 532 | 8294 | 21 | 8294 | 162 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129957 | AUD-2026-05-2000011851ACN-2026-05-4000129957 | 21 | 21 | 27 | 80 | 0 | -21 | 36 | 41
DINESH KUMAR | 2026-06-10 |  |  | Internal inspection for UG12/UG13 completed | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129958 | Closed | DINESH KUMAR | 2026-06-10 | Reviewed and found internal inspection of all AG and UG tanks completed except for Ug12 and UG13 which could not be completed due to ethanol water contamination issue. UG12 and ug13 have been emptied out after sending contaminated ethanol for reprocessing. | 4.2 | Maintenance activities reviewed | 1254 | JALANDHAR DEPOT | Internal inspection of UG12 and UG13 to be completed at the earliest | SOD | Marketing | NFZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-05-2000011851ACN-2026-05-4000129958 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129958 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129958 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129958 | AUD-2026-05-2000011851ACN-2026-05-4000129958 | 21 | 21 | 27 | 80 | 0 | -21 | 44 | 41
DINESH KUMAR | 2026-06-10 |  |  | PO issue on M/s Honey well.Hence complied | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129959 | Closed | DINESH KUMAR | 2026-06-10 | Only one project at Location of TAS revamping for which AR is valid till 31.03.2027. Tendering has been completed. Under recap | 4.3 | Project progress reviewed | 1254 | JALANDHAR DEPOT | Location to follow up for issuance of PO on priority | SOD | Marketing | NFZ | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-05-15 | AUD-2026-05-2000011851ACN-2026-05-4000129959 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129959 | 2026-08-21 | 59.7538 | 282 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129959 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129959 | AUD-2026-05-2000011851ACN-2026-05-4000129959 | 21 | 21 | 27 | 80 | 0 | -21 | 37 | 41
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-10 | DIWAKAR KAMLESH KUMAR | 2026-06-10 | Necessary Repair done | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125094 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-10 | Full field round completed (gantry/tank farm/product pump house/siding/control room/Fire Pump House/ TT Parking/security/admin) | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 3708 | VISAKH NBOT | Green gantry wall broken , to be repaired. Insulation mats to be kept properly in MCC room. | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011315ACN-2026-03-4000125094 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125094 | 2026-09-18 17:30 | 31.0247 | 282 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125094 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125094 | AUD-2026-03-2000011315ACN-2026-03-4000125094 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 41
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-10 | DIWAKAR KAMLESH KUMAR | 2026-06-10 | Necessary repair done. Now there is no leakage | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125551 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-10 | Steam leakage observed near Tank 205 pipeline | 6.7 |  | 3708 | VISAKH NBOT | Steam leakage to be immediately rectified | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125551 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125551 | 2026-09-18 17:30 | 31.0247 | 282 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125551 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125551 | AUD-2026-03-2000011315ACN-2026-03-4000125551 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 41
DHAMIJA VINOD KUMAR | 2026-06-11 | NEGI APARNA | 2026-06-11 | Necessary safety trainings and induction training have been provided to contract engineers as per OISD 154. HMEL two days safety trainings and work permit trainings have also been provided and all the 6 contract engineers have passed the validation test of HMEL. | LOCATION VISIT-HMEL MKTG TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011401 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127748 | Closed | NEGI APARNA | 2026-06-11 | Interacted with all officers of the Location and enquired about their respective areas of operation & issue faced, if any. Special emphasis given on new officers, guiding them how to learn, update, innovate & conduct themselves. Advised LIC to formally assign mentors to the new officers for their learning & development. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1187 | HMEL WHITE OIL TERMINAL | Newly appointed Contract Engineers be nurtured in day to day operations of the location | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 2 | CONTRACTOR SAFETY | S2 | F1 | 2026-04-15 | AUD-2026-04-2000011401ACN-2026-04-4000127748 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011401ACN-2026-04-4000127748 | 2026-09-29 13:30 | 20.1913 | 283 | >20 | AUD-2026-04-2000011401 - ACN-2026-04-4000127748 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011401ACN-2026-04-4000127748 | AUD-2026-04-2000011401ACN-2026-04-4000127748 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
DHAMIJA VINOD KUMAR | 2026-06-11 | NEGI APARNA | 2026-06-11 | VTS deviations are being monitored on daily basis and corrective action is being taken regularly. TTs getting blocked in novex arebeing monitored, suitable action against transporters , if any, are being taken regularly. | LOCATION VISIT-HMEL MKTG TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011401 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127749 | Closed | NEGI APARNA | 2026-06-11 | Discussion held on Novex Governance Module, VTS/VA/TAS alerts & their analysis, EM Locking checks & various other issues. All officers were suitably sensitized. | 1.6 | Expectations clearly communicated to officers | 1187 | HMEL WHITE OIL TERMINAL | VTS deviations to be identified and closed on regular basis as per guidelines. | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-15 | AUD-2026-04-2000011401ACN-2026-04-4000127749 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011401ACN-2026-04-4000127749 | 2026-09-29 13:30 | 20.1913 | 283 | >20 | AUD-2026-04-2000011401 - ACN-2026-04-4000127749 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011401ACN-2026-04-4000127749 | AUD-2026-04-2000011401ACN-2026-04-4000127749 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
DHAMIJA VINOD KUMAR | 2026-06-11 | NEGI APARNA | 2026-06-11 | Contract engineers have been provided the necessary fire safety training by HMEL FIRE TEAM as per their guidelines. Further, regular TBT/trainings are being done for enhancing safety culture. TT crew are being provided Fire fighting equipment training on regularbasis and records are being maintained. | LOCATION VISIT-HMEL MKTG TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011401 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128650 | Closed | NEGI APARNA | 2026-06-11 | Yes, officers are aware of operating firefighting equipments themselves. Fire extinguisher was operated by TT crew. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1187 | HMEL WHITE OIL TERMINAL | LIC to ensure training of fire fighting equipments to newly inducted Contract Engineers and refresher trainings to TT Crew | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-04-2000011401ACN-2026-04-4000128650 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011401ACN-2026-04-4000128650 | 2026-09-29 13:30 | 20.1913 | 283 | >20 | AUD-2026-04-2000011401 - ACN-2026-04-4000128650 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011401ACN-2026-04-4000128650 | AUD-2026-04-2000011401ACN-2026-04-4000128650 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
DHAMIJA VINOD KUMAR | 2026-06-11 | NEGI APARNA | 2026-06-11 | TT driver of TT no. PB03BE9177 was imparted fire fighting training and concerned transporter and Direct sales officer was advised to ensure that all MTO/Hexane TT crew must have proper fire extinguishers alongwith valid test certificate. | LOCATION VISIT-HMEL MKTG TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011401 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128651 | Closed | NEGI APARNA | 2026-06-11 | Fire Extinguisher of TT No. PB03BE9177 checked randomly & not found in order. | 2.14 | TT crew fire extinguisher usage checked | 1187 | HMEL WHITE OIL TERMINAL | Safety equipments of all the TTs must be checked and refresher training be imparted to TT crew members. | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-04-2000011401ACN-2026-04-4000128651 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011401ACN-2026-04-4000128651 | 2026-09-29 13:30 | 20.1913 | 283 | >20 | AUD-2026-04-2000011401 - ACN-2026-04-4000128651 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011401ACN-2026-04-4000128651 | AUD-2026-04-2000011401ACN-2026-04-4000128651 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
DHAMIJA VINOD KUMAR | 2026-06-11 | NEGI APARNA | 2026-06-11 | Necessary safety trainings and induction training have been provided to contract engineers as per OISD 154. HMEL two days safety trainings and work permit trainings have also been provided and all the 6 contract engineers have passed the validation test of HMEL. | LOCATION VISIT-HMEL BITUMEN TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011402 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128652 | Closed | NEGI APARNA | 2026-06-11 | Interacted with the Location officer and Contract Engineers and discussed the issues faced by them, if any. | 1.1 | Interaction with all officers (1–1.5 hrs) | 3129 | BATHINDA BIT HMEL | Location officer to nurture newly appointed Contract Engineer in day to day operations of the location | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 2 | CONTRACTOR SAFETY | S2 | F1 | 2026-04-15 | AUD-2026-04-2000011402ACN-2026-04-4000128652 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011402ACN-2026-04-4000128652 | 2026-09-29 17:00 | 20.0455 | 283 | >20 | AUD-2026-04-2000011402 - ACN-2026-04-4000128652 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011402ACN-2026-04-4000128652 | AUD-2026-04-2000011402ACN-2026-04-4000128652 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
GARBYAL LOKENDER | 2026-06-12 | DIGRA SUNIL KUMAR | 2026-06-12 | ALL THE NEW OFFICERS ARE BEING GUIDED BY SENIOR OFFICERS OF THE LOCATION | LOCATION VISIT-JAMMU_17.02.26 | 2026-02-17 | AUD-2026-04-2000011041 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128326 | Closed | DIGRA SUNIL KUMAR | 2026-06-12 | Interacted with all officers of the Location and enquired about their respective areas of operation & issue faced, if any. Special emphasis given on new officers, guiding them how to learn, update, innovate & conduct themselves. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1256 | JAMMU DEPOT | Advised LIC to formally assign mentors to the guide new officers for their learning & development. | SOD | Marketing | NFZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-15 | AUD-2026-04-2000011041ACN-2026-04-4000128326 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011041ACN-2026-04-4000128326 | 2026-09-04 | 45.7538 | 284 | >20 | AUD-2026-04-2000011041 - ACN-2026-04-4000128326 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000011041ACN-2026-04-4000128326 | AUD-2026-04-2000011041ACN-2026-04-4000128326 | 21 | 21 | 26 | 80 | 1 | -4 | 33 | 41
GARBYAL LOKENDER | 2026-06-12 | DIGRA SUNIL KUMAR | 2026-06-12 | TAS AMC LPR HAS BEEN PLACED IN THE MONTH OF APRIL 2026 | LOCATION VISIT-JAMMU_17.02.26 | 2026-02-17 | AUD-2026-04-2000011041 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128327 | Closed | DIGRA SUNIL KUMAR | 2026-06-12 | 1) Discussed about the New Transport Tender LOA and guided about the induction process of TTs. 2) TAS AMC is expiring on 02.04.26. | 1.3 | Pending issues reviewed | 1256 | JAMMU DEPOT | Follow-up to be done with all concerned for placement of TAS AMC. | SOD | Marketing | NFZ | 2026-03-25 | FAILURE TO FOLLOW PROCEDURES | 8 | EMERGENCY | S2 | F4 | 2026-03-25 | AUD-2026-04-2000011041ACN-2026-04-4000128327 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011041ACN-2026-04-4000128327 | 2026-09-04 | 45.7538 | 284 | >20 | AUD-2026-04-2000011041 - ACN-2026-04-4000128327 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000011041ACN-2026-04-4000128327 | AUD-2026-04-2000011041ACN-2026-04-4000128327 | 21 | 21 | 26 | 80 | 1 | -4 | 30 | 41
KOSHLENDRA SINGH YADAV | 2026-06-12 | SINGH YASHDEEP | 2026-06-12 |  | LOCATION VISIT-SANGRUR_18-19.02.26 | 2026-02-19 | AUD-2026-04-2000010746 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128562 | Closed |  |  | Interacted with all officers of the Location and enquired about their respective areas of operation. Special emphasis given on new officers, guiding them how to learn, update, innovate & conduct themselves. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1180 | SANGRUR DEPOT | Advised LIC to formally assign mentors to the new officers for their learning & development. | SOD | Marketing | NFZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-04-2000010746ACN-2026-04-4000128562 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010746ACN-2026-04-4000128562 | 2026-07-17 | 94.7538 | 284 | >20 | AUD-2026-04-2000010746 - ACN-2026-04-4000128562 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010746ACN-2026-04-4000128562 | AUD-2026-04-2000010746ACN-2026-04-4000128562 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 41
KOSHLENDRA SINGH YADAV | 2026-06-12 | SINGH YASHDEEP | 2026-06-12 |  | LOCATION VISIT-SANGRUR_18-19.02.26 | 2026-02-19 | AUD-2026-04-2000010746 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128563 | Closed |  |  | Scrap observed at Location & found it to be already in the process of disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1180 | SANGRUR DEPOT | Physical disposal to be expedited | SOD | Marketing | NFZ | 2026-04-15 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-04-15 | AUD-2026-04-2000010746ACN-2026-04-4000128563 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010746ACN-2026-04-4000128563 | 2026-07-17 | 94.7538 | 284 | >20 | AUD-2026-04-2000010746 - ACN-2026-04-4000128563 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010746ACN-2026-04-4000128563 | AUD-2026-04-2000010746ACN-2026-04-4000128563 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 41
NIDAMARTHI NAGA KIRAN | 2026-06-13 | SATYENDRA CHOURASIA | 2026-05-23 | 5 DCTs Cancellation confirmation from RO's obtained w.r.t. letter dated 12-13.01.2026 | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129552 | Closed | SATYENDRA CHOURASIA | 2026-05-23 | 5 DCTs Cancellation confirmation from RO's | 1.2 | Performance review conducted | 1919 | SECUNDERABAD TERMINAL | 5 DCTs Cancellation confirmation from RO's | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129552 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129552 | 2026-08-06 19:00 | 73.9622 | 285 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129552 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129552 | AUD-2026-05-2000012102ACN-2026-05-4000129552 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 41
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-13 | DIWAKAR KAMLESH KUMAR | 2026-06-13 | During monthly mock drill Mega Phone is being used, Fire Combat team is doing fire fighting at the correct emergency site,Sprinklers are being used as per direction of Fire Chief and other Auxiliary and rescue teams tare reaching site .ope of correct length available. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125083 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-13 | Double contingency scenario not applicable for VNBOT. Single contingency drill conducted. Mock Drill Observations for improvement i) Mega Phone not used by Fire chief ii) Fire in Bay no 10 was declared but fire combat team operated the Foam Monitor on Bay no 11 initially and later directed Bay no 10. iii) delay in operating the sprinklers of adjacent bays for cooling iv) Auxiliary and rescue teams took more time to reach the site v) The rope tied to the Person with SCABA for checking LEL is short in length . | 2.2 | Double contingency scenario simulated; observations recorded | 3708 | VISAKH NBOT | Short comings observed in the fire drill to be improved in next mock drills | SOD | Marketing | SCR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125083 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125083 | 2026-09-18 17:30 | 31.0247 | 285 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125083 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125083 | AUD-2026-03-2000011315ACN-2026-03-4000125083 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 41
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-13 | DIWAKAR KAMLESH KUMAR | 2026-06-13 | Corrective action taken. CBACS system covered with Galvalume sheet and at bottom Height of level on which person stands has been increased. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125088 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-15 | CBAC near TT gantry entrance taking more time in face recognition due to light issues , to be rectified. | 2.8 | Access control systems checked | 3708 | VISAKH NBOT | CBAC near TT Gantry entrance is taking more time to respond which is an issue attending any emergency at TT Gantry | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125088 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125088 | 2026-09-18 17:30 | 31.0247 | 285 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125088 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125088 | AUD-2026-03-2000011315ACN-2026-03-4000125088 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 41
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-13 | DIWAKAR KAMLESH KUMAR | 2026-06-13 | Scrap has been disposed of Vide Invoice No AP0160042130, Billing Document: 9023026495 dt 067-06-26 .quantity 6.62 MT , Invoice amount: INR 234379.24/- | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125095 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-13 | Scrap worth Rs. 1.9 Lakhs disposed and one more RFD for scrap worth Rs. 5.0 Lakhs sent to CPO for floating tender. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 3708 | VISAKH NBOT | to follow up with Zonal CPO for floating of tender. | SOD | Marketing | SCR | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011315ACN-2026-03-4000125095 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125095 | 2026-09-18 17:30 | 31.0247 | 285 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125095 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125095 | AUD-2026-03-2000011315ACN-2026-03-4000125095 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 41
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137937 | Open | G RAMADOSS | 2026-06-16 | 1. Met DRM on 3-6-26 and emphasised on the need to sort the land ownership as well as area for which railway lease rental to be paid dispute at the earliest. 2. Dip Elimination is pending. | 1.3 | Pending issues reviewed | 1777 | Hassan Terminal | 1. Already Hassan Railways have requested District Administration to appoint surveyors for carrying out comprehensive survey. Can expect a result within a month's time. To be completed by JUly 26. 2. Process already started and File Note will be processed by 15-07-26 | SOD | Marketing | SWZ | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000012598ACN-2026-06-4000137937 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137937 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137937 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137937 |  | AUD-2026-06-2000012598ACN-2026-06-4000137937 | 21 |  | 27 | 80 | 1 | 2 | 48
|  |  |  | Under Compliance | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137938 | Open | G RAMADOSS | 2026-06-16 | In Feb 2026 visit by RNR, 19 recommendations were made | 1.4 | Earlier action points status checked | 1777 | Hassan Terminal | 5 out of 19 complied. EDC: 30.06.2026 | SOD | Marketing | SWZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000137938 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137938 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137938 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012598ACN-2026-06-4000137938 |  | AUD-2026-06-2000012598ACN-2026-06-4000137938 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137939 | Open | G RAMADOSS | 2026-06-16 | 1 Officer short plus 2 NM employees retiring in June & August. | 1.5 | HQO / Zonal support required identified | 1777 | Hassan Terminal | LIC advised to send email highlighting the manpower shortage so that the same will be taken up with HQO for provising 2 additional Contract Engineers till regular officer is posted. | SOD | Marketing | SWZ | 2026-06-25 |  | 6 |  | S3 | F2 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137939 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137939 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137939 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137939 |  | AUD-2026-06-2000012598ACN-2026-06-4000137939 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137940 | Open | G RAMADOSS | 2026-06-16 | HSD tank inadequate | 1.8 | Improvement plans discussed | 1777 | Hassan Terminal | Advised location to send proposal for additional 10 TKL HSD tank | SOD | Marketing | SWZ | 2026-06-25 |  | 1 |  | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137940 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137940 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137940 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012598ACN-2026-06-4000137940 |  | AUD-2026-06-2000012598ACN-2026-06-4000137940 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137941 | Open | G RAMADOSS | 2026-06-16 | Lux levels checked on 3-6-26 | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1777 | Hassan Terminal | Lux level needs to be improved near ETP,secondary roads, Foam tank shed | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000137941 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137941 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137941 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137941 |  | AUD-2026-06-2000012598ACN-2026-06-4000137941 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137942 | Open | G RAMADOSS | 2026-06-16 | 1) Interacted with security and their awareness on emergency preparedness found to be satisfactory. 2) CBACS server is not workingon 24X7 basis. This is causing discontinuity in registering the visitors and both CBACS and Manual system are being sued alternately. 3) When Emergency Gate key box opened and local alarm came, No Main Gate Security responded but Patrolling duty security responded without knowing the situation. M/Gate security to be sensitised to be alert and respond instentaneously | 2.4 | Security alertness checked (night-halt / surprise checks) | 1777 | Hassan Terminal | 1) CBACS Server issue to be sorted incluidng the network connectivity so that 100% registration of visitors is done through CBACS itself and consistency has to be maintained. 2) Training to security staff to be intensified to respond to all forms of alerts inside and outside terminal. | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000137942 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137942 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137942 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137942 |  | AUD-2026-06-2000012598ACN-2026-06-4000137942 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137943 | Open | G RAMADOSS | 2026-06-16 | 4 CCTVs are not working | 2.6 | CCTV functioning checked | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-06-25 |  | 8 |  | S4 | F2 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137943 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137943 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137943 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137943 |  | AUD-2026-06-2000012598ACN-2026-06-4000137943 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137944 | Open | G RAMADOSS | 2026-06-16 | 37 out of 41 are wokring | 2.7 | VA alerts checked / analysed | 1777 | Hassan Terminal | 4 cameras to be rectified | SOD | Marketing | SWZ | 2026-06-25 |  | 8 |  | S4 | F2 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137944 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137944 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137944 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137944 |  | AUD-2026-06-2000012598ACN-2026-06-4000137944 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Complied | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137945 | Open | G RAMADOSS | 2026-06-16 | Checked open patch HCD of TK-102 alarm triggered in Control room, main gate and local hooter also activated, Storm water dyke valveopened for TK-102 local hooter activated, alarm trigerred in control room and main gate | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1777 | Hassan Terminal | HCD integration of TK-302 to be completed | SOD | Marketing | SWZ | 2026-06-30 |  | 8 |  | S4 | F2 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000137945 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137945 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137945 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137945 |  | AUD-2026-06-2000012598ACN-2026-06-4000137945 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137946 | Open | G RAMADOSS | 2026-06-16 | Officers operated MEFG, Monitor near TK-102 and MEFG near OWS. Naveen operated Tk101 Sprinkler, Aham operated Tk202 HVLR, Gopichandoperated Tk201 MEFG. Officers were able to operate. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1777 | Hassan Terminal | Officers able to operate, Foam generation of MEFG of TK-102 & monitor-15 to be checked, | SOD | Marketing | SWZ | 2026-06-30 |  | 8 |  | S4 | F2 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000137946 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137946 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137946 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137946 |  | AUD-2026-06-2000012598ACN-2026-06-4000137946 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137947 | Open | G RAMADOSS | 2026-06-16 | Location needs to have one security guard with HVD | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1777 | Hassan Terminal | Location to get few persons trained and aid them to take HVD & HAZ license | SOD | Marketing | SWZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-06-2000012598ACN-2026-06-4000137947 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137947 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137947 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137947 |  | AUD-2026-06-2000012598ACN-2026-06-4000137947 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137948 | Open | G RAMADOSS | 2026-06-16 | Checked EM locks using intelligent key for TTs:KA54A0768 ,KA460802 ,KA458712 & KA13AA2028 and found to be ok | 3.1 | TT fittings & discipline checked | 1777 | Hassan Terminal | 1. Additional latch to be provided for TTs inside locking box. 2. Tyres of Trucks entering into premises to be checked at parkinggate and corrective action to be intimated to drivers. Tyres of KA 45 8712 and KA 06 AB 7296 to be changed. 3. Speed limit of trucks 10 KMPH to be maintained | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137948 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137948 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137948 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137948 |  | AUD-2026-06-2000012598ACN-2026-06-4000137948 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137949 | Open | G RAMADOSS | 2026-06-16 | Few TTs checked for post fill Dips. In KA46A0832/Puradamma Tpt- Comp2-10L, Comp3-20L excess observed. Removed the excess. | 3.2 | Post-loading dip checks verified | 1777 | Hassan Terminal | Asked LIC & TAS officer to get the bay thoroughly checked for MFM accuracy and get it recalibrated if required. If TT is faulty, get the TT recalibrated | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000137949 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000137949 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000137949 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000137949 |  | AUD-2026-06-2000012598ACN-2026-06-4000137949 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138550 | Open | G RAMADOSS | 2026-06-16 | There are pending Route deviations to be corrected. Speed violations are on the higher side. | 3.3 | VTS deviations reviewed | 1777 | Hassan Terminal | All pending routes to be corrected in a timebound manner. Counselling and if required ITDG action to be initiated for controlling and achieving Nil in speed violations. | SOD | Marketing | SWZ | 2026-06-30 |  | 8 |  | S4 | F2 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000138550 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138550 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138550 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138550 |  | AUD-2026-06-2000012598ACN-2026-06-4000138550 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138551 | Open | G RAMADOSS | 2026-06-16 | Checked EM locks using intelligent key for 1. KA13AA2231-EM HE34875 & HE34876 --> Ok 2. KA10A5319- EM HE5631 & HE 5632 --> Ok 3. KA46A0832- EM HE31223 & HE31224 --> Ok 4. KA11C2511 - EM 27031-OK & HE31343-Not OK | 3.5 | EM Lock SOP compliance verified | 1777 | Hassan Terminal | Not OK EM Lock to be replaced to the TT with a Joint Inspection Report and defective EM Lock to be sent to M/s. Sterna, Coimbatore for investigation and report to be submitted | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000138551 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138551 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138551 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138551 |  | AUD-2026-06-2000012598ACN-2026-06-4000138551 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138552 | Open | G RAMADOSS | 2026-06-16 | Yes Records maintained. However, physical verification of Ethanol TT dip rod to be done for each TT. There is abnormal variation between MFM reading and tank dip levels | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1777 | Hassan Terminal | Same to be checked and necessary CAPA to be made so that both readings are matching | SOD | Marketing | SWZ | 2026-06-20 |  | 9 |  | S3 | F3 | 2026-06-20 | AUD-2026-06-2000012598ACN-2026-06-4000138552 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138552 | 2026-09-22 17:00 | 27.0455 | 292 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138552 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138552 |  | AUD-2026-06-2000012598ACN-2026-06-4000138552 | 21 |  | 27 | 80 | 1 | 2 | 42
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138553 | Open | G RAMADOSS | 2026-06-16 | Water level variation is observed which needs to be rectified | 3.7 | Inventory physical dip of minimum two tanks taken | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-06-30 |  | 8 |  | S4 | F2 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000138553 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138553 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138553 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138553 |  | AUD-2026-06-2000012598ACN-2026-06-4000138553 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138554 | Open | G RAMADOSS | 2026-06-16 | Yes, Manual dips are posting in view of round the clock operations, month end. | 3.1 | TFMS/SAP reconciliation checked | 1777 | Hassan Terminal | To keep the number of tanks for which manual dips to be updated in view of PLT receipts to bare minimum | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000138554 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138554 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138554 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138554 |  | AUD-2026-06-2000012598ACN-2026-06-4000138554 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138555 | Open | G RAMADOSS | 2026-06-16 | Daily report of MFM Vs BCU totalizer being maintained, K-Factor changes report checked and no abnormalities found. Local loading details being maintained. Checked seals of BCU,MFM of Bay-06 and K-factors of MFMs matching with calibration certificate | 3.11 | MFM vs BCU totalizer comparison checked | 1777 | Hassan Terminal | While verifying the TAS Log Book, few days before 4-6-26 (Day of visit), it was noticed KA 13 C8848 had a contamination of MS compartment and 1298 L of HSD gone into MS compartment. As a mitigation measure, location has unloaded the entire compartment product (contaminated) into to UG Horizontal tank. THis was not the right procedure and in effect, the entire UG tank has become contaminated. Location (LIC & PLT officer) to look into this, take QC help and mitigate the entire tank product without blocking the same. | SOD | Marketing | SWZ | 2026-06-20 |  | 9 |  | S3 | F3 | 2026-06-20 | AUD-2026-06-2000012598ACN-2026-06-4000138555 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138555 | 2026-09-22 17:00 | 27.0455 | 292 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138555 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138555 |  | AUD-2026-06-2000012598ACN-2026-06-4000138555 | 21 |  | 27 | 80 | 1 | 2 | 42
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138556 | Open | G RAMADOSS | 2026-06-16 | Local loading observed for the quarterly prover verification . Records are being maintained | 3.14 | Local loading checks (if applicable) | 1777 | Hassan Terminal | Batch control Log Book: Missing MRPL Batch No/Test Report No/Date & Sign. Record to be complete in all aspects. | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000138556 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138556 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138556 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138556 |  | AUD-2026-06-2000012598ACN-2026-06-4000138556 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138557 | Open | G RAMADOSS | 2026-06-16 | All employees and CWM were found with Coverall. Overall Housekeeping to be improved | 3.15 | Housekeeping & PPE usage checked | 1777 | Hassan Terminal | 1) Gantry cleanliness to be done 2) MFM area tree branches to be trimmed 3) Scrap yard to be cleaned and disposed off 4) Cable drums kept in open atmosphere, to be shifted inside warehouse and to be arranged. | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000138557 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138557 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138557 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138557 |  | AUD-2026-06-2000012598ACN-2026-06-4000138557 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138558 | Open | G RAMADOSS | 2026-06-16 | All points of OISD audit are complied, pending MDSA/SSA points to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1777 | Hassan Terminal | To be complied at the earliest | SOD | Marketing | SWZ | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-06-2000012598ACN-2026-06-4000138558 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138558 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138558 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138558 |  | AUD-2026-06-2000012598ACN-2026-06-4000138558 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138559 | Open | G RAMADOSS | 2026-06-16 | 1. Patch painting work to be carried out for foam marks on TK-201,202,102 2. Survey to be carried out for ensuring flameproofness of all JBs 3. Double valves to be provided for strainers of TT gantry | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1777 | Hassan Terminal | 1. Patch painting work to be carried out for foam marks on TK-201,202,102 2. Survey to be carried out for ensuring flameproofness of all JBs 3. Double valves to be provided for strainers of TT gantry | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012598ACN-2026-06-4000138559 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138559 | 2026-09-22 17:00 | 27.0455 | 302 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138559 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138559 |  | AUD-2026-06-2000012598ACN-2026-06-4000138559 | 21 |  | 27 | 80 | 1 | 2 | 44
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138560 | Open | G RAMADOSS | 2026-06-16 | Reviewed progress of 2 current projects related to Bottom Loading and VHF sets procurement | 4.3 | Project progress reviewed | 1777 | Hassan Terminal | To complete the ongoing projects within the agreed timelines | SOD | Marketing | SWZ | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-06-2000012598ACN-2026-06-4000138560 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138560 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138560 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012598ACN-2026-06-4000138560 |  | AUD-2026-06-2000012598ACN-2026-06-4000138560 | 21 |  | 27 | 80 | 1 | 2 | 48
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138561 | Open | G RAMADOSS | 2026-06-16 | Few lots were hetting disposed off. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1777 | Hassan Terminal | To make location scrap free by 30.09.2026. Monthly progress to be updated to Zone | SOD | Marketing | SWZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-06-2000012598ACN-2026-06-4000138561 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138561 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138561 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138561 |  | AUD-2026-06-2000012598ACN-2026-06-4000138561 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138562 | Open | G RAMADOSS | 2026-06-16 | Hazard Validity, W&M and TT Gantry Bay calibration details to be updated in LIC cabin | 6.1 | Updation of various statutory renewal dates in formation in LIC cabin | 1777 | Hassan Terminal | To be done timely | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000138562 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138562 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138562 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138562 |  | AUD-2026-06-2000012598ACN-2026-06-4000138562 | 21 |  | 27 | 80 | 1 | 2 | 43
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138563 | Open | G RAMADOSS | 2026-06-16 | Check MFM calibration is overdue | 6.2 | PLT Receipt Check MFM Calibration | 1777 | Hassan Terminal | To be done @FCRI, Palghat immediately | SOD | Marketing | SWZ | 2026-08-15 |  | 16 |  | S4 | F4 | 2026-08-15 | AUD-2026-06-2000012598ACN-2026-06-4000138563 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138563 | 2026-09-22 17:00 | 27.0455 | 348 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138563 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | HIGH | AUD-2026-06-2000012598ACN-2026-06-4000138563 |  | AUD-2026-06-2000012598ACN-2026-06-4000138563 | 21 |  | 27 | 80 | 1 | 2 | 50
|  |  |  | Pending | HASSAN_TML_Q1_SR.MGMT INSPECTION | 2026-06-04 18:00 | AUD-2026-06-2000012598 | 2026-06-03 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138564 | Open | G RAMADOSS | 2026-06-16 | Sno Electrician's Validity expired on 31.03.2026 | 6.3 | Electrician License Validity | 1777 | Hassan Terminal | Validity of Licenses to be checked, updated and to be ensured | SOD | Marketing | SWZ | 2026-06-25 |  | 9 |  | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012598ACN-2026-06-4000138564 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012598ACN-2026-06-4000138564 | 2026-09-22 17:00 | 27.0455 | 297 | >20 | AUD-2026-06-2000012598 - ACN-2026-06-4000138564 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012598ACN-2026-06-4000138564 |  | AUD-2026-06-2000012598ACN-2026-06-4000138564 | 21 |  | 27 | 80 | 1 | 2 | 43
[5 empty] | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138571 | Open |  |  | Lux level checked on 09.05.2026 record reviewed. Values in tank farm area were found not meeting the standard requirement | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1797 | GULBARGA NEW IRD | Lux level to be improved at Tank Farm Area | SOD | Marketing | SWZ | 2026-07-31 |  | 8 |  | S4 | F2 | 2026-07-31 | AUD-2026-06-2000013300ACN-2026-06-4000138571 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138571 | 2026-08-19 18:00 | 61.0038 | 333 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138571 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013300ACN-2026-06-4000138571 |  | AUD-2026-06-2000013300ACN-2026-06-4000138571 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138581 | Open |  |  | All OISD points are complied. Pending MDSA/SSA points to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1797 | GULBARGA NEW IRD | Location to expediate the closure of Pending MDSA/SSA points.MDSA pending observations: 8 and SSA pending points: 6 | SOD | Marketing | SWZ | 2026-09-30 |  | 8 |  | S4 | F2 | 2026-09-30 | AUD-2026-06-2000013300ACN-2026-06-4000138581 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138581 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138581 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013300ACN-2026-06-4000138581 |  | AUD-2026-06-2000013300ACN-2026-06-4000138581 | 21 |  | 27 | 80 | 5 | 5 | 57
NIDAMARTHI NAGA KIRAN | 2026-06-16 | SATYENDRA CHOURASIA | 2026-05-23 | NPCB projects are being closed in given time frame. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123666 | Closed | SATYENDRA CHOURASIA | 2026-05-23 | Yes. NPCB projects are reviewed & advised location complete the jobs within timelines. | 4.2 | Maintenance activities reviewed | 1919 | SECUNDERABAD TERMINAL | NPCB projects to be completed within given timelines | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011062ACN-2026-03-4000123666 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123666 | 2026-08-06 19:00 | 73.9622 | 288 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123666 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123666 | AUD-2026-03-2000011062ACN-2026-03-4000123666 | 21 | 21 | 26 | 80 | 1 | -12 | 31 | 42
NIDAMARTHI NAGA KIRAN | 2026-06-16 | SATYENDRA CHOURASIA | 2026-05-23 | PM orders are being closed in given time frame. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123667 | Closed | SATYENDRA CHOURASIA | 2026-05-23 | PM orders are being closed in month end. Advised location to complete PM orders as per given time frame. | 4.3 | Project progress reviewed | 1919 | SECUNDERABAD TERMINAL | Advised location to complete PM orders as per given time frame. | SOD | Marketing | SCR | 2026-01-27 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-01-27 | AUD-2026-03-2000011062ACN-2026-03-4000123667 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123667 | 2026-08-06 19:00 | 73.9622 | 288 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123667 | 532 | 8294 | 21 | 8294 | 265 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123667 | AUD-2026-03-2000011062ACN-2026-03-4000123667 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 42
NIDAMARTHI NAGA KIRAN | 2026-06-16 | SATYENDRA CHOURASIA | 2026-05-23 | Emergency Gate Key hooter working, rectified. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129555 | Closed | SATYENDRA CHOURASIA | 2026-05-23 | Security alertness was checked, and the opening of the emergency gate by security personnel was inspected. It was observed that no alarm was triggered while removing the emergency gate key. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1919 | SECUNDERABAD TERMINAL | Emergency Gate Key alarm not working , to be rectified | SOD | Marketing | SCR | 2026-05-20 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129555 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129555 | 2026-08-06 19:00 | 73.9622 | 288 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129555 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129555 | AUD-2026-05-2000012102ACN-2026-05-4000129555 | 21 | 21 | 27 | 80 | 1 | -12 | 38 | 42
NIDAMARTHI NAGA KIRAN | 2026-06-16 | SATYENDRA CHOURASIA | 2026-05-23 | 5 DCTs Cancellation confirmation from RO's obtained w.r.t. letter dated 12-13.01.2026 | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129568 | Closed | SATYENDRA CHOURASIA | 2026-05-23 | DCT TT induction Pending | 6.7 |  | 1919 | SECUNDERABAD TERMINAL | DCT induction status – 5 DCTs liable for rejection | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129568 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129568 | 2026-08-06 19:00 | 73.9622 | 288 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129568 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129568 | AUD-2026-05-2000012102ACN-2026-05-4000129568 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 42
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-16 | DIWAKAR KAMLESH KUMAR | 2026-06-16 | PLT taken in TK203 on – 09.08.2025 Qty – 3192.195 kl ticket no - 2025_26044 Doc no – 4908496829. Qty utilised in VNBOT – 2038.490 kl in bunkering and TT loading. Qty back pumped to VR – 1153.704 kl on 23.04.2026 Doc no – 4904583086. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125080 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Pending Issues reviewed . | 1.3 | Pending issues reviewed | 3708 | VISAKH NBOT | To follow up with VR for correction of offspec product of tank | SOD | Marketing | SCR | 2026-04-15 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-15 | AUD-2026-03-2000011315ACN-2026-03-4000125080 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125080 | 2026-09-18 17:30 | 31.0247 | 288 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125080 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125080 | AUD-2026-03-2000011315ACN-2026-03-4000125080 | 21 | 21 | 26 | 80 | 2 | 1 | 33 | 42
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-16 | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Project no Project Title Start date End date Status SOD-241835 FE digital display -VNBOT 01-04-2024 31-03-2026 Closed SOD-242148 UPGRAD OF HONEYWELL 01-04-2024 31-03-2026 Closed MAKE CIU 880 TO 888 SOD-251613 VNBOT_INCREASING 01-04-2025 31-03-2026 Closed FIRE BREAK WALL HWIGHT | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125079 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Performance review done. NPCB projects to be completed within time and no AR extension | 1.2 | Performance review conducted | 3708 | VISAKH NBOT | Three ARs to be closed by 31.03.2026 | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125079 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125079 | 2026-09-18 17:30 | 31.0247 | 288 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125079 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125079 | AUD-2026-03-2000011315ACN-2026-03-4000125079 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 42
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-16 | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Water sensor cleaned. Now the reading is matching. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125090 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Tank 210 and Tank 211 Physical dip checked. TK 210 physical dip 1533.6 cms(O+W) versus TAS dip of 1533.8 cms and water dip of 37.1 against TAS water dip of 16.0 cms. TK 211 Physical dip 1403.1 cms(O+W) and TAS dip of 1403.4 cms and water dip of 6.7 cms against TAS water dip of 4.0 cms. | 3.7 | Inventory physical dip of minimum two tanks taken | 3708 | VISAKH NBOT | To take UP with TAS vendor for Tanks water dip correction. | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125090 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125090 | 2026-09-18 17:30 | 31.0247 | 288 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125090 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125090 | AUD-2026-03-2000011315ACN-2026-03-4000125090 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 42
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-16 | DIWAKAR KAMLESH KUMAR | 2026-06-13 | LOTO provided | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125099 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-13 | DG control panel under maintenance , LOTO not provided | 6.5 |  | 3708 | VISAKH NBOT | LOTO to be provied | SOD | Marketing | SCR | 2026-03-11 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-11 | AUD-2026-03-2000011315ACN-2026-03-4000125099 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125099 | 2026-09-18 17:30 | 31.0247 | 288 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125099 | 532 | 8294 | 21 | 8294 | 222 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125099 | AUD-2026-03-2000011315ACN-2026-03-4000125099 | 21 | 21 | 26 | 80 | 2 | 1 | 28 | 42
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137537 | Open |  |  |  | 1.4 | Earlier action points status checked | 1892 | KOZHIKODE DEPOT | Pending observations - Action is to be taken urgently on below pending recommendations and Complied points are to be closed in SAP. Total points are pending for complaince : xx / xxx 1. Advised location to procure agreement copies of all transporters and DCT's and confirm that all SD are accounted properly. Conducttrainings of DCT (Sales area vice ) & Transporters 2. One officer of location attended LFT for one day. Officer has to be nominated for the complete training - All the officers are to be attend LFT in subsequent batches 3. Follow up with PESO for permission and railways for exemption for demmurage 4. One experienced Officer required. 5. Route corrections to be regularly checked and done in coordination with sales officers. 6. Location to close all NPCB within timelines. 7. One pending point related to SCM to be complied by 15-03-2026 8. Lighting inporvement to be completed by 10.03.2026 9.One CCTV is not working - to be attended 10. Continue monitoring Foam (AFFF and ARAFF) inventory as per OISD requirment 11. HCD at TK2 dyke is sent for rectification. 12. Driver cabin shall have metal sheet in the backside in place of galss window. Location to ensure no tt with glass window ispermitted for loading 13. Patch painting and painting under side of wind girder to be carried out on TK-2. TK1 full painting to be done 14. Location isadvised to have grease application on TSV flange bolts and other rusted flanges | SOD | Marketing | CZR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137537 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137537 | 2026-09-17 16:00 | 32.0872 | 394 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137537 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137537 |  | AUD-2026-06-2000013060ACN-2026-06-4000137537 | 21 |  | 27 | 80 | 2 | -4 | 57
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137538 | Open |  |  | 2. Experienced manpower at location 2. Renwal of Agreement with MRPL 3. Common AMC POs for maintenance services | 1.5 | HQO / Zonal support required identified | 1892 | KOZHIKODE DEPOT | 1. One EO employee reported at location in 1st week of June 2026 2. Agreement with MRPL is to be renewed. As existing agreement validity is till 3. AMC for pumps and Fire Engines maintenance common PO will be helpful | SOD | Marketing | CZR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137538 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137538 | 2026-09-17 16:00 | 32.0872 | 394 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137538 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137538 |  | AUD-2026-06-2000013060ACN-2026-06-4000137538 | 21 |  | 27 | 80 | 2 | -4 | 57
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137539 | Open |  |  | Random compliances reviewed | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1892 | KOZHIKODE DEPOT | Maintain a register of compliances for all satutory licenses with applicable clauses 1. Registration and amendment of labor license in Shram Suvidha Portal. Job completion and commencement notifications are to be updated timely. 2. ETP regualr operation log book to be maintained 3. CCTV verification by DSO / LIC at periodic intervals is to be maintained 4. Start recoding field observations in E dairy portal as per KPI for the year 5. Hazardous waste storage shed to be maintained. 6. Unwanted and scrap items are to be stored at one place. Take action for timely disposal, from depo premises and rly siding area as well. 7. Dip elimination file note renewal as per HQO circular 8. One Fire pump is under maintenance - submit MOC with EDC and take action for timely restoration 9. Open MOCs to be closed as per validity or as soon as jobs are completed, whichever is earlier. | SOD | Marketing | CZR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137539 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137539 | 2026-09-17 16:00 | 32.0872 | 394 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137539 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137539 |  | AUD-2026-06-2000013060ACN-2026-06-4000137539 | 21 |  | 27 | 80 | 2 | -4 | 57
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137546 | Open |  |  | EM Locks not available for Kasargod MRPL loads | 3.5 | EM Lock SOP compliance verified | 1892 | KOZHIKODE DEPOT | EM locks for MRPL loads through Kasargod depo. KMS box and Card readers are installed. Balance works are to be handled urgently to ensure all loads pf Kasargod MRPL are with EM locks | SOD | Marketing | CZR | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013060ACN-2026-06-4000137546 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137546 | 2026-09-17 16:00 | 32.0872 | 302 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137546 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137546 |  | AUD-2026-06-2000013060ACN-2026-06-4000137546 | 21 |  | 27 | 80 | 2 | -4 | 44
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137549 | Open |  |  | Location has approved TFMS -SAP integration file note. Sustence of dip elimination file note approval is dated . Needs to be renewed as per HQO circular. | 3.10 | TFMS/SAP reconciliation checked | 1892 | KOZHIKODE DEPOT | Dip elimination file note approvals are to be renewed urgently. | SOD | Marketing | CZR | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013060ACN-2026-06-4000137549 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137549 | 2026-09-17 16:00 | 32.0872 | 302 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137549 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137549 |  | AUD-2026-06-2000013060ACN-2026-06-4000137549 | 21 |  | 27 | 80 | 2 | -4 | 44
[5 empty] | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138600 | Open |  |  | House keeping is well maintained at terminal. Observed workman using PPE`s. Security briefing at Gate. Interacted with SG regardingof entry management for licensed area | 3.15 | Housekeeping & PPE usage checked | 1892 | KOZHIKODE DEPOT | 1. Upkeep of calibration shed and 1st floor / terrace of admin /control room building to be improeved. 2. To place dust bins nearTT parking entry gate for collection of empty bottles and other waste material. 3. Location to display PPE Matrix prominently 4. Rust formation observed for Gantry structure, take action suitably | SOD | Marketing | CZR | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013060ACN-2026-06-4000138600 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000138600 | 2026-09-17 16:00 | 32.0872 | 302 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000138600 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000138600 |  | AUD-2026-06-2000013060ACN-2026-06-4000138600 | 21 |  | 27 | 80 | 2 | -4 | 44
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137956 | Open |  |  | Close follow up with MRPL executing the plan of Hook up arrangement for MS PLT ,what we have discussed with MRPL Team for commissioning the same by July 2026. | 1.6 | Expectations clearly communicated to officers | 1775 | BENGALURU TERMINAL | Close follow up with MRPL executing the plan of Hook up arrangement for MS PLT ,what we have discussed with MRPL Team for commissioning the same by July 2026. | SOD | Marketing | SWZ | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-06-2000013105ACN-2026-06-4000137956 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137956 | 2026-09-24 17:00 | 25.0455 | 333 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137956 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137956 |  | AUD-2026-06-2000013105ACN-2026-06-4000137956 | 21 |  | 27 | 80 | 0 | 0 | 48
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137957 | Open |  |  | Rationalisation of number of registers maintained by security at entry can be looked into for effective controls at Security Main Gate | 2.4 | Security alertness checked (night-halt / surprise checks) | 1775 | BENGALURU TERMINAL | Rationalisation of number of registers maintained by security at entry can be looked into for effective controls at Security Main Gate | SOD | Marketing | SWZ | 2026-07-15 |  | 4 |  | S2 | F2 | 2026-07-15 | AUD-2026-06-2000013105ACN-2026-06-4000137957 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137957 | 2026-09-24 17:00 | 25.0455 | 317 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137957 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137957 |  | AUD-2026-06-2000013105ACN-2026-06-4000137957 | 21 |  | 27 | 80 | 0 | 0 | 46
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137959 | Open |  |  | Sterna key resolution for new retail outlets | 3.1 | TT fittings & discipline checked | 1775 | BENGALURU TERMINAL | Sterna key resolution for new retail outlets | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013105ACN-2026-06-4000137959 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137959 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137959 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137959 |  | AUD-2026-06-2000013105ACN-2026-06-4000137959 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137960 | Open |  |  | Location to reconcile with Sterna and take up with SOs for recovery of dormant keys which are mentioned below. Sterna has informed that their management is not approving issuance of fresh keys when the number of dormant keys with location is so high. | 3.5 | EM Lock SOP compliance verified | 1775 | BENGALURU TERMINAL | Location to reconcile with Sterna and take up with SOs for recovery of dormant keys which are mentioned below. Sterna has informed that their management is not approving issuance of fresh keys when the number of dormant keys with location is so high. | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013105ACN-2026-06-4000137960 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137960 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137960 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137960 |  | AUD-2026-06-2000013105ACN-2026-06-4000137960 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137962 | Open |  |  | 1. The area below foam pourer in Tank 20 (HSD) appears to be rusted, same to be attended immediately 2. Torn-off wind socks to be replaced immediately and adequate stock to be kept. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1775 | BENGALURU TERMINAL | 1. The area below foam pourer in Tank 20 (HSD) appears to be rusted, same to be attended immediately 2. Torn-off wind socks to be replaced immediately and adequate stock to be kept. | SOD | Marketing | SWZ | 2026-07-15 |  | 4 |  | S2 | F2 | 2026-07-15 | AUD-2026-06-2000013105ACN-2026-06-4000137962 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137962 | 2026-09-24 17:00 | 25.0455 | 317 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137962 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137962 |  | AUD-2026-06-2000013105ACN-2026-06-4000137962 | 21 |  | 27 | 80 | 0 | 0 | 46
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137963 | Open |  |  | Grease stain marks on tanks on which thickness test were carried out are giving shabby look (At least in 3 AG tanks) and the same have to be cleaned immediately | 4.2 | Maintenance activities reviewed | 1775 | BENGALURU TERMINAL | Grease stain marks on tanks on which thickness test were carried out are giving shabby look (At least in 3 AG tanks) and the same have to be cleaned immediately | SOD | Marketing | SWZ | 2026-07-15 |  | 4 |  | S2 | F2 | 2026-07-15 | AUD-2026-06-2000013105ACN-2026-06-4000137963 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137963 | 2026-09-24 17:00 | 25.0455 | 317 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137963 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137963 |  | AUD-2026-06-2000013105ACN-2026-06-4000137963 | 21 |  | 27 | 80 | 0 | 0 | 46
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137964 | Open |  |  | 1. Commissioning of Tank 30 (Ethanol/Gasohol) to be done on priority, PESO final approval & OISD pre-commissioning report to be expedited 2. Road excavated for maintenance work to be put back to original condition prior to releasing GRN. Any civil/ fabrication jobs done, vendors to be asked to do site clearance before processing their bills | 4.3 | Project progress reviewed | 1775 | BENGALURU TERMINAL | 1. Commissioning of Tank 30 (Ethanol/Gasohol) to be done on priority, PESO final approval & OISD pre-commissioning report to be expedited 2. Road excavated for maintenance work to be put back to original condition prior to releasing GRN. Any civil/ fabrication jobs done, vendors to be asked to do site clearance before processing their bills | SOD | Marketing | SWZ | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013105ACN-2026-06-4000137964 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137964 | 2026-09-24 17:00 | 25.0455 | 302 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137964 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137964 |  | AUD-2026-06-2000013105ACN-2026-06-4000137964 | 21 |  | 27 | 80 | 0 | 0 | 44
[5 empty] | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137965 | Open |  |  | Proper segregation of licensed & de-licensed area to be carried out at TT calibration/ MCC area. Please send NPCB proposal for the same | 6.1 |  | 1775 | BENGALURU TERMINAL | Proper segregation of licensed & de-licensed area to be carried out at TT calibration/ MCC area. Please send NPCB proposal for the same | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013105ACN-2026-06-4000137965 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137965 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137965 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013105ACN-2026-06-4000137965 |  | AUD-2026-06-2000013105ACN-2026-06-4000137965 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137057 | Open |  |  | Pending Issues reviewed. Open irregularities pertaining to TT accidents to be closed . | 1.3 | Pending issues reviewed | 1979 | VIJAYAWADA TERMINAL | Open irregularities pertaining to TT accidents to be closed . | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012864ACN-2026-06-4000137057 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137057 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137057 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137057 |  | AUD-2026-06-2000012864ACN-2026-06-4000137057 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137058 | Open |  |  | Recent review recommendations were reviewed along with pending audit points of SSA & MDSA | 1.4 | Earlier action points status checked | 1979 | VIJAYAWADA TERMINAL | Pending audit points of SSA & MDSA to be completed by 30.12.2026 | SOD | Marketing | SCR | 2026-12-30 |  | 5 |  | S1 | F5 | 2026-12-30 | AUD-2026-06-2000012864ACN-2026-06-4000137058 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137058 | 2026-08-21 16:00 | 59.0872 | 485 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137058 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137058 |  | AUD-2026-06-2000012864ACN-2026-06-4000137058 | 21 |  | 27 | 80 | 12 | 12 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137059 | Open |  |  | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, LIC to record min. 5 e-diary obervations daily | 1.6 | Expectations clearly communicated to officers | 1979 | VIJAYAWADA TERMINAL | LIC to record min. 5 e-diary obervations daily | SOD | Marketing | SCR | 2026-06-05 |  | 5 |  | S1 | F5 | 2026-06-05 | AUD-2026-06-2000012864ACN-2026-06-4000137059 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137059 | 2026-08-21 16:00 | 59.0872 | 277 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137059 | 532 | 8294 | 21 | 8294 | 136 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137059 |  | AUD-2026-06-2000012864ACN-2026-06-4000137059 | 21 |  | 27 | 80 | 12 | 12 | 40
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137064 | Open |  |  | Checked . Out of total 65 CCTV cameras , 2 cameras are not working. One camera cable issue and second camera swicth issue sent for repair. TWG Bay 40 camera is hazy, Railway siding camera angle to be adjusted, | 2.6 | CCTV functioning checked | 1979 | VIJAYAWADA TERMINAL | Location to ensure the 2 nos CCTV put back into service on priority basis. | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137064 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137064 | 2026-08-21 16:00 | 59.0872 | 302 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137064 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137064 |  | AUD-2026-06-2000012864ACN-2026-06-4000137064 | 21 |  | 27 | 80 | 12 | 12 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137066 | Open |  |  | Location does not have any trained personnel with HVD/HZA Endorsement | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1979 | VIJAYAWADA TERMINAL | Location to get security to get HVD/HZA endorsement for movingTT 50–100m in case of any emergency | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-06-2000012864ACN-2026-06-4000137066 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137066 | 2026-08-21 16:00 | 59.0872 | 333 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137066 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137066 |  | AUD-2026-06-2000012864ACN-2026-06-4000137066 | 21 |  | 27 | 80 | 12 | 12 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137070 | Open |  |  | Checked for past 3 months . 88 instances recorded , mostly due to power failure and reset issues | 3.13 | K-factor changes reviewed (if any) | 1979 | VIJAYAWADA TERMINAL | Location to take up with TAS vendor for corrective action | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137070 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137070 | 2026-08-21 16:00 | 59.0872 | 302 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137070 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137070 |  | AUD-2026-06-2000012864ACN-2026-06-4000137070 | 21 |  | 27 | 80 | 12 | 12 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137071 | Open |  |  | MDSA, TAS , SSA , T4S audit compliances reviewed .Advised location to ensure 100 % compliance as per target date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1979 | VIJAYAWADA TERMINAL | 100% Compliance as per target dates | SOD | Marketing | SCR | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-06-2000012864ACN-2026-06-4000137071 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137071 | 2026-08-21 16:00 | 59.0872 | 486 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137071 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137071 |  | AUD-2026-06-2000012864ACN-2026-06-4000137071 | 21 |  | 27 | 80 | 12 | 12 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137072 | Open |  |  | Yes. The two ongoing NPCB projects are reviewed & advised location to complete the jobs within target dates i.e. June end for Automated bay positioning at TTG and Tank 1C Repairs by Dec 2026. | 4.3 | Project progress reviewed | 1979 | VIJAYAWADA TERMINAL | Completion of NPCB projects within timelines | SOD | Marketing | SCR | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-06-2000012864ACN-2026-06-4000137072 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137072 | 2026-08-21 16:00 | 59.0872 | 486 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137072 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137072 |  | AUD-2026-06-2000012864ACN-2026-06-4000137072 | 21 |  | 27 | 80 | 12 | 12 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137073 | Open |  |  | Miscellaneous scrap lying in Scrap Yard RFD to be made. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1979 | VIJAYAWADA TERMINAL | Miscellaneous scrap lying in Scrap Yard RFD to be made. | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137073 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137073 | 2026-08-21 16:00 | 59.0872 | 302 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137073 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137073 |  | AUD-2026-06-2000012864ACN-2026-06-4000137073 | 21 |  | 27 | 80 | 12 | 12 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-06-4000137074 | Open |  |  | MFM based accounting being done for OMC(BPC) PLTs. VVSPL VBS MFM calibration to be done by Pipeline group for MFM based accounting. | 5.1 | MFM based accounting at Pipeline and OMC location | 1979 | VIJAYAWADA TERMINAL | To take up with VVSPL for completion of MFM calibration and commencing of MFM based accounting | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012864ACN-2026-06-4000137074 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137074 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137074 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137074 |  | AUD-2026-06-2000012864ACN-2026-06-4000137074 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137075 | Open |  |  | Emergency Trolley items not as per the name plate , BA set not available, fire proximity suit not available, FLP Torches not available | 6.1 |  | 1979 | VIJAYAWADA TERMINAL | To ensure all items are available as per the name plate on the emergency Trolley | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137075 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137075 | 2026-08-21 16:00 | 59.0872 | 302 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137075 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137075 |  | AUD-2026-06-2000012864ACN-2026-06-4000137075 | 21 |  | 27 | 80 | 12 | 12 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137077 | Open |  |  | Smoke detector system kept off condition. | 6.3 |  | 1979 | VIJAYAWADA TERMINAL | Smoke detector control panel to be shifted from Suryapet Terminal and replace at MCC room | SOD | Marketing | SCR | 2026-06-20 |  | 5 |  | S1 | F5 | 2026-06-20 | AUD-2026-06-2000012864ACN-2026-06-4000137077 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137077 | 2026-08-21 16:00 | 59.0872 | 292 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137077 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137077 |  | AUD-2026-06-2000012864ACN-2026-06-4000137077 | 21 |  | 27 | 80 | 12 | 12 | 42
|  |  |  | Work is in progress. Expected to be completed by 30.10.2026 | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137078 | Open | LOMESH KUMAR PATRE | 2026-07-31 | Tank 1C repair works PO placed , works to be started at the earliest. | 6.4 |  | 1979 | VIJAYAWADA TERMINAL | Ensure completion of TK1C repair works within time i.e. by 31.12.2026 | SOD | Marketing | SCR | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-12-31 | AUD-2026-06-2000012864ACN-2026-06-4000137078 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137078 | 2026-08-21 16:00 | 59.0872 | 486 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137078 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012864ACN-2026-06-4000137078 |  | AUD-2026-06-2000012864ACN-2026-06-4000137078 | 21 |  | 27 | 80 | 12 | 12 | 70
[5 empty] | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138615 | Open |  |  | MRPL to MAPOL pipeline rack bottom PCC not there | 6.3 | PCC below pipeline | 1895 | MANGALORE TERMINAL | MRPL to MAPOL pipeline rack bottom to be made PCC | SOD | Marketing | SWZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013350ACN-2026-06-4000138615 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138615 | 2026-07-29 17:00 | 82.0455 | 486 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138615 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013350ACN-2026-06-4000138615 |  | AUD-2026-06-2000013350ACN-2026-06-4000138615 | 21 |  | 27 | 80 | 2 | 2 | 70
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138618 | Open |  |  | 1.Dip Elimination: Dip elimination is pending and in progress 2.NPCB Projects due as on 30.06.2026: A. Bio-Diesel Closed Loop Line : Mechanical SOR floated and will be finalized within May, 2026. B. SOP BOARD AND SAFETY : TENDER under progress. C. Hubli DC based Lighting: Quotations from vendors has been asked. Will be processed accordingly. D. DYKE IMPERVIOUSNESS: WORK UNDER PROGRESS. E. ELCB for Building circuit : Quotations from vendors has been asked. Will be processed accordingly. F. FLP Hooter with visual siren : Hooter has been supplied. Quotation from TAS vendor asked for integration in current system. G. FOAM Pourer Testing arrangement : One Foam Pourer needs to be replaced. H. Closed Hydrant Line near Ethanol Gantry : Mechanical SOR floated and will be finalized within May, 2026. I. PCC Below Hydrant Line : Work under progress. J. Earth Pit Construction: Work done, Project needs to be closed. K. Cable Tray Replacement : Quotations from vendors has been asked. Will be processed accordingly. | 1.3 | Pending issues reviewed | 1800 | HUBLI DEPOT | 1. Location to expedite and initiate dip elimination filenote at the earliest. 2. To expediate the closure of 12 AR's as per respective AR target date, last AR closing date is 31/10/2026. | SOD | Marketing | SWZ | 2026-10-31 |  | 9 |  | S3 | F3 | 2026-10-31 | AUD-2026-06-2000012499ACN-2026-06-4000138618 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138618 | 2026-09-11 19:30 | 37.9413 | 425 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138618 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138618 |  | AUD-2026-06-2000012499ACN-2026-06-4000138618 | 21 |  | 27 | 80 | 18 | 18 | 61
|  |  |  | RFD initiated. ESA points compliance are under process. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138619 | Open | DEVA DHRUVA | 2026-07-31 | Location complied with the timelined for closure of ESA points except for 12 points. Location also has initiated action for scrap disposal by 30.06.2026 | 1.4 | Earlier action points status checked | 1800 | HUBLI DEPOT | Open ESA points to be closed. Scrap disposal to be initiated by 30.06.2026. | SOD | Marketing | SWZ | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-06-2000012499ACN-2026-06-4000138619 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138619 | 2026-09-11 19:30 | 37.9413 | 394 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138619 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138619 |  | AUD-2026-06-2000012499ACN-2026-06-4000138619 | 21 |  | 27 | 80 | 18 | 18 | 57
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138621 | Open |  |  | HSD tankage is inadequate | 1.8 | Improvement plans discussed | 1800 | HUBLI DEPOT | Location advised to send proposal for additional tankages | SOD | Marketing | SWZ | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138621 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138621 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138621 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012499ACN-2026-06-4000138621 |  | AUD-2026-06-2000012499ACN-2026-06-4000138621 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138622 | Open |  |  | Lux level checked on 23.05.2026. Below Lux level found: Secondary road: 3, 7, 8 & 12 against 10 required Gantry: 170, 78, 89 against 60 Tank Manifold: 28, 31, 29 % 40 against 60 Pump house: 100, 70 & 120 against 100 Gate Entry: 70, 80 and 28 agaist 20 required. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1800 | HUBLI DEPOT | Lux level needs improvement in secondary road and Tank farm area to be done. | SOD | Marketing | SWZ | 2026-12-31 |  | 9 |  | S3 | F3 | 2026-12-31 | AUD-2026-06-2000012499ACN-2026-06-4000138622 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138622 | 2026-09-11 19:30 | 37.9413 | 486 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138622 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138622 |  | AUD-2026-06-2000012499ACN-2026-06-4000138622 | 21 |  | 27 | 80 | 18 | 18 | 70
|  |  |  | All CCTV camera made functional except one PTZ camera, sent for repair. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138624 | Open | DEVA DHRUVA | 2026-07-31 | CCTV Infrastructure: Out of 46 cameras, 40 cameras are functional. Required parts and spare has been received. Engineer awaited forinstallation. | 2.6 | CCTV functioning checked | 1800 | HUBLI DEPOT | All CCTV cameras to be made functional inluding 2 PTZ cameras which are non-functional in VA. | SOD | Marketing | SWZ | 2026-06-30 |  | 9 |  | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138624 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138624 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138624 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138624 |  | AUD-2026-06-2000012499ACN-2026-06-4000138624 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138629 | Open |  |  | Five TTs checked : KA22AA0201, KA22AA7327, KA48A9099, KA22AA7087 and KA545548. Fitting of TTs KA22AA0201 and KA22AA7327 need to be chace as their mentioned fittings in not matching with PESO licenses. | 3.1 | TT fittings & discipline checked | 1800 | HUBLI DEPOT | Location to take appropriate action to avoid any deviation from compliance of statutory. Location to check all TTs with PESO approved tank dimensions and action to be initiated if any violation is observed. | SOD | Marketing | SWZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138629 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138629 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138629 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138629 |  | AUD-2026-06-2000012499ACN-2026-06-4000138629 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138631 | Open |  |  | The reconciliation percentage for Feb 2026 stands at 94%. | 3.1 | TFMS/SAP reconciliation checked | 1800 | HUBLI DEPOT | To improve >95% and sustain | SOD | Marketing | SWZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138631 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138631 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138631 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012499ACN-2026-06-4000138631 |  | AUD-2026-06-2000012499ACN-2026-06-4000138631 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138634 | Open |  |  | Pending ESA/MDSA/SSA points are related to Earth Pits, Sprinkler line etc. are under progress. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1800 | HUBLI DEPOT | Location to expediate the closure of Pending MDSA/SSA points. | SOD | Marketing | SWZ | 2026-12-31 |  | 9 |  | S3 | F3 | 2026-12-31 | AUD-2026-06-2000012499ACN-2026-06-4000138634 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138634 | 2026-09-11 19:30 | 37.9413 | 486 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138634 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012499ACN-2026-06-4000138634 |  | AUD-2026-06-2000012499ACN-2026-06-4000138634 | 21 |  | 27 | 80 | 18 | 18 | 70
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138636 | Open |  |  | Periodical maintenance is being carried out by location | 4.2 | Maintenance activities reviewed | 1800 | HUBLI DEPOT | VRU not functioning due to frequent tripping issues. To identify AMC vendor and put VRU into operation at the earliest. | SOD | Marketing | SWZ | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138636 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138636 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138636 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012499ACN-2026-06-4000138636 |  | AUD-2026-06-2000012499ACN-2026-06-4000138636 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138637 | Open |  |  | Reviewed progress of current projects related to Hydrant Line, Dyke work etc and found satsfactory. | 4.3 | Project progress reviewed | 1800 | HUBLI DEPOT | To complete the projects within the agreed timelines | SOD | Marketing | SWZ | 2026-10-31 |  | 2 |  | S1 | F2 | 2026-10-31 | AUD-2026-06-2000012499ACN-2026-06-4000138637 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138637 | 2026-09-11 19:30 | 37.9413 | 425 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138637 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012499ACN-2026-06-4000138637 |  | AUD-2026-06-2000012499ACN-2026-06-4000138637 | 21 |  | 27 | 80 | 18 | 18 | 61
[5 empty] | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138639 | Open |  |  | Overall housekeeping, look and feel of the location to be improved | 6.1 | Housekeeping | 1800 | HUBLI DEPOT | To take photographs of all areas on monthly basis and compare the improvement | SOD | Marketing | SWZ | 2026-07-31 |  | 2 |  | S1 | F2 | 2026-07-31 | AUD-2026-06-2000012499ACN-2026-06-4000138639 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138639 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138639 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012499ACN-2026-06-4000138639 |  | AUD-2026-06-2000012499ACN-2026-06-4000138639 | 21 |  | 27 | 80 | 18 | 18 | 48
[5 empty] | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138464 | Open |  |  | Pending audit point-Dip elimination is reviewed | 1.3 | Pending issues reviewed | 1999 | DHARAMAPURI TERMINAL | Location shall expedite and complete the dip elimination | SOD | Marketing | SZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013161ACN-2026-06-4000138464 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138464 | 2026-09-11 | 38.7538 | 332 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138464 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013161ACN-2026-06-4000138464 |  | AUD-2026-06-2000013161ACN-2026-06-4000138464 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138467 | Open |  |  | Work regarding audit compliance found to be in progress. | 4.2 | Maintenance activities reviewed | 1999 | DHARAMAPURI TERMINAL | Location shall comply with the same by 30.06.2026 | SOD | Marketing | SZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013161ACN-2026-06-4000138467 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138467 | 2026-09-11 | 38.7538 | 302 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138467 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013161ACN-2026-06-4000138467 |  | AUD-2026-06-2000013161ACN-2026-06-4000138467 | 21 |  | 27 | 80 | 2 | 2 | 44
[5 empty] | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138468 | Open |  |  | Location shall expedite disposal of available scraps | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1999 | DHARAMAPURI TERMINAL | Location shall expedite disposal of available scraps | SOD | Marketing | SZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013161ACN-2026-06-4000138468 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138468 | 2026-09-11 | 38.7538 | 332 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138468 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013161ACN-2026-06-4000138468 |  | AUD-2026-06-2000013161ACN-2026-06-4000138468 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138471 | Open |  |  | Procurement of land for additional TT parking to be expedited. Capex Funds currently freezed by Management. Matter taken up with SOD HQO -F&P | 1.5 | HQO / Zonal support required identified | 1871 | MADURAI DEPOT | Additional TT parking including land purchase & other development need to be done. | SOD | Marketing | SZ | 2026-07-30 |  | 3 |  | S1 | F3 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138471 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138471 | 2026-07-03 | 108.7538 | 332 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138471 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013157ACN-2026-06-4000138471 |  | AUD-2026-06-2000013157ACN-2026-06-4000138471 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138473 | Open |  |  | 07 CCTVs are not working. Backup of 92 days available. | 2.6 | CCTV functioning checked | 1871 | MADURAI DEPOT | Location to take up with vendor and made working of all CCTVs | SOD | Marketing | SZ | 2026-07-30 |  | 4 |  | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138473 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138473 | 2026-07-03 | 108.7538 | 332 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138473 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013157ACN-2026-06-4000138473 |  | AUD-2026-06-2000013157ACN-2026-06-4000138473 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138475 | Open |  |  | Nil abnormal variations. There is a 70 KL unused tank which was in Black oil service and lying idle. | 3.9 | Abnormal variations / unused assets reviewed | 1871 | MADURAI DEPOT | Location advised to put the same on Idle assets/Surplus portal for needy locations. | SOD | Marketing | SZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138475 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138475 | 2026-07-03 | 108.7538 | 332 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138475 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013157ACN-2026-06-4000138475 |  | AUD-2026-06-2000013157ACN-2026-06-4000138475 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138478 | Open |  |  | TFMS and HCD projects work ongoing. | 4.3 | Project progress reviewed | 1871 | MADURAI DEPOT | To take up with Honeywell and AST for stabilising TAS. | SOD | Marketing | SZ | 2026-07-30 |  | 2 |  | S1 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138478 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138478 | 2026-07-03 | 108.7538 | 332 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138478 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013157ACN-2026-06-4000138478 |  | AUD-2026-06-2000013157ACN-2026-06-4000138478 | 21 |  | 27 | 80 | 2 | 2 | 48
[5 empty] | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138480 | Open |  |  | Scrap disposal of UG tank to be completed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1871 | MADURAI DEPOT | Scrap disposal of UG tank to be completed or upload the same on Idle/Surplus assets portal. | SOD | Marketing | SZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138480 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138480 | 2026-07-03 | 108.7538 | 332 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138480 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013157ACN-2026-06-4000138480 |  | AUD-2026-06-2000013157ACN-2026-06-4000138480 | 21 |  | 27 | 80 | 2 | 2 | 48
|  |  |  | Issue taken up withRailways Standing committee. Awaiting for railway reply and appropriate action will be taken. | TIRUNELVELI_IRD_Q1_ZONAL HEAD INSPECTION | 2026-05-06 18:00 | AUD-2026-06-2000013162 | 2026-05-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138483 | Open | BINU K | 2026-09-18 | Railway revised LLF to be paid. Issue taken up withRailways Standing committee. | 1.3 | Pending issues reviewed | 1879 | TIRUNELVELI DEPOT | Location to expedite the payment process in consulation with SZ legal, HQO and railways. | SOD | Marketing | SZ | 2026-07-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013162ACN-2026-06-4000138483 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013162ACN-2026-06-4000138483 | 2026-05-08 | 164.7538 | 332 | >20 | AUD-2026-06-2000013162 - ACN-2026-06-4000138483 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013162ACN-2026-06-4000138483 |  | AUD-2026-06-2000013162ACN-2026-06-4000138483 | 21 |  | 27 | 80 | 0 | 0 | 48
KUMAR CHAKRABORTI ALOK | 2026-06-17 | PATHAK AHELI | 2026-06-16 | 100% usage of c-BACS system & strict adherence to security protocols at entry gate to be ensured | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137958 | Closed | PATHAK AHELI | 2026-06-16 | 100% usage of c-BACS system & strict adherence to security protocols at entry gate to be ensured post Badaun Incident | 2.8 | Access control systems checked | 1775 | BENGALURU TERMINAL | 100% usage of c-BACS system & strict adherence to security protocols at entry gate to be ensured post Badaun Incident | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013105ACN-2026-06-4000137958 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137958 | 2026-09-24 17:00 | 25.0455 | 289 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137958 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013105ACN-2026-06-4000137958 | AUD-2026-06-2000013105ACN-2026-06-4000137958 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 42
KUMAR CHAKRABORTI ALOK | 2026-06-17 | PATHAK AHELI | 2026-06-16 | TTs shifted and 1 TT scrapped | SENIOR MGMT INSP AT BENGALURU TML 2026 | 2026-06-01 | AUD-2026-06-2000013105 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137961 | Closed | PATHAK AHELI | 2026-06-16 | 3 TTs parked at the TT calibration shed is blocking the space (2 are on ITDG action and 1 is Co TT to be scrapped). These TTs to beshifted to a non-obstructive area till they are disposed off | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1775 | BENGALURU TERMINAL | 3 TTs parked at the TT calibration shed is blocking the space (2 are on ITDG action and 1 is Co TT to be scrapped). These TTs to beshifted to a non-obstructive area till they are disposed off | SOD | Marketing | SWZ | 2026-06-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013105ACN-2026-06-4000137961 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013105ACN-2026-06-4000137961 | 2026-09-24 17:00 | 25.0455 | 289 | >20 | AUD-2026-06-2000013105 - ACN-2026-06-4000137961 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013105ACN-2026-06-4000137961 | AUD-2026-06-2000013105ACN-2026-06-4000137961 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 42
SABLE RONAK MOHANKUMAR | 2026-06-17 | SINGH PREETI | 2026-06-17 | Witnessing of Earth Pit testing now being ensured by location, and all all earth pits are being treated suitably for getting minimum resistance. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124909 | Closed | SINGH PREETI | 2026-06-17 | Yes checked and found ok. 7. Following earth pit is tested and found resistance within limits. EP/FS/01 near foam shed: Grid-0.065, Electrode-0.75 EP/DYK-2/23 Near TF-09: Grid-0.31, Electrode-1.7 | 3.16 | Earth pits / boundary / vegetation control checked | 1385 | PALANPUR TERMINAL | Location to ensure witnessing of the earth pit testing activity in field and earthpit treatments to be done to get minimum resistance. | SOD | Marketing | NWR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011223ACN-2026-03-4000124909 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124909 | 2026-08-22 22:00 | 57.8372 | 289 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124909 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124909 | AUD-2026-03-2000011223ACN-2026-03-4000124909 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 42
SABLE RONAK MOHANKUMAR | 2026-06-17 | SINGH PREETI | 2026-06-17 | There is one recommendation of SSA that is pending; Remote operation of all MOVs. Currently few MOVs are not operating in remote. These MOV Actuators have been declared as obsolete by OEM. We have proposed for Capital Budget for procurement of new MOV Actuators. Till the till they are replaced, MOC Approval has been taken for manual operation of MOVs with hand operated valves. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124910 | Closed | SINGH PREETI | 2026-06-17 | Current compliance status of SSA has been discussed with Palanpur team with action plan for ensuring time bound closure of pending 1 Nos recommendations. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011223ACN-2026-03-4000124910 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124910 | 2026-08-22 22:00 | 57.8372 | 289 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124910 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124910 | AUD-2026-03-2000011223ACN-2026-03-4000124910 | 21 | 21 | 26 | 80 | 1 | 1 | 57 | 42
SABLE RONAK MOHANKUMAR | 2026-06-17 | SINGH PREETI | 2026-06-17 | Records are being maintained now for action taken for all VTS Deviations. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124907 | Closed | SINGH PREETI | 2026-06-17 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011223ACN-2026-03-4000124907 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124907 | 2026-08-22 22:00 | 57.8372 | 289 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124907 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011223ACN-2026-03-4000124907 | AUD-2026-03-2000011223ACN-2026-03-4000124907 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 42
SABLE RONAK MOHANKUMAR | 2026-06-17 | SINGH PREETI | 2026-06-17 | Verification of locks using Intelligent Key being done by LIC and records are also being maintained. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124908 | Closed | SINGH PREETI | 2026-06-17 | Yes reviewed and observed that verification is not being done by LIC with provided Intelligent key by HQO. | 3.5 | EM Lock SOP compliance verified | 1385 | PALANPUR TERMINAL | Location to ensure correction action in line with circular for verification within 15 days. LIC to ensure verification of locks using Intelligent Key provided by HQO and record details on provided link by HQO in line with SOP/Circular. | SOD | Marketing | NWR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011223ACN-2026-03-4000124908 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124908 | 2026-08-22 22:00 | 57.8372 | 289 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124908 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011223ACN-2026-03-4000124908 | AUD-2026-03-2000011223ACN-2026-03-4000124908 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | 1. 100 % Dip Checks done in TTG & records updated in SAP. 2. TT shortages are being reviewed & action taken as per ITDG. 3. PCSA - File Note for payment to OISD approved. However, due to non-availability of HVLR & few TAS integration jobs, commissioning of TK-11 is delayed. Necessary budget being sought for completion of the balance jobs. 4. Vendor has been called to lift the balance bitumin lying in Depot. However, vendor has repeatedly delayed citing non availability of any bitumen which can be lifted. 5. Stock lossis reviewed on daily basis & currently the same is within the target. 6. Random checks of EBMS % ensured for loading & unloading trucks. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123967 | Closed | BHUYAN PRARTHANA | 2026-06-18 | Day-to-day operational activities were reviewed. The Junior Executive was advised to get engaged in field for TT dip checking / TT fittings checking. He is also advised to have hand on training and operational knowledge of all the safety critical equipment | 1.1 | Interaction with all officers (1–1.5 hrs) | 1677 | GUWAHATI DEPOT | Location to improve DIP checking by officers at TT gantry for 100% of TTs loaded and maintain records. LIC to carry out surprise check of loaded TTs including bridging TTs. Action to be taken promptly on shortages received in bridging TTs. All safety fittings of TTs to be checked thouroughly. Calibration reverification to be ensured for 100% of TTs. PCSA to be expedited for the MS tank. Bitumen disposal procedure to be closed in coordination with MSTC. Stock loss in MS/ EBMS and HSD to be brought under control . EBMS %agefor both TTs loaded and TT received to be strictly checked by officers and records maintained. LIC to conduct surprise check for both loaded TTs and TTs unloaded and records maintained. | SOD | Marketing | GZR | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123967 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123967 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123967 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123967 | AUD-2026-03-2000011012ACN-2026-03-4000123967 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | PESO Night Operation approval received. PCSA - File Note for payment to OISD approved. However, due to non-availability of HVLR & few TAS integration jobs, commissioning of TK-11 is delayed. Necessary budget being sought for completion of the balance jobs. Actions being taken as per ITDG. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123969 | Closed | BHUYAN PRARTHANA | 2026-06-18 | PESO Night Permission - Application submitted, Inspection schedule awaited from PESO PCSA for TK-11 - Location was advised to expedite it post OISD Audit NRD TTs - To take action as per ITDG Offline VTS in Bridging TTs | 1.3 | Pending issues reviewed | 1677 | GUWAHATI DEPOT | Location to expedite and take corrective action | SOD | Marketing | GZR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-15 | AUD-2026-03-2000011012ACN-2026-03-4000123969 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123969 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123969 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123969 | AUD-2026-03-2000011012ACN-2026-03-4000123969 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | 100 % TT Dip checks are ensured & maintainerd in SAP. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123970 | Closed | BHUYAN PRARTHANA | 2026-06-18 | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1677 | GUWAHATI DEPOT | It is advised to upload the 100%TT dip checking data in SAP. It was also advised to process the TT dip elimination FN immediately after completion of TAS revamping project and analysing the data for 3 months | SOD | Marketing | GZR | 2026-05-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-03-2000011012ACN-2026-03-4000123970 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123970 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123970 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123970 | AUD-2026-03-2000011012ACN-2026-03-4000123970 | 21 | 21 | 26 | 80 | 5 | 5 | 39 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | TT checking being done on regular basis & records are maintained. ITDG actions are taken where deviations are observed. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123979 | Closed | BHUYAN PRARTHANA | 2026-06-18 | TT fitting check being carried for TTs and found satisfactory. | 3.1 | TT fittings & discipline checked | 1677 | GUWAHATI DEPOT | Location to be more stringent in fittings and drawing checks for TTs. Part B check to be done more stringently. | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123979 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123979 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123979 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123979 | AUD-2026-03-2000011012ACN-2026-03-4000123979 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | Coordination being done with Sales Officer & few secondary routes have been created in Shillong & Silchar SA. Further coordination being done with SO to create more secondary routes. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123980 | Closed | BHUYAN PRARTHANA | 2026-06-18 | Review of VTS deviation done on regular basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC | 3.3 | VTS deviations reviewed | 1677 | GUWAHATI DEPOT | Location is advised to create the secondary route wherever applicable | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123980 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123980 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123980 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123980 | AUD-2026-03-2000011012ACN-2026-03-4000123980 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | All open points of MDSA, SSA & Comprehensive audit are being reviewed & complied in a time bound manner. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123985 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | OISD - NIL pending Point SSA - 9 Pending point MDSA - 12 pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1677 | GUWAHATI DEPOT | Location to close the open points at the earliest | SOD | Marketing | GZR | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011012ACN-2026-03-4000123985 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123985 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123985 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123985 | AUD-2026-03-2000011012ACN-2026-03-4000123985 | 21 | 21 | 26 | 80 | 5 | 5 | 31 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | Both projects closed | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123987 | Closed | BHUYAN PRARTHANA | 2026-06-18 | Each Project progress was reviewed and depot ensured to close all the project within timeline. | 4.3 | Project progress reviewed | 1677 | GUWAHATI DEPOT | Location to expedite the closure of TAS revamping project & bottom loading project. | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123987 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123987 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123987 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123987 | AUD-2026-03-2000011012ACN-2026-03-4000123987 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | All records being maintained & certified by PLT officer. IOC MFM vs HPC SAP figures being checked & reviewed by LIC on weekly basis. No abnormality observed. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-03-4000123988 | Closed | BHUYAN PRARTHANA | 2026-06-18 | MFM based accounting is being done. | 5.1 | MFM based accounting at Pipeline and OMC location | 1677 | GUWAHATI DEPOT | PLT operations record keeping to be improved | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123988 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123988 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123988 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123988 | AUD-2026-03-2000011012ACN-2026-03-4000123988 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-18 | BHUYAN PRARTHANA | 2026-06-18 | 1. General Housekeeping being duly reviewed on daily basis & necessary action is taken. 2. Gain & Loss booking being reviewed by LIC on daily basis. Parameters are under limit/target. 3. VTS is available in all the TT. Updation issues are being taken up with source location of bridging (Patna & Bokaro). 4. OLA implemented (> 85 %) except in few exceptional cases along with sequential allocation of TT for bridging loads ensuring equal RTKM distribution. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123989 | Closed | BHUYAN PRARTHANA | 2026-06-18 | 1. Parking Housekeeping and Sanitation 2. Gain Loss Booking review at location 3. VTS non availability / missing in Brigding TTs 4. RTKM mismatch and huge deviation from avg. RTKM for few transporters | 6.1 | Additional Observations | 1677 | GUWAHATI DEPOT | Location is advised to take corrective action | SOD | Marketing | GZR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011012ACN-2026-03-4000123989 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123989 | 2026-09-01 | 48.7538 | 290 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123989 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123989 | AUD-2026-03-2000011012ACN-2026-03-4000123989 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-19 | BHUYAN PRARTHANA | 2026-06-19 | All the project will be completed within scheduled timeframe: 1. OWS collection system with drainage. Tender under TE/CE (completion date: 31.12.2026). 2. Swing ladder installation completed. AR closure under progress. 3. Four side approach road for UG Tanks completed. AR closure under progress. 4. SITC of HCD, ESD Push Button, Hooter, Smoke Detector and its integration with TAS - Job completed. AR closure under progress. 5. Bottom loading bay extension - AR closed | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123968 | Closed | BHUYAN PRARTHANA | 2026-06-19 | Review of officers carried out with respect to KPI and overall location performance with respect to monthly MIS reports. ProjectProgress was not found in line with the timelines. Respective officers was advised to ensure to close the project within the timelines. Close Loop Hydrant line OWS and Drian TAS Revamping project | 1.2 | Performance review conducted | 1677 | GUWAHATI DEPOT | Location to ensure to complete all the project activities within the scheduled timeframe. | SOD | Marketing | GZR | 2026-03-10 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123968 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123968 | 2026-09-01 | 48.7538 | 291 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123968 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123968 | AUD-2026-03-2000011012ACN-2026-03-4000123968 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
TAPAS RANJAN PANDA | 2026-06-19 | BHUYAN PRARTHANA | 2026-06-19 | CBACS turnstile has been made functional & enrolment of officers & contract manpower being done. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123976 | Closed | BHUYAN PRARTHANA | 2026-06-19 | Access control system of the licence entry gate and control room was not functional. Location informed that the vendor M/s Godrej already visited the site and will be rectifying it shortly. | 2.8 | Access control systems checked | 1677 | GUWAHATI DEPOT | Location to closely coordinate with M/s Godrej and ensure 100% functionality of the access control system | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123976 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123976 | 2026-09-01 | 48.7538 | 291 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123976 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123976 | AUD-2026-03-2000011012ACN-2026-03-4000123976 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 42
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139171 | Open |  |  | TT Crews are aware of the eye sight issues. Same is being checked at location during the regular medical health camp.Location not having equipment for checking colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1677 | GUWAHATI DEPOT | Advised location to procure one colour blindness check equipment immediately. | SOD | Marketing | GZR | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013067ACN-2026-06-4000139171 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139171 | 2026-09-01 | 48.7538 | 576 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139171 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139171 |  | AUD-2026-06-2000013067ACN-2026-06-4000139171 | 21 |  | 27 | 80 | 5 | 5 | 83
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139173 | Open |  |  | It was given to understand that the reco is being done on Auto dips only except in case of exception.Recently TFMS equipments are changed.Monitoring are being done through manual dips. | 3.8 | Auto vs Manual reconciliation checked | 1677 | GUWAHATI DEPOT | Advised location to initiate TFMS File note approval for Auto dip posting as confirmed by Location that reading sustainance is achieved. | SOD | Marketing | GZR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-06-2000013067ACN-2026-06-4000139173 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139173 | 2026-09-01 | 48.7538 | 363 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139173 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139173 |  | AUD-2026-06-2000013067ACN-2026-06-4000139173 | 21 |  | 27 | 80 | 5 | 5 | 52
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139176 | Open |  |  | OISD - 29 (21 pending) SSA - 119 (7 pending) Comprehensive Audit - 133 (10 Pending) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1677 | GUWAHATI DEPOT | All pending point to be complied as per Target | SOD | Marketing | GZR | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013067ACN-2026-06-4000139176 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139176 | 2026-09-01 | 48.7538 | 576 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139176 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139176 |  | AUD-2026-06-2000013067ACN-2026-06-4000139176 | 21 |  | 27 | 80 | 5 | 5 | 83
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000139177 | Open |  |  | Yes. 1.For braking ESD glass,no hammer available 2. Near Visitors entrance height of baricade to be increased 3. For DFMD entry separate baggage tray to be kept. 4. Cable entry seal back of MCC room to be done properly 5. bay No-6 open pit to be covered 6.UG tankarea grass needs to be cleaned on regular basis.7.Control room entry to be ensured only through access control. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1677 | GUWAHATI DEPOT | All points to be checked and to be complied. | SOD | Marketing | GZR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013067ACN-2026-06-4000139177 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139177 | 2026-09-01 | 48.7538 | 486 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139177 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139177 |  | AUD-2026-06-2000013067ACN-2026-06-4000139177 | 21 |  | 27 | 80 | 5 | 5 | 70
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000139179 | Open |  |  | Last year Rs 49 lakhs Scrap disposed.2 nos. TT RFD failed,needs to expedite for disposal. other Scrap to be identified. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1677 | GUWAHATI DEPOT | RFD to be made immediately and completion by Dec;26. | SOD | Marketing | GZR | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013067ACN-2026-06-4000139179 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139179 | 2026-09-01 | 48.7538 | 332 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139179 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139179 |  | AUD-2026-06-2000013067ACN-2026-06-4000139179 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000139181 | Open |  |  | Bottom loading arms are not properly parked. | 6.3 |  | 1677 | GUWAHATI DEPOT | Arrangement for Bottom loading arm support to be done at gantry for proper resting of arm. | SOD | Marketing | GZR | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013067ACN-2026-06-4000139181 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139181 | 2026-09-01 | 48.7538 | 332 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139181 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139181 |  | AUD-2026-06-2000013067ACN-2026-06-4000139181 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000139182 | Open |  |  | Water stagnation around gantry area Placement of R2 and KM Box are not placed in convenient place. | 6.4 |  | 1677 | GUWAHATI DEPOT | Water stagnation around gantry area Placement of R2 and KM Box are not placed in convenient place. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139182 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139182 | 2026-09-01 | 48.7538 | 302 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139182 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013067ACN-2026-06-4000139182 |  | AUD-2026-06-2000013067ACN-2026-06-4000139182 | 21 |  | 27 | 80 | 5 | 5 | 44
KUSHAGRA VASHISHTH | 2026-06-20 |  |  | 1. MFM based accounting started at location in March 26'. 2. EDU System made functional. 3. TFMS server made functional with the help of vendor M/S Honeywell. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122043 | Closed | KUSHAGRA VASHISHTH | 2026-06-20 | Three TAS audit points of Feb 2025 not complied. Quotation given by HAIL to be discussed with DGM IS (SJ) | 1.3 | Pending issues reviewed | 1278 | JODHPUR TERMINAL | 1. MFM based accounting not being done for PLT receipt (target 31.03.2026) 2. Driver name announcement system not working (target completion 28.02.2026) 3. TFMS server to be made functional (Target completion 10.03.2026) | SOD | Marketing | NWF | 2026-03-31 | INSTRUMENTATION OR ALARM FAILURES | 3 | PROCESS SAFETY | S3 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122043 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122043 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122043 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122043 | AUD-2026-02-2000010963ACN-2026-02-4000122043 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
KUSHAGRA VASHISHTH | 2026-06-20 |  |  | Bio metric access of TT driver has been made functional and activated with the help of TAS vendor. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122044 | Closed | KUSHAGRA VASHISHTH | 2026-06-20 | Bio metric access of TT driver not done (TAS audit point of Nov 2025) | 1.4 | Earlier action points status checked | 1278 | JODHPUR TERMINAL | Study to be made. Location to revert with necessary support/help required. This point is recurring in last two audits | SOD | Marketing | NWF | 2026-03-31 | INSTRUMENTATION OR ALARM FAILURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122044 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122044 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122044 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122044 | AUD-2026-02-2000010963ACN-2026-02-4000122044 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
KUSHAGRA VASHISHTH | 2026-06-20 |  |  | Location has carried out necessary modification as advised. Location has also carried out GAP analysis with respect to OISD-244, IS3043. One tendor has been floated for modification in earth pits. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122358 | Closed | KUSHAGRA VASHISHTH | 2026-06-20 | Checked three Earth Pits: 1. Earth Pit no. 103: One bolt was fully loose. May be bolt is required to be changed. The plates were having gaps. 2. Earth pit no. 104: Gaps were observed between plates. 3. Earth pit no. 189: The plates were not having any gap. It was found Okay. However, 25x3 mm strip was used for earthing. This is non standard. Additionaly, this 25x 3 mm strip was found corroded and very thin at one place. | 3.16 | Earth pits / boundary / vegetation control checked | 1278 | JODHPUR TERMINAL | As OISD audit of location is due in 2026-27. Location should ensure the following: 1. Make one team with one officer as leader. 2. That officer should learn all aspect of earthing by going through OISD 244, IS 3043. 3. Take two months target for checking and modifying all Earth pits. 4. he should also cross check all Earth pit layout diagram and correct the same as per actual. | SOD | Marketing | NWF | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-02-2000010963ACN-2026-02-4000122358 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122358 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122358 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122358 | AUD-2026-02-2000010963ACN-2026-02-4000122358 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 42
KUSHAGRA VASHISHTH | 2026-06-20 |  |  | fire engine 2 has been repaired with the help of OEM vendor. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122364 | Closed | KUSHAGRA VASHISHTH | 2026-06-20 | Fire engine no. 2 to be repaired. | 6.1 | Fire engine | 1278 | JODHPUR TERMINAL | Pls ensure timely action | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122364 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122364 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122364 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122364 | AUD-2026-02-2000010963ACN-2026-02-4000122364 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
KUSHAGRA VASHISHTH | 2026-06-20 |  |  | All points of comprehensive audit complied. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122365 | Closed | KUSHAGRA VASHISHTH | 2026-06-20 | 14 points of Comprehensive audit to be complied | 6.2 | Safety Audit points | 1278 | JODHPUR TERMINAL | Pls ensure timely action | SOD | Marketing | NWF | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122365 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122365 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122365 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122365 | AUD-2026-02-2000010963ACN-2026-02-4000122365 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
KUSHAGRA VASHISHTH | 2026-06-20 | SAINI JASVINDER SINGH | 2026-04-07 | History cards are updated for now, it is being ensured that all the cards are being updated for every equipment. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122369 | Closed | SAINI JASVINDER SINGH | 2026-04-07 | History card of CCTV, HVLR, RSFPS, Pumps, Tanks, VRU should be updated properly. It was being updated properly upto FY 2021-22. After that, history cards are not being updated properly. | 6.6 | History card | 1278 | JODHPUR TERMINAL | Pls update all details including visit of OEM, any servicing done, any filter changed. Even if material changed is under the scope of CAMC vendor, pls write name of material changed ans associated cost | SOD | Marketing | NWF | 2026-03-10 | LACK OF TRAINING OR COMPETENCY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010963ACN-2026-02-4000122369 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122369 | 2026-09-25 20:45 | 23.8893 | 292 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122369 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122369 | AUD-2026-02-2000010963ACN-2026-02-4000122369 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Training given to All FOC Memebers for proper communication , Recording of Manpower/Visitor count. Double hydrant valve found jammed replaced and now working ok. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122726 | Closed | NAVIN KUMAR | 2026-06-20 | 1. Date 09.03.2026 2. Area of drill conducted: Inside depot premises 3. Scenerio covered: Fire in MS pump strainer 4. Double/single Contingency: Single contingency 5. Obervations : Communications by team to Fire chief to be improved Location to check hose pipe and DH male female coupling in presurraised condition to ensure proper connection. Location to check and verify the sequence of events and shutdown of depot premises. Focus shall be given on correctness of manpower/visitor count during drills. Location to ensure communication to mutual aid member and district authorities. Location to check and verify the cause and effect in field. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122726 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122726 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122726 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122726 | AUD-2026-03-2000011218ACN-2026-03-4000122726 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Camera repaired and As on 20.06.26 all cameras in working condition | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122727 | Closed | NAVIN KUMAR | 2026-06-20 | Total camera 55/ working 50. 5 under repair, sent to vendor. Back up available. | 2.6 | CCTV functioning checked | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011218ACN-2026-03-4000122727 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122727 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122727 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122727 | AUD-2026-03-2000011218ACN-2026-03-4000122727 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | SST conducted for grass cutting staff to wear PPE inside hazardeous area . | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122728 | Closed | NAVIN KUMAR | 2026-06-20 | Non compliance of Fire Extinguisher (TT Unloading) TAS_1146_SOP033_020126_000033 found valid and corrective taken by the location. PPE non compliance TAS_1146_SOP043_020126_000007 closed with comment Grass cutting labour at siding area ...SST conducted. Person found to be entered with PPE inside depot premises and removed in siding area. | 2.7 | VA alerts checked / analysed | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | INSTRUMENTATION OR ALARM FAILURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122728 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122728 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122728 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122728 | AUD-2026-03-2000011218ACN-2026-03-4000122728 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Discussed in Daily gate meeting with TT Crew for proper uses of PPE and SST with Grass cutting staff also conducted for same . | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122734 | Closed | NAVIN KUMAR | 2026-06-20 | Improper usage of PPE by TT crew and grass cutting staff is observed at location. | 3.15 | Housekeeping & PPE usage checked | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-12 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-12 | AUD-2026-03-2000011218ACN-2026-03-4000122734 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122734 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122734 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122734 | AUD-2026-03-2000011218ACN-2026-03-4000122734 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | 1.EP121 clamping done with double bolting and Green wire also removed with proper earthing connection. 2.Concertina coil repaired in common boundary wall. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122735 | Closed | NAVIN KUMAR | 2026-06-20 | 1. Earth pit 121: Improper clamp, single bolt connection of earthstrip. Earthpit cover resting on Green wires. EP 71, had improper connection. EP 69, connected to HMT, found constructed properly, with proper connections. Earthpit no 101, which is due for testing,on 28/03/26, gave results of 1.84 ohms (individual) and 0.03 Ohms (grid), against last test readings of 1.11 ohms and 0.11 Ohms, respectively. 2. Location to provide bottom concertina wire in common boundary wall of depot and siding. | 3.16 | Earth pits / boundary / vegetation control checked | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122735 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122735 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122735 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122735 | AUD-2026-03-2000011218ACN-2026-03-4000122735 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | All Compliances as per planned closure date in FY202526 closed | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122737 | Closed | NAVIN KUMAR | 2026-06-20 | OISD : Total point 22, Pending point: 3, EDC: 15.08.2026 MDSA: Total point 41, Pending point: 13, EDC: 31.12.2026 SSA: Total point 17, Pending point: 3, EDC: 15.08.2026 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1146 | MEERUT DEPOT | Points scheduled for closure in current FY shall be closed. | SOD | Marketing | NUZ | 411354 | LACK OF TRAINING OR COMPETENCY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011218ACN-2026-03-4000122737 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122737 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122737 | 532 | 8294 | 21 | 8294 | -365039 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122737 | AUD-2026-03-2000011218ACN-2026-03-4000122737 | 21 | 21 | 26 | 80 | 0 | 0 | 52208 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Verified the TAS Ethanol Blending Report for a one-week period. Ethanol blending was found to be consistently maintained at 20% across all bays. A sample TAS report is attached for ready reference. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122731 | Closed | NAVIN KUMAR | 2026-06-20 | TT no UP82T5707 was checked for ethanol blending % and blending found 18%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122731 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122731 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122731 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122731 | AUD-2026-03-2000011218ACN-2026-03-4000122731 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Lock of UP14HT4601 of Vansh Oil carrier sent for inspection at Sterna security . (Panchnama record attach) | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122732 | Closed | NAVIN KUMAR | 2026-06-20 | EM locks of following TTs were checked with intelligent key. UP23T6953 of Sony Filling: Both bottom lock (HE1281) and top lock (HE1282) were found ok. UP15FT8488 of RR oil Carrier: Both bottom lock (HE20893) and top lock (HE30894) were found ok. UP15DT8216of Bhatti Oil : Both bottom lock (HE16562) and top lock (HE16703) were found ok. UP15HT5417 of Nitya Parth Transport: Both bottom lock (HE9734) and top lock (HE31739) were found ok. UP14HT4601 of Vansh Oil: Bottom lock (HE29562) found ok. However, top lock (HE29561) found suspected. | 3.5 | EM Lock SOP compliance verified | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | THIRD PARTY ERRORS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122732 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122732 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122732 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122732 | AUD-2026-03-2000011218ACN-2026-03-4000122732 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Ethanol empty TT is being checked by the two officers on regular basis as in line with the HQO circular (sample record attach) | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122733 | Closed | NAVIN KUMAR | 2026-06-20 | UP15ET4413 Dip checked and found ok. Gaps observed in empty TT check by two officer in line with HQO circular. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-12 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-12 | AUD-2026-03-2000011218ACN-2026-03-4000122733 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122733 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122733 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122733 | AUD-2026-03-2000011218ACN-2026-03-4000122733 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | MOHAMMAD MAZHARUDDIN | 2026-03-23 | 1. Leak arrested and recitifed. 2. Pressure guages all around the depot were calibrated by in house facility available at depot. 3. Noted. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122738 | Closed | SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | 1. Leak observed from gland of pump no 15 (MS). 2. With no pump in operation HSD pump suction lines were showing negative pressureand delivery lines were showing pressure of 8.0 Kgf/cm2. 3. Electrical panels found to be kept maintained properly. Electricians also found having required awareness. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122738 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122738 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122738 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122738 | AUD-2026-03-2000011218ACN-2026-03-4000122738 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Project with Target date as 31.03.2026 closed in SAP . | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122739 | Closed | NAVIN KUMAR | 2026-06-20 | Project works related to compliance shall be expedited and timely closure fo project scheduled for closure in current FY shall be ensured. | 4.3 | Project progress reviewed | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 411354 | THIRD PARTY ERRORS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011218ACN-2026-03-4000122739 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122739 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122739 | 532 | 8294 | 21 | 8294 | -365039 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122739 | AUD-2026-03-2000011218ACN-2026-03-4000122739 | 21 | 21 | 26 | 80 | 0 | 0 | 52208 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Scrap items identified from the Asset Master (e-Waste) and miscellaneous scrap lying at HPCL Meerut Depot have been segregated. TheScrap Disposal Committee has been constituted, inspection has been completed, and the disposal process has been initiated in AAROHAN (SIR-PTR No. 1146/26-27/1-2). Expected Date of Completion: 31.12.2026 | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122740 | Closed | NAVIN KUMAR | 2026-06-20 | location to identify and segragate scrap available in scrap yard and initiate disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 411354 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011218ACN-2026-03-4000122740 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122740 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122740 | 532 | 8294 | 21 | 8294 | -365039 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122740 | AUD-2026-03-2000011218ACN-2026-03-4000122740 | 21 | 21 | 26 | 80 | 0 | 0 | 52208 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | LRUT and DCVG for UG sections conducted and no fault found . Inspection of Above ground line done and leakage in hydrant/monitors arrested . | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122741 | Closed | NAVIN KUMAR | 2026-06-20 | Jockey pump starting every 20 minutes in night and around 6 minutes in day | 6.1 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122741 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122741 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122741 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122741 | AUD-2026-03-2000011218ACN-2026-03-4000122741 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Ethanol records updated on daily basis . Sample record attach. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122742 | Closed | NAVIN KUMAR | 2026-06-20 | Sample registers of Ethanol, found not updated after 14/02/26. | 6.2 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-12 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-12 | AUD-2026-03-2000011218ACN-2026-03-4000122742 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122742 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122742 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122742 | AUD-2026-03-2000011218ACN-2026-03-4000122742 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Sprinkler Cleaning done and now found working ok. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122743 | Closed | NAVIN KUMAR | 2026-06-20 | Sprinkler lines of Tk04 were operated. Sprinklers M18-M24 and U34 were found choked. | 6.3 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122743 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122743 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122743 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122743 | AUD-2026-03-2000011218ACN-2026-03-4000122743 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Valve operating platform for TK4 Repaired and fixed properly. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122744 | Closed | NAVIN KUMAR | 2026-06-20 | Valve operating platform of Tk4 was found resting on a MS channel, which has already got moved from position. | 6.4 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122744 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122744 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122744 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122744 | AUD-2026-03-2000011218ACN-2026-03-4000122744 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | The oil leakage was attended and the DG bed and surrounding area were cleaned to remove all oil stains and dirt. Regular inspectionand preventive maintenance are being carried out to prevent recurrence. The 810 kVA DG is serviced by Cummins' authorized service provider, JAKSON on monthly basis. The last service was completed in May 2026, and the service report is attached for ready reference | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122745 | Closed | NAVIN KUMAR | 2026-06-20 | Oil soaked bottom surface under gland area observed in 500 KVA DG. There was leak from 810 KVA DG also. | 6.5 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122745 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122745 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122745 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122745 | AUD-2026-03-2000011218ACN-2026-03-4000122745 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | Practice has been put in place for mandatory inspection of all TT compartments for partition leakage and verification of the proof line of the dip rod in-line with Calibration Chart by the calibration officer prior to water filling and calibration of the TT. Water filling in compartments during TT calibration is being monitored by the officer. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122746 | Closed | NAVIN KUMAR | 2026-06-20 | Verification of MFMs with prover tanks, found as being carried out in presence of officer. Calibration of TTs was also found to be checked after completion of filling water. However, checking of partition leak was not being done. During filling of water in various compartments, no presence of Officer was there. Tallying actual proof line level of dip rods was not being done. | 6.6 |  | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122746 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122746 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122746 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122746 | AUD-2026-03-2000011218ACN-2026-03-4000122746 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Complied. Communication of teams with fire chief has been improved in recent drills. Training has been imprated to all contract workmen for use of equipments for different fire scenerios. Monthly drills are conduted for different scenerios. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122067 | Closed | VERMA RAHUL | 2026-06-20 | Double contingency scenario: 1. Oil leakage in TK24 manifold area 2. Fire in first chamber of ETP | 2.2 | Double contingency scenario simulated; observations recorded | 1128 | MATHURA TERMINAL | 1. Teams to ensure communication with fire chief and coordinate for instructions. 2. Session shall be conducted with contract workmen and fire fighting team members for usage of right equipments as per scenarios - leakage, fire etc. 3. Different scenarios shallbe covered in the monthly drills. | SOD | Marketing | NUZ | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-02-2000010909ACN-2026-02-4000122067 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122067 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122067 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122067 | AUD-2026-02-2000010909ACN-2026-02-4000122067 | 21 | 21 | 26 | 80 | 14 | 13 | 30 | 42
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-06-20 | NAVIN KUMAR | 2026-06-20 | One Security Guard Mr Sanjeev Kumar Having License no:UP1720000002287 identified for same . | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122729 | Closed | NAVIN KUMAR | 2026-06-20 | As of now, No such person is available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1146 | MEERUT DEPOT | Location to identify such person. | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122729 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122729 | 2026-09-25 19:00 | 23.9622 | 292 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122729 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122729 | AUD-2026-03-2000011218ACN-2026-03-4000122729 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Lux level is meeting at all places. Faulty High mast lamps have been repaired. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122068 | Closed | VERMA RAHUL | 2026-06-20 | Lux level: TWPH 160, Road 13, TK07 manifold: 63, 80, TK05 manifold 33,50, TK 17 manifold 41, Gantry Bay no 12 - 78, Bay 9 - 144, admin building 275. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1128 | MATHURA TERMINAL | Location to review LUX level at primary & secondary roads. Faulty lamps of highmast tower to be replaced. | SOD | Marketing | NUZ | 2026-03-30 | INSTRUMENTATION OR ALARM FAILURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-30 | AUD-2026-02-2000010909ACN-2026-02-4000122068 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122068 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122068 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122068 | AUD-2026-02-2000010909ACN-2026-02-4000122068 | 21 | 21 | 26 | 80 | 14 | 13 | 30 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Complied. Both cameras are working. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122069 | Closed | VERMA RAHUL | 2026-06-20 | CCTV Back up available till date: 23 Nov'25. 2 camera (Bay No 9-10, PTZ TK23) out of 71 are not working. CCTV footages of 01.01.26and 23.01.26 were checked randomly for patrolling by Security. Security found as carrying out patrolling properly. | 2.6 | CCTV functioning checked | 1128 | MATHURA TERMINAL | functionality of non working camera shall be restored | SOD | Marketing | NUZ | 2026-03-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-02-2000010909ACN-2026-02-4000122069 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122069 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122069 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122069 | AUD-2026-02-2000010909ACN-2026-02-4000122069 | 21 | 21 | 26 | 80 | 14 | 13 | 30 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | VTS has been revied by officers on daily basis. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122077 | Closed | VERMA RAHUL | 2026-06-20 | Being monitored by zone on daily basis and actions are being taken by location. However, for few routes, correction is required. | 3.3 | VTS deviations reviewed | 1128 | MATHURA TERMINAL | Corrective action to be taken as found and pointed out during random checking by zone and location. | SOD | Marketing | NUZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010909ACN-2026-02-4000122077 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122077 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122077 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122077 | AUD-2026-02-2000010909ACN-2026-02-4000122077 | 21 | 21 | 26 | 80 | 14 | 13 | 31 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Complied. Most of TT's are coming in Locked conditions, exceptionally where one lock is applied by dealer due to system issues details of such dealers is shared with sales team for propoer locking in future. Letter from dealer also collected in response to this. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122079 | Closed | VERMA RAHUL | 2026-06-20 | Randomly checked TT, which are coming inside are found to be in locked condition how ever few of them found to be with pre OTP. Locks of TTs UP81CT9210, UP80GT0034, UP81AF5757, UP79T6969 and UP81ET4673 were checked with intelligent key. All found ok. | 3.5 | EM Lock SOP compliance verified | 1128 | MATHURA TERMINAL | Corrective action to be taken in coordination with dealers and regional sales officer. | SOD | Marketing | NUZ | 2026-03-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010909ACN-2026-02-4000122079 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122079 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122079 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122079 | AUD-2026-02-2000010909ACN-2026-02-4000122079 | 21 | 21 | 26 | 80 | 14 | 13 | 31 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Empty TT's are checked by 2 officers. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122080 | Closed | VERMA RAHUL | 2026-06-20 | Ethanol TT dip checked and found ok. Physical verification of empty ethanol TT is being done by one officer. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1128 | MATHURA TERMINAL | Location to strengthen and follow empty TT check SOP at location. | SOD | Marketing | NUZ | 2026-02-27 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-27 | AUD-2026-02-2000010909ACN-2026-02-4000122080 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122080 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122080 | 532 | 8294 | 21 | 8294 | 234 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122080 | AUD-2026-02-2000010909ACN-2026-02-4000122080 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Complied, provision of acknowledgment and recording comment has been incorporated in TAS. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122081 | Closed | VERMA RAHUL | 2026-06-20 | Critical alarms available is system however provision of acknowledgment and recording comment is not available in TAS. Location hastaken up with TAS vendor who has recently taken over. | 3.12 | Critical alarms checked & corrective actions reviewed | 1128 | MATHURA TERMINAL | Corrective action to be taken. | SOD | Marketing | NUZ | 2026-02-28 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010909ACN-2026-02-4000122081 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122081 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122081 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122081 | AUD-2026-02-2000010909ACN-2026-02-4000122081 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | SAFE100 Self Safety Audit 2025: Total points: 64, Open points: 8, EDC: 31.12.2026 MDSA 25-26: Total points: 52, Open points: 11, EDC: 31.12.2026 MDSA 24-25: Total points: 86, Open points: 01, EDC: 31.12.2026 OISD ESA 2023-24: Total points: 41, Open points: 00, EDC: NA Action for remaining Points will be taken as per timeline. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122084 | Closed | VERMA RAHUL | 2026-06-20 | Compliance is being done. Status as of Jan'26: SAFE100 Self Safety Audit 2025: Total points: 64, Open points: 21, EDC: 31.12.2026 MDSA 25-26: Total points: 52, Open points: 24, EDC: 31.12.2026 MDSA 24-25: Total points: 86, Open points: 01, EDC: 31.12.2026 OISD ESA 2023-24: Total points: 41, Open points: 00, EDC: NA | 3.18 | OISD/MDSA/SSA compliance reviewed | 1128 | MATHURA TERMINAL | Location to ensure timely and quality closure of audit observation scheduled for closure in current FY. | SOD | Marketing | NUZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010909ACN-2026-02-4000122084 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122084 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122084 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122084 | AUD-2026-02-2000010909ACN-2026-02-4000122084 | 21 | 21 | 26 | 80 | 14 | 13 | 31 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | All Projects completed and closed as per deadline. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122086 | Closed | VERMA RAHUL | 2026-06-20 | Project review done. | 4.3 | Project progress reviewed | 1128 | MATHURA TERMINAL | Location to complete TAS projects as per project completion time. | SOD | Marketing | NUZ | 2026-03-10 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122086 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122086 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122086 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122086 | AUD-2026-02-2000010909ACN-2026-02-4000122086 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | No action required. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122091 | Closed | VERMA RAHUL | 2026-06-20 |  | 6.3 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122091 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122091 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122091 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122091 | AUD-2026-02-2000010909ACN-2026-02-4000122091 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 42
ARYA VIPIN KUMAR | 2026-06-20 | VERMA RAHUL | 2026-06-20 | Pipeline support has been provided. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122093 | Closed | VERMA RAHUL | 2026-06-20 | A pipeline support found hanging from foam line of Tk07. | 6.5 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122093 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122093 | 2026-09-18 | 31.7538 | 292 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122093 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122093 | AUD-2026-02-2000010909ACN-2026-02-4000122093 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | Lux level mainatined as per OISD requirement | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124795 | Closed | SINGH BHOPENDRA | 2026-05-02 | TT Gantry: 42 Main Gate: 83 ETP: 61 Tank Farm: 24 Tank no 2: 31 MCC room: 48.8 Security room: 91 TLF Pump house: 193 TT gantry front: 45 TLF PH manifold:73 TT in gate: 55 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124795 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124795 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124795 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124795 | AUD-2026-03-2000011014ACN-2026-03-4000124795 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | All CCTV cameras are functioning properly. Screenshots are attached for reference. The officer was present during both the pre-water filling and post-water filling stages of TT calibration. The officer also inspected the inside of the TT compartments and checkedthe TT fittings. CCTV footage/screenshots attached during the TT calibration process confirm the presence of the officer. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124796 | Closed | SINGH BHOPENDRA | 2026-06-20 | Total CCTV installed: 66, working 61. Last back up available till date 09.12.2025. CCTV footages were verified for checking extentof supervision of TT calibration. It was found that for TT no UP27T0089 and UP24AT4959, only post filling of water, dips were beingchecked. Checking of Proof line, leak of partition, or appropriateness of inside of compartments were not checked. | 2.6 | CCTV functioning checked | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124796 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124796 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124796 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124796 | AUD-2026-03-2000011014ACN-2026-03-4000124796 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | All VA alerts are being reviewed and closed with appropriate and accurate remarks at VA portal. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124797 | Closed | SINGH BHOPENDRA | 2026-05-02 | Number of cameras in VA is 55 Nos /Number of camera active in VA is 48. PPE noncompliance CALIBRATION_SHED TAS_1157_SOP043_030326_000001 alert was closed with false remarks however alerts was valid. | 2.7 | VA alerts checked / analysed | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124797 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124797 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124797 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124797 | AUD-2026-03-2000011014ACN-2026-03-4000124797 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | Sprinkler has been cleaned | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124798 | Closed | SINGH BHOPENDRA | 2026-05-02 | Tested foam pourers of Tk3. Found working properly. Fire wall valve of Tk3 was checked. Found its integrity proper. Sprinkler lines of Tk2 was operated. Sprinklers L22, L25 and U15 found choked. MEFG of TK5 was operated. Its performance found satisfactory. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124798 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124798 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124798 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124798 | AUD-2026-03-2000011014ACN-2026-03-4000124798 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | TT crew training was provided as per OISD-154. Additionally, the working and functioning of the VTS were discussed with the TT crewduring the daily gate meeting | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124800 | Closed | SINGH BHOPENDRA | 2026-06-20 | TT crew interacted with, were found not aware of VTS Emergency button. | 2.15 | TT crew roadside emergency procedures checked | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124800 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124800 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124800 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124800 | AUD-2026-03-2000011014ACN-2026-03-4000124800 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | Action taken records found and TK-7 False ESD rectified | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124804 | Closed | SINGH BHOPENDRA | 2026-05-02 | Action taken record not available for ESD active alarm date 07.02.2026. | 3.12 | Critical alarms checked & corrective actions reviewed | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124804 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124804 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124804 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124804 | AUD-2026-03-2000011014ACN-2026-03-4000124804 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | The location has initiated the maintenance of TAS local loading reports to support and verify proof tank bay calibration activities. A copy of the TAS report is attached for reference. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124805 | Closed | SINGH BHOPENDRA | 2026-06-20 | Local loading reports reviewed. Reports are signed and remarks are updated. Prover unloading records are not attached with daily day end reports. Day end summary reports are not containing local loading/top up data (including prover) whereas same is reflecting TAS report. | 3.14 | Local loading checks (if applicable) | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124805 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124805 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124805 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124805 | AUD-2026-03-2000011014ACN-2026-03-4000124805 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | Traning Provided to worker for use of PPE's as Claibration shed & Hazardours area | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124806 | Closed | SINGH BHOPENDRA | 2026-05-02 | Housekeeping satisfactory. PPE usage shall be ensured at calibration tower. | 3.15 | Housekeeping & PPE usage checked | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124806 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124806 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124806 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124806 | AUD-2026-03-2000011014ACN-2026-03-4000124806 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-05-02 | All MOC Closed after work | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124807 | Closed | SINGH BHOPENDRA | 2026-05-02 | Total MOC: 25, Open: 2, Closed: 23. Over due: 1 Nos | 3.17 | MOC status reviewed | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124807 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124807 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124807 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124807 | AUD-2026-03-2000011014ACN-2026-03-4000124807 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | All projects have been completed within the scheduled time and approved budget. There has been no time overrun or budget overrun inany project. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124809 | Closed | SINGH BHOPENDRA | 2026-06-20 | Project works related to compliance shall be expedited and timely closure shall be ensured. | 4.3 | Project progress reviewed | 1157 | BAREILLY DEPOT | Location to ensure closure of project scheduled for closure in current FY | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124809 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124809 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124809 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124809 | AUD-2026-03-2000011014ACN-2026-03-4000124809 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | VCB, aluminium cable, and MS scrap were disposed of in March 2026 through M/s Amarpal and M/s Janta Disposal. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124810 | Closed | SINGH BHOPENDRA | 2026-06-20 | location to identify and segregate scrap available in scrap yard initiate disposal for revenue generation. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124810 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124810 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124810 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124810 | AUD-2026-03-2000011014ACN-2026-03-4000124810 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | Maintenance work has been completed to rectify the oil leakage, and the oil marks at the site have been cleaned. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124811 | Closed | SINGH BHOPENDRA | 2026-06-20 | Oil leak observed from MS2, MS3, HSD8 and HSD9 pumps. | 6.1 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124811 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124811 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124811 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124811 | AUD-2026-03-2000011014ACN-2026-03-4000124811 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | The OEM AMC team attended the site and completed the necessary maintenance activities to rectify the leakage. The area has been cleaned and restored to normal condition. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124812 | Closed | SINGH BHOPENDRA | 2026-06-20 | Leak observed in both 250 KVA and 500 KVA DG | 6.2 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124812 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124812 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124812 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124812 | AUD-2026-03-2000011014ACN-2026-03-4000124812 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | Training was imparted to the concerned personnel on the procedure for acknowledging alarms in the TAS panel. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124813 | Closed | SINGH BHOPENDRA | 2026-06-20 | Security staff of security cabin found as not having complete knowledge of all alarms in panels. | 6.3 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124813 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124813 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124813 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124813 | AUD-2026-03-2000011014ACN-2026-03-4000124813 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | We have implemented transformer WTI, OTI, and BU relay alarm testing by installing a Normally Open (NO) push button in the transformer panel | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124814 | Closed | SINGH BHOPENDRA | 2026-06-20 | Alarm nomenclature shall be provided in VCB annunciator panel. | 6.4 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124814 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124814 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124814 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124814 | AUD-2026-03-2000011014ACN-2026-03-4000124814 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | The unused OWS pits have been dismantled/demolished as they were no longer in service | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124815 | Closed | SINGH BHOPENDRA | 2026-06-20 | location to demolish non required OWS pits and valves in the filed after installation of ETP at location. | 6.5 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124815 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124815 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124815 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124815 | AUD-2026-03-2000011014ACN-2026-03-4000124815 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | The location has started disconnecting the unloading hose from the unloading pipeline after completion of rake unloading at the siding | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124816 | Closed | SINGH BHOPENDRA | 2026-06-20 | Unloading hoses shall be kept connected from the unloading points at TW siding and oil was dripping in drain. | 6.6 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124816 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124816 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124816 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124816 | AUD-2026-03-2000011014ACN-2026-03-4000124816 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | The unloading points have been properly blinded, and hose connections are being secured with four nuts and bolts to ensure safe operation | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124817 | Closed | SINGH BHOPENDRA | 2026-06-20 | Unloading points blind and hoses were found connected with 2 bolts instead of 4 bolts. | 6.7 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124817 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124817 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124817 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124817 | AUD-2026-03-2000011014ACN-2026-03-4000124817 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
SONAR AMIT KUMAR | 2026-06-20 | SINGH BHOPENDRA | 2026-06-20 | it took some time for the rainwater mixed with oil to reach the OWS through the drain. However, the drain has been cleaned | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124819 | Closed | SINGH BHOPENDRA | 2026-06-20 | One the unloading point support was found settled and gap was filled with piece of stone as temporary support. | 6.9 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124819 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124819 | 2026-07-16 | 95.7538 | 292 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124819 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124819 | AUD-2026-03-2000011014ACN-2026-03-4000124819 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | LIC has taken resposibility to ensure for guiding the officers for knowledge transfer. | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125545 | Closed | G RAMADOSS | 2026-03-22 | Dharpuri Terminal Team of officers are fully motivated with enthusiasm and zeal to perform at peak of their potential to not only meet the set Goals & Targets but also excel in the same. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1999 | DHARAMAPURI TERMINAL | Officers were appreciated for theor efforts and maintaining the terminal in super notch level. They were advised to maintain the same tempo and ensure 100% Safety and compliance to SOP. LIC was advised to guide the officers in getting updated on all OISD standards applicable to Terminal. | SOD | Marketing | SZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011224ACN-2026-03-4000125545 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125545 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125545 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011224ACN-2026-03-4000125545 | AUD-2026-03-2000011224ACN-2026-03-4000125545 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | LIC shall take review of performace | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125546 | Closed | G RAMADOSS | 2026-03-22 | Reviewed performance of all Officers and officers were found focussed on the Goals and Targets with emphasis on process/efficiency improvement | 1.2 | Performance review conducted | 1999 | DHARAMAPURI TERMINAL | Team to focus on G&T for the year and come up with improvements process and work efficency. LIC advised to review the individual performance and advise officers to ensure 100% achievement. | SOD | Marketing | SZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011224ACN-2026-03-4000125546 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125546 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125546 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011224ACN-2026-03-4000125546 | AUD-2026-03-2000011224ACN-2026-03-4000125546 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | 1.DCV installation shall be completed by May 2026 and dip elimination by Aug 2026. 2. 3 ARs which are due on 31.03.2026 shall be closed as per due date. | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125547 | Closed | G RAMADOSS | 2026-03-22 | 1.Dip Elimination: Dip elimination is pending. Location informed that PO is placed for 2 DCV and expected to be received by end of April 2026. 2.NPCB Projects due as on 31.03.2026: Pond works: Civil works in progress and targetted to be completed by 31.03.26as per terminal. 1 KL Prover: Prover received at site and erection works in progress. CEMS: Integration works completed on 09.03.2026. | 1.3 | Pending issues reviewed | 1999 | DHARAMAPURI TERMINAL | 1. Location to expedite and achieve dip elimination at the earliest 2. To expediate the closure of 3 AR's as per target date of 31.03.2026 | SOD | Marketing | SZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S4 | F2 | 2026-08-31 | AUD-2026-03-2000011224ACN-2026-03-4000125547 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125547 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125547 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011224ACN-2026-03-4000125547 | AUD-2026-03-2000011224ACN-2026-03-4000125547 | 21 | 21 | 26 | 80 | 2 | 2 | 52 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | Location has contacted CECRI and in process of getting offer | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125548 | Closed | G RAMADOSS | 2026-03-22 | Earth pit issues were there at terminal with respect to high resistance values. Location already taken up with consultant for same as per advise of HQO. | 3.16 | Earth pits / boundary / vegetation control checked | 1999 | DHARAMAPURI TERMINAL | Location to complete CECRI study and submit report to HQO for further action for rectification of earth pits to get correct values | SOD | Marketing | SZ | 2026-04-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-15 | AUD-2026-03-2000011224ACN-2026-03-4000125548 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125548 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125548 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011224ACN-2026-03-4000125548 | AUD-2026-03-2000011224ACN-2026-03-4000125548 | 21 | 21 | 26 | 80 | 2 | 2 | 33 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | Work in progress | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125900 | Closed | G RAMADOSS | 2026-03-22 | Reviewed progress of 4 current projects related to Pond works, 1 kL mobile prover, CEMS and UG pump. | 4.3 | Project progress reviewed | 1999 | DHARAMAPURI TERMINAL | All 4 ongoing projects to be expedited before 31-03-2026 | SOD | Marketing | SZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011224ACN-2026-03-4000125900 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125900 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125900 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011224ACN-2026-03-4000125900 | AUD-2026-03-2000011224ACN-2026-03-4000125900 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | In Progress, will be completed by 31-03-2026 | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125901 | Closed | G RAMADOSS | 2026-03-22 | Location initiated action for scrap disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1999 | DHARAMAPURI TERMINAL | Location to expediate the disposal of scrap at the earliest. | SOD | Marketing | SZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011224ACN-2026-03-4000125901 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125901 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125901 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011224ACN-2026-03-4000125901 | AUD-2026-03-2000011224ACN-2026-03-4000125901 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 42
MADHUSUDHANAN M | 2026-06-21 |  |  | W.I.P | DHARAPURI TERMINAL SR MGMT AUDIT | 2026-03-13 | AUD-2026-03-2000011224 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125549 | Closed | G RAMADOSS | 2026-03-22 | All OISD points are complied. Pending MDSA/SSA points are related to Earth pits, Dip elimination, UG pump, Valves rectification | 3.18 | OISD/MDSA/SSA compliance reviewed | 1999 | DHARAMAPURI TERMINAL | Location to expediate the closure of Pending MDSA/SSA points. | SOD | Marketing | SZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-03-2000011224ACN-2026-03-4000125549 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011224ACN-2026-03-4000125549 | 2026-09-11 | 38.7538 | 293 | >20 | AUD-2026-03-2000011224 - ACN-2026-03-4000125549 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011224ACN-2026-03-4000125549 | AUD-2026-03-2000011224ACN-2026-03-4000125549 | 21 | 21 | 26 | 80 | 2 | 2 | 57 | 42
MADHUSUDHANAN M | 2026-06-22 |  |  | PO validity is extended | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138465 | Closed | MADHUSUDHANAN M | 2026-06-22 | Requirement of additional MEB and fund for DCV are identified | 1.5 | HQO / Zonal support required identified | 1999 | DHARAMAPURI TERMINAL | Zone to extend the PO validity not attributable to party as funds have not been released | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013161ACN-2026-06-4000138465 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138465 | 2026-09-11 | 38.7538 | 294 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138465 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013161ACN-2026-06-4000138465 | AUD-2026-06-2000013161ACN-2026-06-4000138465 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 42
MADHUSUDHANAN M | 2026-06-22 |  |  | Being reviewed and recorded | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138466 | Closed | MADHUSUDHANAN M | 2026-06-22 | All 98 CCTVs are working. Backup of 95 days available. | 2.6 | CCTV functioning checked | 1999 | DHARAMAPURI TERMINAL | LIC and safety officer to regularly monitor the CCTV footage for at least 10-15 min daily twice a day and record observations | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 2 | ASSET INTEGRITY | S2 | F1 | 2026-07-30 | AUD-2026-06-2000013161ACN-2026-06-4000138466 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138466 | 2026-09-11 | 38.7538 | 294 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138466 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013161ACN-2026-06-4000138466 | AUD-2026-06-2000013161ACN-2026-06-4000138466 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 42
MADHUSUDHANAN M | 2026-06-22 |  |  | Faded stickers and earthpit stickers are replaced | DHARMAPURI_TML_Q1_ZONAL HEAD INSPECTION | 2026-06-10 18:00 | AUD-2026-06-2000013161 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-06-4000138469 | Closed | MADHUSUDHANAN M | 2026-06-22 | 1) Faded SOP boards at TTG shall be replaced. 2) Earth pit board dates shall be painted or done with proper stickers. | 5.2 | Best practices identified for sharing across zones/locations | 1999 | DHARAMAPURI TERMINAL | Location shall comply with the same. | SOD | Marketing | SZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013161ACN-2026-06-4000138469 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013161ACN-2026-06-4000138469 | 2026-09-11 | 38.7538 | 294 | >20 | AUD-2026-06-2000013161 - ACN-2026-06-4000138469 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013161ACN-2026-06-4000138469 | AUD-2026-06-2000013161ACN-2026-06-4000138469 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | a) TT exit time and LPM are reviewed on daily basis. ( Complied) b)Checklist for VTS and EM locking is being filled and checked ondaily basis. C) Safety officer is checking equiments on daily basis and filling the daily safet checklist d) Tank painting detailshas been submitted to HQO | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.10 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127481 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | a) The TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlierVC's with all Location TAS officer b) The Transportation officer to maintain Annex-1 of VTS circular and ensuring that all TT's are covered for VTS and EM locking check on monthly baisis with record c) The Safety Officer shall ensure that all field equipment are maintained in intact and operational condition at all times through regular inspection and monitoring. d) The Maintenance Officer shall initiate and pursue budget proposals for tank painting and any required repair works to ensure asset integrity and compliance with maintenance standards. | 1.1000000000000001 | Improvement plans discussed | 1341 | HISAR TERMINAL | a) A structured monitoring system to be ensured to track TT exit time and LPM on a daily basis, with periodic review by location. b) A monthly compliance checklist shall be institutionalized for VTS coverage and EM locking verification of all TTs. c) A preventive maintenance and inspection schedule shall to be followed for all critical field equipment, with records maintained and periodically audited to ensure operational readiness. d) Budget requisitions shall be initiated in a timely manner, with systematic follow-upto ensure prompt approval and disbursement of funds. | SOD | Marketing | NZ | 2026-05-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-30 | AUD-2026-03-2000010926ACN-2026-03-4000127481 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127481 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127481 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127481 | AUD-2026-03-2000010926ACN-2026-03-4000127481 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | b)Portable MEFG unit has been placed in PLT process area. B) Mock drills are being done on monthly basis and evacuation procedures are being followed. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127482 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Review of Mock drill conducted on 13/01/2026 at 1434 hours with scenario considering TT during loading catches fire and PLT processarea, MS receipt line leakage near flow control valve and fire.. Following observation were observed during the drill a) All equipment used during the fire drill worked well b) Portable MEFG can be used at the PLT process area for pool fire. c) Material evacuation can also be exercised | 2.1 | Fire drill conducted in last 6 months (surprise) | 1341 | HISAR TERMINAL | b) Provision and strategically position Portable MEFG units in the PLT process area, and include their operation in regular mock drills to enhance preparedness for pool fire scenarios. c) Incorporate structured material evacuation procedures into the emergency response plan and regularly practice the same during mock drills to ensure effective and timely evacuation during actual incidents. | SOD | Marketing | NZ | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127482 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127482 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127482 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127482 | AUD-2026-03-2000010926ACN-2026-03-4000127482 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Location has maintained the water level. Location has procured 2843 KL water via invoice no 2025-26/128 on 25.03.26 | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127486 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | The minimum fire water requirement for the location is 10,400 KL as per the Fire Water Calculation Sheet. At present, 9,182 KL of fire water is available in the fire water tanks at the location. | 2.1 | Fire water levels verified | 1341 | HISAR TERMINAL | The required water level in the Fire Water Tank shall be maintained at all times as per the Fire Water Calculation Chart to ensure adequate availability during emergency situations. | SOD | Marketing | NZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127486 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127486 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127486 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127486 | AUD-2026-03-2000010926ACN-2026-03-4000127486 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | a) Lights has been repaired in fire punp house and Near ROSOV of TK4 to miantian the uniform ullumination | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127484 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Lux level checked on 10/03/2026 at various location with in the premises including; Visitor's Road - Required Lux - 20 Lux / Observed Value - 31.5 Lux TT Gantry Bay-01 - Required Lux - 60 Lux / Observed Value - 141 Lux TT Gantry Bay-02 - Required Lux - 60 Lux / Observed Value - 140 Lux Roads b/w Gantry & Pump House - Required Lux - 10 Lux / Observed Value - 8 Lux Manifold - Required Lux - 60 Lux / Observed Value - 225 Lux Near ROSOV of TK 4 - Required Lux - 60 Lux / Observed Value - 46 Lux ETP - Required Lux - 60 Lux / Observed Value - 225 Lux Tank - 04 MOV - Required Lux - 60 Lux / Observed Value - 99.5 Lux Fire Pump House - Required Lux - 100 Lux / Observed Value - 60 Lux Jockey Pump House - Required Lux - 100 Lux / Observed Value - 97.5 Lux | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1341 | HISAR TERMINAL | a) Focus lights should be properly aligned to ensure effective and uniform illumination. b) Adequate lighting arangements to be made for uniform illumination. | SOD | Marketing | NZ | 2026-05-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-30 | AUD-2026-03-2000010926ACN-2026-03-4000127484 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127484 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127484 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127484 | AUD-2026-03-2000010926ACN-2026-03-4000127484 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | a)Servicing of Fire extinguisher has been done by the transporter b) Protective screen on exhaust pipe has been installed by the transporter c) Safety training will be done for all drivers in June/July 2026. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127487 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Part B Check was done on DCT HR61-C4382 of M/s Sharan Filling on 12/03/2026. Following Observations were recorded: a) Fire Extinguisher Servicing due (Nov 2025) b) Protective Screen is not available on exhaust pipe c) Last safety Training attended in sep 2025. | 3.1 | TT fittings & discipline checked | 1341 | HISAR TERMINAL | a) Ensure immediate servicing of the fire extinguisher and implement a tracking system to monitor due dates to prevent recurrence of overdue servicing. b) Provide and install a protective screen on the exhaust pipe to mitigate fire hazards and ensure compliance with safety standards. c) Ensure periodic safety training is conducted for all drivers as per defined frequency and maintain updated training records to ensure competency and awareness. | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127487 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127487 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127487 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127487 | AUD-2026-03-2000010926ACN-2026-03-4000127487 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | "The variation observed in TT no.- HR39E7060 was taken up with W&M and calibration was checked again. It was found that marking ofDip line of Chamber-02, was correct but in calibration chart it was written wrong, which has been corrected by W&M. The report hasbeen attached for your reference. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127488 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Post loading dip checks were performed on two TTs during the visit- its findings were shared with the location. Out of the two TTs checked during the visit, HR39E7060 of +8mm variation was observed in Chamber 1 loaded with MS. In the same TT while verification ofdip rod, a variation of 4mm was observed in the dip marking for Chamber no. 2. and a variation of 2mm observed for Chamber 3. This TT was calibrated at Hisar Terminal on 26.12.2026. Variation for dip as well as measurement of dip rod in case of TT# HR64A2760 were found within norms. | 3.2 | Post-loading dip checks verified | 1341 | HISAR TERMINAL | Location to exercise stringent during calibration of TTs at the location w.r.t. verfication of dip rod markings done by W&M officer. | SOD | Marketing | NZ | 2026-04-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010926ACN-2026-03-4000127488 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127488 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127488 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127488 | AUD-2026-03-2000010926ACN-2026-03-4000127488 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | 5% Monitoring of daily trips is being done. Records maintained | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127489 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Check for 5% VTS deviation is being done by the location and has been reviewed during visit | 3.3 | VTS deviations reviewed | 1341 | HISAR TERMINAL | Proper record for 5 % daily check and 100% monthly check to be made | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127489 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127489 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127489 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127489 | AUD-2026-03-2000010926ACN-2026-03-4000127489 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | 5% EM locks of daily reported TTs are being checked and records maintained. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127490 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Check for 5% EM locks is being done by the location and has been reviewed during visit | 3.5 | EM Lock SOP compliance verified | 1341 | HISAR TERMINAL | Proper record for 5 % daily check and 100% monthly check to be made | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127490 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127490 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127490 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127490 | AUD-2026-03-2000010926ACN-2026-03-4000127490 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Observed ethanol density at 15.6 Deg C is being calculated and compared with invoice density. (Complied) | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127491 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Ethanol TT# PB11DC8809 was verified for dips before and after unloading on 12.03.2026. Dip rod was also measured. The dips observedin the tanker were Ch.1 (7KL): NIL, Ch.2 (7KL): -5mm, Ch.3 (6KL): +3mm, Ch.4 (6KL): -1mm, Ch.5 (7KL): NIL & Ch.7 (7KL): +13mm. Records of Ethanol decantation was also checked and it was found that the location is not calculating the density of ethanol received @ 15.6 deg. C for comparison with the invoice density @ 15.6 deg. C. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1341 | HISAR TERMINAL | Location to calculate and check the observed ethanol density at 15.6 deg. C in each case and compare it with the invoice density. | SOD | Marketing | NZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127491 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127491 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127491 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127491 | AUD-2026-03-2000010926ACN-2026-03-4000127491 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | "1. TSI indicates Secondary radar & water level readings. 2. Product dip in Tank TK1 at various levels & temperature variation areunder acceptable limits. 3. Water Dip variation in Tank TS7 has been corrected 4. Sludge shall be removed during tank cleaning 5. Densitometer readings for Tanks having variation above allowable limit has been corrected" | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127492 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Physical dips, density & temparatures of UG tanks TS1, TS3, TS7 & TS9 as well as for AG tanks TK1 & TK5 were verified and compared with TAS readings on 11.03.2026. Details were shared with the location. Following observations were made: 1. TSI doesn't indicate Secondary Radar Readings & Water Level. Location to take up with Honeywell to ensure reflection of water level in the TSI also & confirm. 2. Product Dip variation as well as temperature variation in case of TK1 w.r.t. manual mearurements was observed beyond norms.Similarly, termperature difference in case of tank TS1, TS7 & TS9 is also observed beyond norms. Location to monitor the behaviour of the tanks at various levels to establish if any correction in calibration of radar gauges is required. 3 Water Dip variation is observed in case of tank TS7. Location to look into the readings provided by radar gauges. 4. Sludge of 350mm, 20mm & 30mm appearedduring physical dip measurements with dip tape in case of tanks TK5, TS1 & TS7 respectively. 5. Densitometer recordings in TAS is showing significant variations as compared to the actual physical measurements with the help of hydrometer and thermometers. Location to take up with TAS vendor for immediate rectification of this error so as to have acceptable accuracy. 6. As product level was very low in case of tank TS3, physical measurements of density & temperatures could not be carried out. | 3.7 | Inventory physical dip of minimum two tanks taken | 1341 | HISAR TERMINAL | 1. 2. 3. 4. & 5. Location to review the gaps identified & take up with the TAS vendor if required to ensure immediate corrective action. | SOD | Marketing | NZ | 2026-04-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127492 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127492 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127492 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127492 | AUD-2026-03-2000010926ACN-2026-03-4000127492 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Excess vegitation has been cleared | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127493 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Housekeeping - Housekeeping of the location is found to be satisfactory with some areas requiring minor upkeep which were discussedduring field round with location team. | 3.15 | Housekeeping & PPE usage checked | 1341 | HISAR TERMINAL | Excess vegetation at the site should be cleared, as discussed during the field round | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127493 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127493 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127493 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127493 | AUD-2026-03-2000010926ACN-2026-03-4000127493 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | T4S has been conducted between 18.05.2026 to 20.05.2026 | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127495 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | T4S Audit of the location is pending for which PO has been already placed. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1341 | HISAR TERMINAL | T4S audit to be ensured by April 2026. | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127495 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127495 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127495 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127495 | AUD-2026-03-2000010926ACN-2026-03-4000127495 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Pressure gauge has been changed. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127496 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Pressure Gauge of Jockey pump-02 found to be faulty | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Pressure Gauge to be replaced | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010926ACN-2026-03-4000127496 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127496 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127496 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127496 | AUD-2026-03-2000010926ACN-2026-03-4000127496 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Leakage has been arrrested from all product pump of HSD | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127497 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | In Product pump house leakage observed from Oil Cup | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Leakage to be arrested immediately | SOD | Marketing | NZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127497 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127497 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127497 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127497 | AUD-2026-03-2000010926ACN-2026-03-4000127497 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Crocodile clip and earthing wire has been replaced. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127498 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | The crocodile clip installed at Bay No. 03 & used for earthing of TTs placed for loading was found to be lacking strength to firmlygrip the TT body for the intended purpos due to reduced spring tension leading to inadequate clamping force. This may result in improper bonding/ earthing contact with the TT during gantry operations. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Replace the defective crocodile clip at Bay No. 03 immediately to ensure proper bonding/earthing during TT gantry operations. Also,check for similar kind of issues at other bays and take corrective actions as required. | SOD | Marketing | NZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127498 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127498 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127498 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127498 | AUD-2026-03-2000010926ACN-2026-03-4000127498 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | MS scrap has been disposed off via invoice no HR0150133528 dated 27.03.2026 | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127499 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Scrap available-20 MT. RFD processed with successful action and only upliftment is pending. Target completion-28th March’26 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1341 | HISAR TERMINAL | Complete Scrap disposal in time bound manner. | SOD | Marketing | NZ | 2026-03-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127499 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127499 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127499 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127499 | AUD-2026-03-2000010926ACN-2026-03-4000127499 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
DURGA NARAIN MEENA | 2026-06-22 | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Location will ensure to initiate separate electrical isolation/energization permit fir earthpit checking of DG | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127494 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-05-27 | Earth Pits - Total 249 Nos of Earth pits are there at the location. Earth Pit No 02 & 27 Checked and Found Individual and Grid Reading as mentioned Individual Reading of EP 02 - 1.69 Ω Grid Reading of EP-02 - 0.11 Ω Individual Reading of EP 27 - 1.5 Ω GridReading of EP-27 - 0.14 Ω While revieweing the work permit it is observed that location has not taken Electrical Isolation / energization permit for earthpits connected to Electical equipment. | 3.16 | Earth pits / boundary / vegetation control checked | 1341 | HISAR TERMINAL | A separate Electrical Isolation/Energization Permit shall be obtained while carrying out half-yearly checks of earth pits connectedto electrical equipment. The CWP and the Electrical Isolation/Energization Permit shall also be properly linked. | SOD | Marketing | NZ | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010926ACN-2026-03-4000127494 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127494 | 2026-09-30 17:00 | 19.0455 | 294 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127494 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127494 | AUD-2026-03-2000010926ACN-2026-03-4000127494 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
BINU K | 2026-06-22 | J. NAVANEETH RAMJI | 2026-06-22 | Loctaion is under closure, hence the point is closed | TVL IRD- SR MGMT INSPECTION | 2026-03-19 | AUD-2026-03-2000011226 | 2026-03-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124679 | Closed | J. NAVANEETH RAMJI | 2026-06-22 | Sprinklers to be provided at siding area based on the approval from Railways. BPCL being the siding co-ordinator will execute the project on 50:50 cost sharing basis. | 1.4 | Earlier action points status checked | 1879 | TIRUNELVELI DEPOT | Location to Co-ordinate with Railways and BPCL for providing sprinkler facility . | SOD | Marketing | SZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011226ACN-2026-03-4000124679 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011226ACN-2026-03-4000124679 | 2026-05-08 | 164.7538 | 294 | >20 | AUD-2026-03-2000011226 - ACN-2026-03-4000124679 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011226ACN-2026-03-4000124679 | AUD-2026-03-2000011226ACN-2026-03-4000124679 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 42
BINU K | 2026-06-22 | J. NAVANEETH RAMJI | 2026-06-22 | Operating paltform provided for safe operation of isolation valve and sprinkler nozzle celaned | TVL IRD- SR MGMT INSPECTION | 2026-03-19 | AUD-2026-03-2000011226 | 2026-03-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124680 | Closed | J. NAVANEETH RAMJI | 2026-06-22 | Checked knowledge of TT crew, contract workmen and officers and found satisfactory. Officers capacity to operate HVLR, WCF Monitor found competent to handle the same. A) Operating platform not provided for isolation valve of sprinkler line in Tank 2 B) 3 sprinklers (41,44 and 123) were found choked in Tank 2 | 2.5 | Emergency response preparedness reviewed | 1879 | TIRUNELVELI DEPOT | A) Operating platform to be provided for safe operation of isolation valve B) Sprinkler nozzles to be cleaned. | SOD | Marketing | SZ | 2026-04-10 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-10 | AUD-2026-03-2000011226ACN-2026-03-4000124680 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011226ACN-2026-03-4000124680 | 2026-05-08 | 164.7538 | 294 | >20 | AUD-2026-03-2000011226 - ACN-2026-03-4000124680 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011226ACN-2026-03-4000124680 | AUD-2026-03-2000011226ACN-2026-03-4000124680 | 21 | 21 | 26 | 80 | 0 | 0 | 32 | 42
BINU K | 2026-06-22 | J. NAVANEETH RAMJI | 2026-06-22 | Foam barrels kept on platform | TVL IRD- SR MGMT INSPECTION | 2026-03-19 | AUD-2026-03-2000011226 | 2026-03-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124681 | Closed | J. NAVANEETH RAMJI | 2026-06-22 | AFFF- Stock: 11.56 Requirement: 8.2 KL ARAFFF- Stock:1.4 Requirement: 1.12 KL ARAFF foan cans were kept on the ground near FM - 9 | 2.9 | Foam inventory verified | 1879 | TIRUNELVELI DEPOT | Foam cans to be kept on the elevated platform | SOD | Marketing | SZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011226ACN-2026-03-4000124681 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011226ACN-2026-03-4000124681 | 2026-05-08 | 164.7538 | 294 | >20 | AUD-2026-03-2000011226 - ACN-2026-03-4000124681 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011226ACN-2026-03-4000124681 | AUD-2026-03-2000011226ACN-2026-03-4000124681 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
BINU K | 2026-06-22 | J. NAVANEETH RAMJI | 2026-06-22 | Cleaning and painting has been done | TVL IRD- SR MGMT INSPECTION | 2026-03-19 | AUD-2026-03-2000011226 | 2026-03-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124682 | Closed | J. NAVANEETH RAMJI | 2026-06-22 | Micor rusting observed at two points in MS line in TWD pump house. | 6.1 | Product Pipelines | 1879 | TIRUNELVELI DEPOT | Cleaning and painting to be done | SOD | Marketing | SZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011226ACN-2026-03-4000124682 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011226ACN-2026-03-4000124682 | 2026-05-08 | 164.7538 | 294 | >20 | AUD-2026-03-2000011226 - ACN-2026-03-4000124682 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011226ACN-2026-03-4000124682 | AUD-2026-03-2000011226ACN-2026-03-4000124682 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
SUJEET KUMAR | 2026-06-22 | SAXENA UMESH CHANDRA | 2026-06-22 | On field fire fighting training given to 15 personnel including officers and security workmen. Training as per OISD 154 6.4.2 was also impated to all new officers, employees on 20.06.2026 by HSE Officer Indore New IRD with post-training assessment and evaluation.All new entrants are now have role clarity and are conversant with the depot's fire fighting equipment and facilities. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127175 | Closed | SAXENA UMESH CHANDRA | 2026-06-22 | Yes, Surprise fire drill was conducted near TK 24 on 17.03.2026. The shortcomings and improvement of drills were discussed and briefed to the entire team. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1457 | INDORE DEPOT | 1) Location to have proper coordination 2) Role clarity to be ensured 3) Training required for new officers | SOD | Marketing | CEN | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011235ACN-2026-03-4000127175 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127175 | 2026-09-09 19:00 | 39.9622 | 294 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127175 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127175 | AUD-2026-03-2000011235ACN-2026-03-4000127175 | 21 | 21 | 26 | 80 | 0 | -3 | 31 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | 1- Cable scrap LOT uplifted by vendor M/S Waseem ( Realised value of 1.4 Lakh ) 2- Misc iron scrap sold to vendor M/S Ishal Trading Company 3- e RFD initiated for another iron scrap lot and under progess. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121481 | Closed | PANWAR VIPIN SINGH | 2026-03-03 | Earlier action points of operations audit/ MDSA audit etc checked and advised to make location scrap free by March'26 end and to ensure 100% branding of Tank Trucks. | 1.4 | Earlier action points status checked | 1308 | SITARGANJ DEPOT | 1. Scrap disposal to be ensured. 2. Branding of all the remaining TTs | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121481 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121481 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121481 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121481 | AUD-2026-02-2000010854ACN-2026-02-4000121481 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | Cycle Time: The cycle time increased slightly to 69.27 minutes in the current quarter compared to 68.91 minutes in the previous quarter, primarily due to the non-operation of one bay caused by a DCV malfunction. The issue was rectified during the CAMC visit conducted from 15–18 June, and the bay is now operational. TT Exit Time: Improved to 23.01 minutes in the current quarter from 25.33 minutes in the previous quarter. Loading Rate (LPM): Improved to 900 LPM in the current quarter compared to 873.81 LPM in the previous quarter. TT Branding: Branding has been completed for 99% of TTs; only two TTs are pending. Night Driving: Only 5 instances of night driving were observed during the quarter, with nil night-driving-related incidents reported. Overall, operational performance has improved with reduced TT exit time and higher loading rates, while cycle time is expected to improve further now that all bays are operational. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121482 | Closed | SHUKLA SHIVAM | 2026-06-22 | Officers were advised to improve operational parameters like first two hours loading target, improvement in cycle time, TT exit time, TT loading LPM, 100% TTs branding, Nil Night driving and speed violations etc. | 1.8 | Improvement plans discussed | 1308 | SITARGANJ DEPOT | a) first two hours loading target to be ensured along with improvement in TT exit time & LPM b) TT Branding to be ensured c) Nil Night Driving to be ensured. | SOD | Marketing | NUZ | 2026-03-23 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-23 | AUD-2026-02-2000010854ACN-2026-02-4000121482 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121482 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121482 | 532 | 8294 | 21 | 8294 | 210 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121482 | AUD-2026-02-2000010854ACN-2026-02-4000121482 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | A VTS monitoring mechanism has been established, and a register is being maintained for regular monitoring and record-keeping. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121489 | Closed | SHUKLA SHIVAM | 2026-06-22 | VTS deviations reviewed and discussed, also reviewed the register of alerts monitoring remarks. Advised to start a mechanism so that it could be ensured that all TTs are covered periodically. | 3.3 | VTS deviations reviewed | 1308 | SITARGANJ DEPOT | Compliance w.r.t. the VTS monitoring mechanish is to be established | SOD | Marketing | NUZ | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-02-25 | AUD-2026-02-2000010854ACN-2026-02-4000121489 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121489 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121489 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121489 | AUD-2026-02-2000010854ACN-2026-02-4000121489 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139984 | Open |  |  | A total of 28 recommendations were made during the last sr. mgmt. audit. These were reviewed for compliance and the location is found to have complied with 19 points. | 1.4 | Earlier action points status checked | 1334 | HPCL REWARI IRD | Balance points to be complied. Maximum target date for compliance is Aug'26 end. | SOD | Marketing | NZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-06-2000013601ACN-2026-06-4000139984 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139984 | 2026-09-10 17:00 | 39.0455 | 363 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139984 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139984 |  | AUD-2026-06-2000013601ACN-2026-06-4000139984 | 21 |  | 27 | 80 | 1 | 1 | 52
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139986 | Open |  |  | 1. TAS officer to focus on improvement of TT exit time and LPM for the location. | 1.8 | Improvement plans discussed | 1334 | HPCL REWARI IRD | 1. Daily monitoring of TT exit time and LPM for improvement. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000139986 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139986 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139986 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139986 |  | AUD-2026-06-2000013601ACN-2026-06-4000139986 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139990 | Open |  |  | It has been observed that No Trained Security personnel is having HAZ endorsement to move TT in Gantry. However, DCT/TPT are havingHAZ endorsement to move TT from gantry 50-100 m in case of emergency. However, on checking records of driver maintained at location it was found that few TT drivers of haryana were not having HAZ Endorsed Licence although Training certificates for carrying Hazardous goods is available in records. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1334 | HPCL REWARI IRD | Location to ensure 100% HAZ endorsement on drivers licence | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139990 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139990 | 2026-09-10 17:00 | 39.0455 | 332 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139990 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139990 |  | AUD-2026-06-2000013601ACN-2026-06-4000139990 | 21 |  | 27 | 80 | 1 | 1 | 48
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139993 | Open |  |  | Thorough checking TT No HR47F6164 was done along with concerned officer to sensitize the need for proper inspection of TTs in line with the extant circular. | 3.1 | TT fittings & discipline checked | 1334 | HPCL REWARI IRD | Compliance of the observation made w.r.t. TT inspected to ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139993 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139993 | 2026-09-10 17:00 | 39.0455 | 332 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139993 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139993 |  | AUD-2026-06-2000013601ACN-2026-06-4000139993 | 21 |  | 27 | 80 | 1 | 1 | 48
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139997 | Open |  |  | OISD Status - The OISD audit was conducted from 07th May 2025 to 09th May 2025, during which a total of 27 observations were raised. All observations have been complied with in a time-bound manner, and no observations are pending as of date. MDSA/ComprehensiveStatus - Comphrensive Audit was conducted from 19th to 22nd Nov 2025 , during which 80 observations were raised. Out of 80 observations 55 observations were closed and 25 are pending. Self Safety Audit Status - Self safety Audit was conducted from 03 Sep to 8th Sep'25, during which 41 observations were raised. Out of 41 observations 40 observations were closed and 01 is pending. PNGRB T4S Audit Status - T4S was conducted 27-29 Apr'26. Total of 42 recommendations were there out of which 19 have complied and 23 are pending for compliance. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1334 | HPCL REWARI IRD | All peding points of Comprehensive Audit & T4S audits to be complied in time bound manner. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000139997 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139997 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139997 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139997 |  | AUD-2026-06-2000013601ACN-2026-06-4000139997 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139998 | Open |  |  | Since Rewari Terminal has arge nos of DCT. A meeting was conducted with DCTs. Wherein various safety aspect, VTS block system etc was explains. DCTs rased issue of non payment of Toll to TTs shifted to Bahadurgarh. Sales officer agreed that routes that toll detailes will be uploaded by him in system | 3.2 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1334 | HPCL REWARI IRD | Pending toll payment to DCT to be ensured | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139998 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139998 | 2026-09-10 17:00 | 39.0455 | 332 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139998 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013601ACN-2026-06-4000139998 |  | AUD-2026-06-2000013601ACN-2026-06-4000139998 | 21 |  | 27 | 80 | 1 | 1 | 48
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | Sitarganj is a bridging location, and we receive pre-blended Gasohol from Bareilly Depot. Quality and Quantity (Q&Q) checks are carried out for all incoming TTs at the depot. The ethanol content in the received product is generally found to be in the range of 19–20%, which is within the acceptable limits. Ethanol blending is not carried out at Sitarganj Depot. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121490 | Closed | SHUKLA SHIVAM | 2026-06-22 | Location is receiving E20 MS from Aonla. Location is physically verifying Ethanol blend in the product received for all the compartments received. During the visit, TT No. UP25HT822 was verified and found to be blended with 19% to 19.5% Ethanol which is in-line QC requirement. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1308 | SITARGANJ DEPOT | Blending to be achieved @ 20% | SOD | Marketing | NUZ | 2026-03-25 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-02-2000010854ACN-2026-02-4000121490 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121490 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121490 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121490 | AUD-2026-02-2000010854ACN-2026-02-4000121490 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | EM Lock SOP compliance has been verified, and a new monitoring mechanism has been implemented to ensure that all TTs are covered and checked on a monthly basis. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121491 | Closed | SHUKLA SHIVAM | 2026-06-22 | EM lock SOP compliance verified and advised to start a mechanism so that it could be ensured that all TTs are covered on monthly basis. | 3.5 | EM Lock SOP compliance verified | 1308 | SITARGANJ DEPOT | Compliance w.r.t. the EM Lock monitoring mechanish is to be established | SOD | Marketing | NUZ | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121491 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121491 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121491 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121491 | AUD-2026-02-2000010854ACN-2026-02-4000121491 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | Issue of TSI of TK01: The TSI issue of TK01 has been rectified and is functioning satisfactorily. Investigation for variation beyond permissible limit of 3 mm: Dip readings of TK10 and TK11 were corrected with the support of M/s ICON Controls. At present, the TAS is displaying the correct dip readings, and the tanks are under observation for continued monitoring. TSI of Tanks to be checked for abnormality: All TSIs have been checked and verified. Presently, all TSIs are functioning properly. TSI of Tanks to be checked for abnormality: The tank gauging system has been thoroughly checked, and no abnormalities have been observed. Erroneous reading from Densitometer to be cross-checked and verified with physical readings: In the presence of M/s ICON Controls, the densitometer was removed from the tank and tested in a bucket containing HSD and Gasohol. The density values displayed in TAS were cross-verified with manual densitometer readings and found to be matching, indicating that the densitometer is functioning correctly. Additionally, the densitometer of TK-08 (Hexane) was sent to OMC for verification and was found satisfactory during testing. However, the vendor has suggested tank cleaning as a preventive measure. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121492 | Closed | SHUKLA SHIVAM | 2026-06-22 | Gauging of all the tanks at the location was done during the visit on 17th Feb'26 and details are provided in the Annexure. Following observations were made during the exercise. 1. TSI of TK01 is not displaying product temperature. Location to take necessary corrective action and confirm to zone. 2. A difference of 5mm in product level was observed in case of TK10. Location to investigate the reasons for this variation beyond permissible limit of 3mm and revert back with findings/ corrective action taken. 3. TSI of TK10 & TK11 were showing water levels in the tanks where as the system records in the control room are showing NIL water levels. Physically also, no water was found in the tanks during verification. Location to investigate these anomalies between control room recordsand TSI with resolution/ rectification of the error. 4. A difference of 2.2 Deg. C. was observed between physical product temperature verified and the TAS temperature as recorded in TSI. The difference is beyond the permissible limit of 1 deg. C. Location to investigate the reasons for this difference and submit resolution/ rectification to zone. 5. Densitometer recordings in TAS is showing significant variations as compared to the actual physical measurements with the help of hydrometer and thermometers. Location to take up with TAS vendor for immediate rectification of this error so as to have acceptable accuracy. | 3.7 | Inventory physical dip of minimum two tanks taken | 1308 | SITARGANJ DEPOT | Corrective actions to be taken as per the observations during the the next CAMC visit of the TAS vendor which is scheduled during Feb'26 end. 1. Issue of TSI of TK01 is to be rectified 2. Investigation for variation beyond permissible limit of 3mm 3. TSI of Tanks to be checked for abnormality 4. TSI of Tanks to be checked for abnormality 5. Erroernious reading from Densitometer to be cross checked and verified with Physical one | SOD | Marketing | NUZ | 2026-03-03 | THIRD PARTY ERRORS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-03 | AUD-2026-02-2000010854ACN-2026-02-4000121492 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121492 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121492 | 532 | 8294 | 21 | 8294 | 230 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121492 | AUD-2026-02-2000010854ACN-2026-02-4000121492 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 42
M MAHESH BABU | 2026-06-22 | AALETI SANTHOSH KUMAR | 2026-06-22 | Fire fighting equipment was functional & Restored by 31.03.2026 | CBOT- SR MGMT INSPECTION | 2026-03-11 | AUD-2026-03-2000011225 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125902 | Closed | AALETI SANTHOSH KUMAR | 2026-06-22 | During the visit, a hands-on equipment trial was conducted without contractual assistance. The following officers demonstrated successful operation: Foam Monitor : Shri. Shiva Krishna . Digital display of FE-1 is not functioning. As informed by location PO has been placed on vendor. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1973 | CASSIMODE BLACK OIL TERMINAL | To expedite and make it function by 31-03-2026. | SOD | Marketing | SZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011225ACN-2026-03-4000125902 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011225ACN-2026-03-4000125902 | 2026-09-22 17:00 | 27.0455 | 294 | >20 | AUD-2026-03-2000011225 - ACN-2026-03-4000125902 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011225ACN-2026-03-4000125902 | AUD-2026-03-2000011225ACN-2026-03-4000125902 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | Manual reconciliation is not carried out at the location except in exceptional cases where dip posting is not possible due to instrument failure. There were zero instances of manual reconciliation during the current quarter.Google Sheet has been updated by the location. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121493 | Closed | SHUKLA SHIVAM | 2026-06-22 | Out of total 2318 tank reconciliations done during the period 1st Apr'25 to 16th Feb'26, only 100 instances of manual dip entries are there in SAP. Reconciliation based on auto dip was done for 95.69% of tanks during the period. Out of the 100 reconciliations done based on manual dips, 46 instances were for month end reconciliations when manual dip entries were mandated by HQO. 35 instances are pertaining to May'25 when SAP issue was faced. | 3.8 | Auto vs Manual reconciliation checked | 1308 | SITARGANJ DEPOT | Location to reduce the instance of manual Reconciliation and update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NUZ | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-25 | AUD-2026-02-2000010854ACN-2026-02-4000121493 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121493 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121493 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121493 | AUD-2026-02-2000010854ACN-2026-02-4000121493 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | Necessary precautions have been implemented to ensure proper draining of product lines before closure of product valves and to avoid abnormal variations. Operational staff have been sensitized regarding the procedure, and as a result, no such instance of abnormalvariation has been observed during the current quarter. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121494 | Closed | SHUKLA SHIVAM | 2026-06-22 | There are only 6 instances of abnormal variations during the period 1st Apr'25 to 16th Feb'26 out of which 5 are pertaining to 15thApr'25 involving tanks TK4, TK2, TK5, TK3 & TK1 with cumulative loss for all these tanks as 382 L only; and, balance 1 instance is pertaining to 8th Jan'2026 involving tank TK5. Location had sent a justifying email on 8th Jan'26 to zone for the reasons for the abnormal loss of 4006L in TK5. Subsequently, on 9th Jan'26, the location witnessed a gain of 2314 L. | 3.9 | Abnormal variations / unused assets reviewed | 1308 | SITARGANJ DEPOT | Location to take necessary precautions in future to avoid such instance of abnormal variation due to hasty operations of closure ofproduct valves without draining of product lines in the UG tanks which was the reason for abnormal variation | SOD | Marketing | NUZ | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121494 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121494 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121494 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121494 | AUD-2026-02-2000010854ACN-2026-02-4000121494 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | TFMS-SAP reconciliation achieved 100% for April 2026. TFMS-SAP reconciliation achieved 100% for May 2026. TFMS-SAP reconciliationis 100% for June 2026 (till date). Regular monitoring is being carried out to maintain 100% TFMS-SAP reconciliation. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121495 | Closed | SHUKLA SHIVAM | 2026-06-22 | Avg. TFMS-SAP reconciliation % for the period Apr'25 to Jan'26 is 95%. | 3.10 | TFMS/SAP reconciliation checked | 1308 | SITARGANJ DEPOT | Location to further improve the % of TFMS-SAP reconciliation. | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121495 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121495 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121495 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121495 | AUD-2026-02-2000010854ACN-2026-02-4000121495 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | "1. Daily MFM Vs. BCU Vs. SAP Comparison (Bay-wise): Daily bay-wise MFM Vs. BCU Vs. SAP comparison records are being maintained asper the corporation's requirement. The records are duly verified and signed by the TAS Officer, Planning Officer, and Location In-charge of Sitarganj IRD. 2. Modification of TAS Output: The required modification in the TAS output has been completed through the TAS vendor." | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121496 | Closed | SHUKLA SHIVAM | 2026-06-22 | Dispatches as per MFM totalizer difference and BCU totalizer difference is being compared by the location on daily basis and printouts with signature of TAS officer, Planning Officer as well as LIC. However, bay-wise invoice quantity which is present in the TAS is not recorded in the format being signed daily (cumulative comparison is being done between invoice, MFM & BCU). Further, the TAS day end report is not having the daily summary portion which has been taken up by the location with the TAS vendor for inclusion. | 3.11 | MFM vs BCU totalizer comparison checked | 1308 | SITARGANJ DEPOT | 1. Location to keep daily MFM Vs. BCU Vs. SAP comparison (bay-wise) duly signed as per the corporation's requirement. 2. Location to get the TAS output modified thru the TAS vendor before Feb'26 end. | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121496 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121496 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121496 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121496 | AUD-2026-02-2000010854ACN-2026-02-4000121496 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | The signatures of the TT Gantry Officer, TAS Officer, and Location In-charge (LIC) are being obtained on all local loading reports,and the records are being maintained regularly. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121497 | Closed | SHUKLA SHIVAM | 2026-06-22 | Location is maintaining day-wise local loading report along with other day-end reports. Additional, a month-wise consolidated system generated report with dates is also being maintained as printout taken. However, none of these printouts are being signed by any of the officers. | 3.14 | Local loading checks (if applicable) | 1308 | SITARGANJ DEPOT | Location to ensure signature of all the local loading reports by TT Gantry Officer, TAS Officer as well as LIC on all the days. | SOD | Marketing | NUZ | 2026-02-26 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-26 | AUD-2026-02-2000010854ACN-2026-02-4000121497 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121497 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121497 | 532 | 8294 | 21 | 8294 | 235 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121497 | AUD-2026-02-2000010854ACN-2026-02-4000121497 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 42
|  | ADITYA ASHUTOSH | 2026-06-22 | 1. OISD Status: N/A 2. PCSA Status: Audit was conducted on 3rd Jan 2023, total observations were 43. All observations were complied in time bound manner. 3. Comphrensive/MDSA Status: Audit was conducted from 7th Oct -10 oct 2025, total observations were 90 out of which 5 Points pending which are related to NPCB and tendering under progress for same from HQO. 4. SSA Status: Audit was conducted from 3rd sep - 10 th Sep 2025, Total observations were 53. All points complied. ( Fire noc received, Factory layout renwedand approved, CEA license ammended and approved after CEA inspector visit ) 5. T4S Audit Status: Audit was conducted from 4th - 6th Aug 2023, Total observations were17 and all observations were complied in time bound manner. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121951 | Completed | PANWAR VIPIN SINGH | 2026-03-25 | 1. OISD Status: N/A 2. PCSA Status: Audit was conducted on 3rd Jan 2023, total observations were 43. All observations were complied in time bound manner. 3. Comphrensive/MDSA Status: Audit was conducted from 7th Oct -10 oct 2025, total observations were 90 out of which 14 observations are pending. 4. SSA Status: Audit was conducted from 3rd sep - 10 th Sep 2025, Total observations were 53,out of which 2 observations are pending. 5. T4S Audit Status: Audit was conducted from 4th - 6th Aug 2023, Total observations were17 and all observations were complied in time bound manner. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1308 | SITARGANJ DEPOT | Audit observations must be complied with in a time-bound manner, and their closure should be supported with adequate documentation and proof of compliance. | SOD | Marketing | NUZ | 2026-07-31 |  | 2 |  | S2 | F1 | 2026-07-31 | AUD-2026-02-2000010854ACN-2026-02-4000121951 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121951 | 2026-08-26 17:00 | 54.0455 | 333 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121951 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW | AUD-2026-02-2000010854ACN-2026-02-4000121951 |  | AUD-2026-02-2000010854ACN-2026-02-4000121951 | 21 |  | 26 | 80 | 0 | 0 | 48
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | 1. Timely availability of TTs for loading by transporters: TTs are generally being made available on time for loading. Further, with zonal approval, the depot operating timing has been revised from 08:30–17:00 hrs to 09:00–17:30 hrs, resulting in improved TT availability during morning hours. 2. Availability of drivers for hilly routes in 12 KL TTs: Drivers authorized for hilly routes have been arranged for all 12 KL TTs except 5 TTs. Regular follow-up is being carried out with the transporter to ensure compliance for the remaining TTs. 3. Rotation of TTs for bridging operations: The agreed TT rotation roster was implemented during the lean season. However, due to the current high market demand, all available TTs are being utilized for bridging operations to ensure uninterrupted product supply. 4. Branding of TTs: Branding has been completed for all TTs except 2 TTs. Follow-up with the transporteris ongoing to complete the remaining branding at the earliest. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121952 | Closed | SHUKLA SHIVAM | 2026-06-22 | VC meeting with all Transporters and DCTs was done on 18.02.2026 and advised them to follow all safety instructions including VTS guidleines. Also discussed their issues and provided resolutions in line with applicable tender terms and guidelines for further clarity and improvement. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1308 | SITARGANJ DEPOT | 1. Timely availability of TTs for loading by transporters. 2. All 12MT TTs transporters to provide drivers who can carry loads to hilly region- currently, a few 12MT TTs are getting only plain region loads. 3. Rotation of TTs based on location based roaster agreed during the VC/ meeting with transporters for bridging of product to be implemented. 4. Branding of TTs and deduction of penalties after reasonable time given to transporters for implementation of branding. | SOD | Marketing | NUZ | 2026-03-23 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-23 | AUD-2026-02-2000010854ACN-2026-02-4000121952 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121952 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121952 | 532 | 8294 | 21 | 8294 | 210 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121952 | AUD-2026-02-2000010854ACN-2026-02-4000121952 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | IT assets segregated, major IT assets are usable and remaining 6 assets details sent to IT department as a part of scrap disposal committee. Same shall be disposed after recommendation from IT department. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121955 | Closed | SHUKLA SHIVAM | 2026-06-22 | A lot of E-Scrap was observed kept inside the ware-house/ store room adjoining the Admin Building. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1308 | SITARGANJ DEPOT | Location to seggregate the e-waste (old assets) lying in the store room and initiate RFD for disposal of the same so as to make thelocation scrap-free by Mar'26 end as per the HQO guidelines. | SOD | Marketing | NUZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010854ACN-2026-02-4000121955 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121955 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121955 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121955 | AUD-2026-02-2000010854ACN-2026-02-4000121955 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 42
ADITYA ASHUTOSH | 2026-06-22 | SHUKLA SHIVAM | 2026-06-22 | 1. Location has segregated scrap at scrap yard and one LOT of scrap sold to M/S Ishaal Trading and M/S Waseem and same uplifted by vendors. 2. Remaining misc. scrap auction ( auction no. MSTC/25-26/69963 ) scheduled on 26.03.2026. 3. IT assets segregated, major IT assets are usable and remaining 6 assets details sent to IT department as a part of scrap disposal committee. Same shall be disposed after recommendation from IT department." | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-02-4000121956 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | Disposal of scrap lying in the location. | 5.1 | High priority areas requiring immediate action. | 1308 | SITARGANJ DEPOT | Disposal of scrap lying in the location. | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121956 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121956 | 2026-08-26 17:00 | 54.0455 | 294 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121956 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121956 | AUD-2026-02-2000010854ACN-2026-02-4000121956 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 42
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | "Following pending issues were discussed : 1. Budget shifting for GL code of calibration charges. 2. Finalisation of PO for Housekeeping and Handling services 3. BG related issues of TAS vendor and CCTV vendor. 4. TAS related issues of TAS vendor. A VC was conducted by DGM Operations & Automation, NZ-OND on 16th Feb'26 along with the TAS officer & LIC Sitarganj in which all the pending issues were discussed with the TAS AMC vendor (M/s. ICON). Time-lines for closure of all the pending TAS issues were agreed upon by the vendor and a detailed MOM was prepared for the meeting." | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122509 | Closed | SHUKLA SHIVAM | 2026-06-22 | Following pending issues were discussed : 1. Budget shifting for GL code of calibration charges. 2. Finalisation of PO for Housekeeping and Handling services 3. BG related issues of TAS vendor and CCTV vendor. 4. TAS related issues of TAS vendor. A VC was conducted by DGM Operations & Automation, NZ-OND on 16th Feb'26 along with the TAS officer & LIC Sitarganj in which all the pending issues were discussed with the TAS AMC vendor (M/s. ICON). Time-lines for closure of all the pending TAS issues were agreed upon by the vendor and a detailed MOM was prepared for the meeting. | 1.3 | Pending issues reviewed | 1308 | SITARGANJ DEPOT | 1. Location to take up with HQO thru zone for allocation of budget for the CE 2. Location to obtain workability of rates from the contractor and submit to CPO-NZ. 3. Location to obtain request from the TAS-CAMC provider as discussed during the VC with the vendor. 4. Location to maintain follow-up with the vendor to ensure closure of the pending issues as per the agreed time-lines | SOD | Marketing | NUZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-15 | AUD-2026-03-2000011209ACN-2026-03-4000122509 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122509 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122509 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122509 | AUD-2026-03-2000011209ACN-2026-03-4000122509 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | "1. Scrap Disposal: All scrap materials were disposed of through auction in June 2026. Only E-scrap is presently remaining at the location, and necessary action for its disposal is being pursued. 2. Branding of Remaining TTs: Branding has been completed for all TTs except 2 TTs. Follow-up with the transporter is ongoing to complete the remaining branding at the earliest." | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122510 | Closed | SHUKLA SHIVAM | 2026-06-22 | Earlier action points of operations audit/ MDSA audit etc checked and advised to make location scrap free by March'26 end and to ensure 100% branding of Tank Trucks. | 1.4 | Earlier action points status checked | 1308 | SITARGANJ DEPOT | 1. Scrap disposal to be ensured. 2. Branding of all the remaining TTs | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122510 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122510 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122510 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122510 | AUD-2026-03-2000011209ACN-2026-03-4000122510 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | All circular compliances have been reviewed by the Location In-charge (LIC), and the compliance confirmation has been provided. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122511 | Closed | SHUKLA SHIVAM | 2026-06-22 | VTS and EM lock circulars compliance review done. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1308 | SITARGANJ DEPOT | All circular compliance shall be reviewed by LIC and confirmation to be provided | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122511 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122511 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122511 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122511 | AUD-2026-03-2000011209ACN-2026-03-4000122511 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | "TT Exit Time has improved to 23.01 minutes in the current quarter as compared to 25.33 minutes in the previous quarter. TT Loading Rate has improved to 900 LPM in the current quarter as compared to 873.81 LPM in the previous quarter. Cycle Time is 69.27 minutes in the current quarter against 68.91 minutes in the previous quarter. The marginal increase was due to the non-operation of one bay because of a DCV malfunction. The issue was resolved during the CAMC visit conducted from 15–18 June, and further improvement is expected. Branding has been completed for 99% of TTs, with only 2 TTs remaining. Only 5 instances of night driving were observed during the current quarter. Continuous monitoring of VTS alerts and TT movements is being carried out to minimize night driving and speed violations." | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122512 | Closed | SHUKLA SHIVAM | 2026-06-22 | Officers were advised to improve operational parameters like first two hours loading target, improvement in cycle time, TT exit time, TT loading LPM, 100% TTs branding, Nil Night driving and speed violations etc. | 1.8 | Improvement plans discussed | 1308 | SITARGANJ DEPOT | a) first two hours loading target to be ensured along with improvement in TT exit time & LPM b) TT Branding to be ensured c) Nil Night Driving to be ensured. | SOD | Marketing | NUZ | 2026-03-23 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-23 | AUD-2026-03-2000011209ACN-2026-03-4000122512 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122512 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122512 | 532 | 8294 | 21 | 8294 | 210 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122512 | AUD-2026-03-2000011209ACN-2026-03-4000122512 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | The effectiveness of mock drills is being ensured through proper training and clear communication of roles and responsibilities to all concerned personnel. The required action has been completed and is being regularly followed during mock drills. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122515 | Closed | SHUKLA SHIVAM | 2026-06-22 | Emergency response preparedness was verified by conducting a mock drill based on a scenario in which a fire broke out at Bay No. 01after the driver moved the TT without removing the unloading hoses and earthing cleat. This resulted in the hoses being pulled out,causing product spillage and a static spark subsequently ignited the spilled product, leading to a fire. All equipment were tested and performed well. However, Delay observed in supplying Foam barrel to Fire Fighting team and effective operation of Foam monitor was not observed. Mock drills must be conducted in letter and spirit and all members should be clear with their roles and responsibilities. | 2.5 | Emergency response preparedness reviewed | 1308 | SITARGANJ DEPOT | Effectiveness of the mock drill must be ensured through proper training and clear communication of roles and responsibilities to all concerned personnel. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122515 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122515 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122515 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122515 | AUD-2026-03-2000011209ACN-2026-03-4000122515 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Lighting arrangement has been provided at Bay No. 06 and the work has been completed. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122514 | Closed | SHUKLA SHIVAM | 2026-06-22 | On 16/02/2026 @ 20:00 hrs, Lux level chaecked a various locations including 1. TT Gantry Bay No - 01 - 115 Lux 2. Admin Building - 300 Lux 3. Product Pump House - 366 Lux 4. U/G Tank Farm Area - 56 Lux 5. TT Sealing/Locking bay - 260 Lux 6. Roads - 26 Lux 7. Lighs are required in newly extended Bany no-06 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1308 | SITARGANJ DEPOT | 7. Lighting arangement to be provided in Bay No-06 | SOD | Marketing | NUZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122514 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122514 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122514 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122514 | AUD-2026-03-2000011209ACN-2026-03-4000122514 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | The gate in front of the store room adjoining the Admin Building has been kept in locked condition. Personnel movement is being carried out only through the CBAC system as advised. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122516 | Closed | SHUKLA SHIVAM | 2026-06-22 | During the Visit Access control at main gate was checked and found that CBAC Systen was finctional alongwith Biomatric operational at Maingate, Entry to Licence area and Control room. | 2.8 | Access control systems checked | 1308 | SITARGANJ DEPOT | Gate in front of the store-room adjoining the Admin Building should be kept in locked condition and personnel should move only thruthe CBAC system. | SOD | Marketing | NUZ | 2026-02-28 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122516 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122516 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122516 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122516 | AUD-2026-03-2000011209ACN-2026-03-4000122516 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | 1. Maintenance of Open Path HCD: The Open Path HCD has been repaired, recalibrated, and reinstalled. The system is functioning satisfactorily. 2. Numbering over each ESD: Numbering has been provided on all ESDs as advised. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122517 | Closed | SHUKLA SHIVAM | 2026-06-22 | 1. Total 2 Nos of HCD available at the location. Out of which 01 nos is Open path and 01 Nos is Point type HCD. Open Path HCD is under maintenence as Calibration is required to be done hence it has been handed over to TAS vendor under AMC contrtact. Point type HCD No: 01 Located at Pump House operated; and found to be operated at 39% LEL 2. Tot 13 No of ESD available at the location. The Functionality of ESD has been checked during Mock drill conducted on 17th Feb'26 and found satisfactory. ESD NO: 07 activated placedin Control room and TAS log generated 3. All tanks are underground therefore HVLR and RSFPS is not available at the location | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1308 | SITARGANJ DEPOT | 1. Expedite the maintenance of Open path HCD 2. Numbering over each ESD to be mentioned | SOD | Marketing | NUZ | 2026-03-15 | INSTRUMENTATION OR ALARM FAILURES | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-03-2000011209ACN-2026-03-4000122517 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122517 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122517 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122517 | AUD-2026-03-2000011209ACN-2026-03-4000122517 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | All the observations pertaining to TT No. UP25FT8460 have been complied with by the transporter. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122518 | Closed | SHUKLA SHIVAM | 2026-06-22 | TT fitting and safety check of TT No UP25FT8460 was done. Observations are as follows: 1. Double convex side mirror to be fixed for visibilty of blind spots. 2. Welding to be done on the ends of hinge pin to avoid removal. 3. Check the welding of the hinges laps are properly done for complete surface of the valve box. | 3.1 | TT fittings & discipline checked | 1308 | SITARGANJ DEPOT | Compliance of the observation made w.r.t. TT inspected to be ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NUZ | 2026-03-15 | THIRD PARTY ERRORS | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-03-2000011209ACN-2026-03-4000122518 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122518 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122518 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122518 | AUD-2026-03-2000011209ACN-2026-03-4000122518 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | The VTS monitoring mechanism has been established and is being implemented at the location. A register is being maintained for monitoring and recording VTS-related observations and compliance. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122519 | Closed | SHUKLA SHIVAM | 2026-06-22 | VTS deviations reviewed and discussed, also reviewed the register of alerts monitoring remarks. Advised to start a mechanism so that it could be ensured that all TTs are covered periodically. | 3.3 | VTS deviations reviewed | 1308 | SITARGANJ DEPOT | Compliance w.r.t. the VTS monitoring mechanish is to be established | SOD | Marketing | NUZ | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-02-25 | AUD-2026-03-2000011209ACN-2026-03-4000122519 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122519 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122519 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122519 | AUD-2026-03-2000011209ACN-2026-03-4000122519 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Sitarganj is a bridging location and receives pre-blended Gasohol from Bareilly Depot. Q&Q checks are carried out for all incoming TTs, and the ethanol content is generally found to be within the acceptable range of 19–20%. In case the ethanol content is found tobe outside the acceptable range, the matter is immediately communicated to Bareilly Depot for necessary corrective action in the blending process. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122520 | Closed | SHUKLA SHIVAM | 2026-06-22 | Location is receiving E20 MS from Aonla. Location is physically verifying Ethanol blend in the product received for all the compartments received. During the visit, TT No. UP25HT822 was verified and found to be blended with 19% to 19.5% Ethanol which is in-line QC requirement. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1308 | SITARGANJ DEPOT | Blending to be achieved @ 20% | SOD | Marketing | NUZ | 2026-03-25 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011209ACN-2026-03-4000122520 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122520 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122520 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122520 | AUD-2026-03-2000011209ACN-2026-03-4000122520 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | The EM Lock monitoring mechanism has been established and implemented at the location. Compliance is being monitored regularly, anda register is being maintained for TT inspections and EM Lock verification. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122521 | Closed | SHUKLA SHIVAM | 2026-06-22 | EM lock SOP compliance verified and advised to start a mechanism so that it could be ensured that all TTs are covered on monthly basis. | 3.5 | EM Lock SOP compliance verified | 1308 | SITARGANJ DEPOT | Compliance w.r.t. the EM Lock monitoring mechanish is to be established | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122521 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122521 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122521 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122521 | AUD-2026-03-2000011209ACN-2026-03-4000122521 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Issue of TSI of TK01: The TSI issue of TK01 has been rectified and is functioning satisfactorily. Investigation for variation beyond permissible limit of 3 mm: Dip readings of TK10 and TK11 were corrected with the support of M/s ICON Controls. TAS is presentlydisplaying the correct dip readings, and the tanks remain under observation. TSI of Tanks to be checked for abnormality: All TSIshave been checked and verified. All TSIs are functioning properly. TSI of Tanks to be checked for abnormality: The tank gauging system has been checked, and no abnormalities have been observed. Erroneous reading from Densitometer to be cross-checked and verified with physical readings: In the presence of M/s ICON Controls, the densitometer was tested in HSD and Gasohol samples. The density values displayed in TAS matched the manual densitometer readings, confirming satisfactory performance. Additionally, the densitometer of TK-08 (Hexane) was sent for verification and was found satisfactory. The vendor has suggested tank cleaning as a preventive measure. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122522 | Closed | SHUKLA SHIVAM | 2026-06-22 | Gauging of all the tanks at the location was done during the visit on 17th Feb'26 and details are provided in the Annexure. Following observations were made during the exercise. 1. TSI of TK01 is not displaying product temperature. Location to take necessary corrective action and confirm to zone. 2. A difference of 5mm in product level was observed in case of TK10. Location to investigate the reasons for this variation beyond permissible limit of 3mm and revert back with findings/ corrective action taken. 3. TSI of TK10 & TK11 were showing water levels in the tanks where as the system records in the control room are showing NIL water levels. Physically also, no water was found in the tanks during verification. Location to investigate these anomalies between control room recordsand TSI with resolution/ rectification of the error. 4. A difference of 2.2 Deg. C. was observed between physical product temperature verified and the TAS temperature as recorded in TSI. The difference is beyond the permissible limit of 1 deg. C. Location to investigate the reasons for this difference and submit resolution/ rectification to zone. 5. Densitometer recordings in TAS is showing significant variations as compared to the actual physical measurements with the help of hydrometer and thermometers. Location to take up with TAS vendor for immediate rectification of this error so as to have acceptable accuracy. | 3.7 | Inventory physical dip of minimum two tanks taken | 1308 | SITARGANJ DEPOT | Corrective actions to be taken as per the observations during the the next CAMC visit of the TAS vendor which is scheduled during Feb'26 end. 1. Issue of TSI of TK01 is to be rectified 2. Investigation for variation beyond permissible limit of 3mm 3. TSI of Tanks to be checked for abnormality 4. TSI of Tanks to be checked for abnormality 5. Erroernious reading from Densitometer to be cross checked and verified with Physical one | SOD | Marketing | NUZ | 2026-03-03 | THIRD PARTY ERRORS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-03 | AUD-2026-03-2000011209ACN-2026-03-4000122522 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122522 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122522 | 532 | 8294 | 21 | 8294 | 230 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122522 | AUD-2026-03-2000011209ACN-2026-03-4000122522 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Manual reconciliation is not carried out at the location except in exceptional cases where dip posting is not possible due to instrument failure. There were zero instances of manual reconciliation during the current quarter. The Google Sheet provided by the Zone has been updated by the location team with all relevant details. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122523 | Closed | SHUKLA SHIVAM | 2026-06-22 | Out of total 2318 tank reconciliations done during the period 1st Apr'25 to 16th Feb'26, only 100 instances of manual dip entries are there in SAP. Reconciliation based on auto dip was done for 95.69% of tanks during the period. Out of the 100 reconciliations done based on manual dips, 46 instances were for month end reconciliations when manual dip entries were mandated by HQO. 35 instances are pertaining to May'25 when SAP issue was faced. | 3.8 | Auto vs Manual reconciliation checked | 1308 | SITARGANJ DEPOT | Location to reduce the instance of manual Reconciliation and update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NUZ | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-25 | AUD-2026-03-2000011209ACN-2026-03-4000122523 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122523 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122523 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122523 | AUD-2026-03-2000011209ACN-2026-03-4000122523 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Necessary precautions have been implemented to ensure proper draining of product lines before closure of product valves. Operational staff have been sensitized regarding the correct operating procedure, and no such instance of abnormal variation has been observedduring the current quarter. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122524 | Closed | SHUKLA SHIVAM | 2026-06-22 | There are only 6 instances of abnormal variations during the period 1st Apr'25 to 16th Feb'26 out of which 5 are pertaining to 15thApr'25 involving tanks TK4, TK2, TK5, TK3 & TK1 with cumulative loss for all these tanks as 382 L only; and, balance 1 instance is pertaining to 8th Jan'2026 involving tank TK5. Location had sent a justifying email on 8th Jan'26 to zone for the reasons for the abnormal loss of 4006L in TK5. Subsequently, on 9th Jan'26, the location witnessed a gain of 2314 L. | 3.9 | Abnormal variations / unused assets reviewed | 1308 | SITARGANJ DEPOT | Location to take necessary precautions in future to avoid such instance of abnormal variation due to hasty operations of closure ofproduct valves without draining of product lines in the UG tanks which was the reason for abnormal variation | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122524 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122524 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122524 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122524 | AUD-2026-03-2000011209ACN-2026-03-4000122524 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | TFMS-SAP reconciliation achieved 100% for April 2026. TFMS-SAP reconciliation achieved 100% for May 2026. TFMS-SAP reconciliationis 100% for June 2026 (till date). Regular monitoring is being carried out to maintain 100% TFMS-SAP reconciliation. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122525 | Closed | SHUKLA SHIVAM | 2026-06-22 | Avg. TFMS-SAP reconciliation % for the period Apr'25 to Jan'26 is 95%. | 3.10 | TFMS/SAP reconciliation checked | 1308 | SITARGANJ DEPOT | Location to further improve the % of TFMS-SAP reconciliation. | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122525 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122525 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122525 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122525 | AUD-2026-03-2000011209ACN-2026-03-4000122525 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | 1. Daily MFM Vs. BCU Vs. SAP Comparison (Bay-wise): Daily bay-wise MFM Vs. BCU Vs. SAP comparison records are being maintained as per the corporation's requirement. The records are duly verified and signed by the TAS Officer, Planning Officer, and Location In-charge (LIC). 2. Modification of TAS Output: The required modification in the TAS output has been completed through the TAS vendor. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122526 | Closed | SHUKLA SHIVAM | 2026-06-22 | Dispatches as per MFM totalizer difference and BCU totalizer difference is being compared by the location on daily basis and printouts with signature of TAS officer, Planning Officer as well as LIC. However, bay-wise invoice quantity which is present in the TAS is not recorded in the format being signed daily (cumulative comparison is being done between invoice, MFM & BCU). Further, the TAS day end report is not having the daily summary portion which has been taken up by the location with the TAS vendor for inclusion. | 3.11 | MFM vs BCU totalizer comparison checked | 1308 | SITARGANJ DEPOT | 1. Location to keep daily MFM Vs. BCU Vs. SAP comparison (bay-wise) duly signed as per the corporation's requirement. 2. Location to get the TAS output modified thru the TAS vendor before Feb'26 end. | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122526 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122526 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122526 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122526 | AUD-2026-03-2000011209ACN-2026-03-4000122526 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | All local loading reports are being duly signed by the TT Gantry Officer, TAS Officer, and Location In-charge (LIC). The records are being maintained regularly and compliance is being ensured on all days. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122527 | Closed | SHUKLA SHIVAM | 2026-06-22 | Location is maintaining day-wise local loading report along with other day-end reports. Additional, a month-wise consolidated system generated report with dates is also being maintained as printout taken. However, none of these printouts are being signed by any of the officers. | 3.14 | Local loading checks (if applicable) | 1308 | SITARGANJ DEPOT | Location to ensure signature of all the local loading reports by TT Gantry Officer, TAS Officer as well as LIC on all the days. | SOD | Marketing | NUZ | 2026-02-26 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-26 | AUD-2026-03-2000011209ACN-2026-03-4000122527 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122527 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122527 | 532 | 8294 | 21 | 8294 | 235 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122527 | AUD-2026-03-2000011209ACN-2026-03-4000122527 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Fortnightly cleaning of TT parking area with water, if felt necessary: Fortnightly cleaning of the TT parking area is being carried out as required. 2. Sealing of gaps between window frames and walls: The work will be taken up along with the upcoming civil maintenance work at the location. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122528 | Closed | SHUKLA SHIVAM | 2026-06-22 |  | 3.15 | Housekeeping & PPE usage checked | 1308 | SITARGANJ DEPOT | 1. Fortnightly cleaning of TT parking area with water, if felt necessary 2. Sealing of Gaps between window frames and walls | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122528 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122528 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122528 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122528 | AUD-2026-03-2000011209ACN-2026-03-4000122528 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | xx | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122529 | Closed | SHUKLA SHIVAM | 2026-06-22 |  | 3.16 | Earth pits / boundary / vegetation control checked | 1308 | SITARGANJ DEPOT | XX | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122529 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122529 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122529 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122529 | AUD-2026-03-2000011209ACN-2026-03-4000122529 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | All MOCs are being approved and closed in a time-bound manner as per the prescribed procedure. There are no MOCs pending during FY 2026-27 till date. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122530 | Closed | SHUKLA SHIVAM | 2026-06-22 | During FY 2025-26, Total 07 Nos of MoC's were raised and 06 MoC's were approved. Only One MoC related to TT Parking SOP is under process | 3.17 | MOC status reviewed | 1308 | SITARGANJ DEPOT | MOC to be approved and closer of the same in time bound manner | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011209ACN-2026-03-4000122530 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122530 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122530 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122530 | AUD-2026-03-2000011209ACN-2026-03-4000122530 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | TTs are generally being made available on time for loading. Further, with zonal approval, the depot operating timing has been revised from 08:30–17:00 hrs to 09:00–17:30 hrs, resulting in improved TT availability during morning hours. Drivers authorized for hilly routes have been arranged for all 12 KL TTs except 5 TTs. Regular follow-up is being carried out with the transporter for the remaining TTs. The agreed TT rotation roster was implemented during the lean season. However, due to the current high market demand, all available TTs are being utilized for bridging operations to ensure uninterrupted product supply. Branding has been completed for 99% of TTs, with only 2 TTs remaining. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122532 | Closed | SHUKLA SHIVAM | 2026-06-22 | VC meeting with all Transporters and DCTs was done on 18.02.2026 and advised them to follow all safety instructions including VTS guidleines. Also discussed their issues and provided resolutions in line with applicable tender terms and guidelines for further clarity and improvement. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1308 | SITARGANJ DEPOT | 1. Timely availability of TTs for loading by transporters. 2. All 12MT TTs transporters to provide drivers who can carry loads to hilly region- currently, a few 12MT TTs are getting only plain region loads. 3. Rotation of TTs based on location based roaster agreed during the VC/ meeting with transporters for bridging of product to be implemented. 4. Branding of TTs and deduction of penalties after reasonable time given to transporters for implementation of branding. | SOD | Marketing | NUZ | 2026-03-23 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-23 | AUD-2026-03-2000011209ACN-2026-03-4000122532 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122532 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122532 | 532 | 8294 | 21 | 8294 | 210 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122532 | AUD-2026-03-2000011209ACN-2026-03-4000122532 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | Cleaning of the TT Crew Waiting Room has been carried out and is being maintained regularly. Necessary protection has been provided to the fire water hydrant line in the TT parking area to prevent damage from parked TTs. Paver blocks near the soak pit in the TTparking area have been properly locked and secured. The vertical garden has been maintained properly. Recovery trays near Bay Nos. 04, 05, and 06 have been cleaned and are being monitored regularly. Proper covering arrangement has been provided for the foam barrels placed in the field. Hydrotesting status of the 75 Kg DCP cylinder and associated CO₂ cylinder has been verified and necessary compliance has been ensured. The oversized double compression gland of the motor in the calibration shed has been replaced/corrected. Sand buckets across the premises have been refilled and sand quality has been restored by removing lumps. Leakage observed inboth fire engines and both jockey pumps at the motor/engine coupling points has been rectified. Lighting arrangement has been provided at Bay No. 06. Numbering of all smoke detectors (false ceiling and false flooring) in the Control Room Building has been completed. TT branding has been completed for all TTs except 2 TTs, for which follow-up with the transporter is in progress. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122533 | Closed | SHUKLA SHIVAM | 2026-06-22 | 1. Cleaning of TT Crew waiting room is required 2. Arrangement to be made to protect Fire water Hydrant Line at TT Parking area. Parked TT may cause damage to the facility 3. Paver block to be properly locked near Soal Pit in TT parking area 4. Vertical garden to be maintained properly 5. Presence of Oil is found in the recovery Tray placed near Bay no: 04 / 05 / 06 6. Proper covering arrangement to be provised for Foam Barrel placed in field. 7. 75 Kg DCP cylinder has been hydrotested 01/03/2025, however it cant be ascertained that external CO2 cylinder hydrotesting was done or not. Last testing date 12/10/2020 8. Double compression gland of Motor placed in Calibration shed was found to be over size 9. Sand buckets found to be partially filled with Sand in entire premises and also lumps found. 10. Leakage observed in both the Fire Engine and both Jockey pumps from Motor/Engine coupling point. 11. Lighting arrangement is to provided at Bay no-06 12. Numbering of Smoke Detectors (both False sealing & False flooring) to be done in Control room building 13. Some TTs have been observed without proper branding as per the transportation tender’s requirement. Location to take-up with the respective transporters to ensure proper branding by Feb’26 end. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1308 | SITARGANJ DEPOT | 1. The room must be cleaned thoroughly, and measures should be taken to prevent the ingress of dust. 2. Prevention measures to be taken to avoid any untoward incident 3. Paver blocks to be locked properly 4. Virtical garden to be maintained 5. Mechanism to beemplied to avoid any oil presence 6. Foam Barel Shed to be provised 7. Hydrotesting of CO2 cylinder is to be done 9. Correct size of Double compression glan to be used 10. Leakage to be arrested in Fire Engines and Jockey pumps. 11. Overhead light in Bay No06 to be installed 12. Numbering of Smoke detectors to be done for visual identification. 13. TT Branding to be ensured and 100% compliance to be ensured | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122533 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122533 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122533 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122533 | AUD-2026-03-2000011209ACN-2026-03-4000122533 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | The Open Path HCD has been repaired, recalibrated, and reinstalled by the TAS vendor under the AMC contract. The system is now operational and functioning satisfactorily. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122534 | Closed | SHUKLA SHIVAM | 2026-06-22 | Open Path HCD is under maintenence as Calibration is required to be done hence it has been handed over to TAS vendor under AMC contrtact. | 4.2 | Maintenance activities reviewed | 1308 | SITARGANJ DEPOT | HCD to be installed post calibration and confirmation to be provided to Zone | SOD | Marketing | NUZ | 2026-03-15 | THIRD PARTY ERRORS | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-03-2000011209ACN-2026-03-4000122534 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122534 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122534 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122534 | AUD-2026-03-2000011209ACN-2026-03-4000122534 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | . IT assets segregated, major IT assets are usable and remaining 6 assets details sent to IT department as a part of scrap disposalcommittee. Same shall be disposed after recommendation from IT department." | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122535 | Closed | SHUKLA SHIVAM | 2026-06-22 | A lot of E-Scrap was observed kept inside the ware-house/ store room adjoining the Admin Building. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1308 | SITARGANJ DEPOT | Location to seggregate the e-waste (old assets) lying in the store room and initiate RFD for disposal of the same so as to make thelocation scrap-free by Mar'26 end as per the HQO guidelines. | SOD | Marketing | NUZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011209ACN-2026-03-4000122535 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122535 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122535 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122535 | AUD-2026-03-2000011209ACN-2026-03-4000122535 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 43
ADITYA ASHUTOSH | 2026-06-23 | SHUKLA SHIVAM | 2026-06-22 | All scrap lying at the location has been disposed of through auction in June 2026. | SENIOR MGMT INSPECTION 1308 SITARGANJ | 2026-02-18 14:00 | AUD-2026-03-2000011209 | 2026-02-16 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-03-4000122536 | Closed | SHUKLA SHIVAM | 2026-06-22 | Disposal of scrap lying in the location. | 5.1 | High priority areas requiring immediate action. | 1308 | SITARGANJ DEPOT | Disposal of scrap lying in the location. | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011209ACN-2026-03-4000122536 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011209ACN-2026-03-4000122536 | 2026-08-26 17:00 | 54.0455 | 295 | >20 | AUD-2026-03-2000011209 - ACN-2026-03-4000122536 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011209ACN-2026-03-4000122536 | AUD-2026-03-2000011209ACN-2026-03-4000122536 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 43
AILAVARAPU VENKATA KRISHNA MURTY | 2026-06-25 | DIWAKAR KAMLESH KUMAR | 2026-06-25 | Presently Tank Mode are being selected . | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125092 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-25 | Critical alarms of tank leakage generated due to change in dip level when tank is in dormant mode. | 3.12 | Critical alarms checked & corrective actions reviewed | 3708 | VISAKH NBOT | Correct tank mode to be set before receipt/ dispatch operations | SOD | Marketing | SCR | 2026-03-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-12 | AUD-2026-03-2000011315ACN-2026-03-4000125092 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125092 | 2026-09-18 17:30 | 31.0247 | 297 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125092 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125092 | AUD-2026-03-2000011315ACN-2026-03-4000125092 | 21 | 21 | 26 | 80 | 2 | 1 | 28 | 43
[5 empty] | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140179 | Open |  |  | Emergency exit direction boards to be prominently displayed in all areas. Mobile phones to be provided for external calls in Security & Planning. | 2.5 | Emergency response preparedness reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 |  | 1 |  | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140179 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140179 | 2026-08-22 22:00 | 57.8372 | 303 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140179 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013929ACN-2026-06-4000140179 |  | AUD-2026-06-2000013929ACN-2026-06-4000140179 | 21 |  | 27 | 80 | 1 | 1 | 44
[5 empty] | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140805 | Open |  |  | TT Crew data online updation to be completed. | 6.8 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 |  | 1 |  | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140805 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140805 | 2026-08-22 22:00 | 57.8372 | 303 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140805 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013929ACN-2026-06-4000140805 |  | AUD-2026-06-2000013929ACN-2026-06-4000140805 | 21 |  | 27 | 80 | 1 | 1 | 44
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141151 | Open |  |  | On-Site Mock Fire Drill (Double contingency scenario involving MS product leakage from the downstream flange of ROSOV of tank TK07 and downstream flange leakage from a mainline valve after liquid pumps used for transferring product from VRU to AG- MS tanks) was carried out on 26/05/2026. Positives during both the drills were timely & efficient operation of all safety equipment including sprinklers and foam pourers. Response time by all members of fire drill. Areas of improvement include the following. 1. Replenishment offoam in the foam monitor being used took 2' delay. 2. Mega Phone stopped working during the drill. 3. Leakages were found from the hoses used for fire fighting. 4. Communication from team leaders to the team members was found a bit ineffective with team members acting based on their earlier training experiences. 5. Foam monitor deployed was found overshooting the emergency envisaged area. 6. Hose handling done by the water spray nozzle operator was not as per the norms. 7. Multiple foam nozzles were operated by firecombat team members. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1221 | DELHI TERMINAL | 1. Replenishment drills for foam should be carried out to avoid discontinuous fire fighting thru foam monitors. 2. Mega phones should be kept in prime working conditions and if required, back should be available. 3. Fire Hose pipes should be periodically testedand maintained in prime condition to avoid leakages from them during emergencies. 4. Communication drills should be planned to improve communications and role clarity during drills/ emergencies. 5. Flow controls should be exercised by operator using Foam Monitor to target only the emergy area/ equipment & is surroundings. 6. Hose handling training to be given to the operators. 7. Fire fighting equipment should be deployed strictly as per the instructions from the team leader. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014036ACN-2026-06-4000141151 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141151 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141151 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141151 |  | AUD-2026-06-2000014036ACN-2026-06-4000141151 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141152 | Open |  |  | Total No of CCTV cameras are 57 Nos.. Out of these, one camera viz..Gantry Bay 15-16 is not working since the first week of May'26.Location had sent the faulty camera to M/s. SCORE Information Technologies Ltd. thru RTGP# 11221-R-22916 dtd. 02.05.2026. MOC for the same has been prepared vide MOC No. 3200000829 on date 25.05.2026. Verified 90 days back-up by viewing recording of camera no. Gantry Bay 1-2 for date 11.02.2026. Recording was found available thus ensuring more than 90 days back-up required. | 2.6 | CCTV functioning checked | 1221 | DELHI TERMINAL | 1. Non-operational camera # Gantry Bay 15-16 to be made functional immediately. 2. MOCs in case of change in SOP has to originated and approval taken before implementation of change in SOP. | SOD | Marketing | NZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000014036ACN-2026-06-4000141152 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141152 | 2026-08-27 | 53.7538 | 302 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141152 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141152 |  | AUD-2026-06-2000014036ACN-2026-06-4000141152 | 21 |  | 27 | 80 | 3 | 3 | 44
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141155 | Open |  |  | HVLR- Total 05 No of HVLR are available at the location. HVLR No. 05 – Checked for its movement in all directions with jet as wellas fog mode and found satisfactory. It was operated by Mr. Kuldeep Kumar and his knowledge about the functionality was found satisfactory. The jet flow of the equipment was found to be overshooting the ethanol tanks for which it is provided for protection. Also, leakage was found from the HVLR#4 with its feed gate valve in closed condition. Its foam feed valve was found in closed condition. HVLR No. 03 – Operated by Mr. Likesh and his knowledge about the functionality of its panel was found satisfactory. The operation ofthe HVLR was also found satisfactory with movements happening in all four directions. However, leakage was found from the HVLR withits feed gate valve in closed condition. Location is carrying out monthly testing of HVLRs with the last testing done on 13.04.2026. RSFPS- NA, At Delhi terminal has 7nos. of AG Class A Tanks- all are having Fixed Roof with 5 equipement with IFR. HCD- Open Path HCD No. 03 – Located in the manifold area of Product Pump House was tested with 20% as well as 40% filter. In both cases, local hooter & alarm in TAS room were observed- TAS log was also verified. Location is maintaining month test report of HCD with last testing done on 08.05.2026. ESD- Total 14 Nos. of ESDs are available at the location. The Functionality of ESD# was checked during Mock drill conducted on 26th May'26 and found -. As per OISD 244, functionality of ESD has to be checked during monthly fire drills. Location is carrying out monthly testing of ESDs with last testing done on 28.04.2026. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1221 | DELHI TERMINAL | HVLR: (i) Location to carry out assessment of LPM requirement of all the HVLRs to ensure that they hit the targetted location on the facilities they are supposed to protect. (ii) Location to carry out servicing of inlet gate valves connected all HVLRs to avoid leakages when in closed conditions. (iv) Foam feed valves of HVLRs to be maintained in open condition always. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141155 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141155 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141155 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141155 |  | AUD-2026-06-2000014036ACN-2026-06-4000141155 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141157 | Open |  |  | Thorough checking TT No DL1 GE 4048 was done along with LIC and concerned officer to sensitize the need for proper inspection of TTs in line with the extant circular. Fire extinguisher was operated by the TT Driver and was found satisfactory. | 3.1 | TT fittings & discipline checked | 1221 | DELHI TERMINAL | Compliance of the observation made w.r.t. TT inspected to be ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141157 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141157 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141157 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141157 |  | AUD-2026-06-2000014036ACN-2026-06-4000141157 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141158 | Open |  |  | EM lock checked using Intelligent Key was done for four no of TTs and online report as per requirement was submitted after checking. Plastic dust cover were found broken in few locks location & location has been advise to replace them and confirm to zone. Intelligent key result was observed to be erratic and location has been advised to take up matter with M/s Sterna | 3.5 | EM Lock SOP compliance verified | 1221 | DELHI TERMINAL | New Intelligent key to be taken from M/s Sterna | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141158 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141158 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141158 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141158 |  | AUD-2026-06-2000014036ACN-2026-06-4000141158 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141159 | Open |  |  | Before and after unloading inspection of ethanol TT No: UP21ET1914 was verified physically and found Ok. Leakage oberved form hose connection in TT no TTPB07CF9655. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1221 | DELHI TERMINAL | Location to rectify the hose connection arrangement and confirm | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141159 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141159 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141159 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141159 |  | AUD-2026-06-2000014036ACN-2026-06-4000141159 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141160 | Open |  |  | Housekeeping of the location is found to be good and Green belts is being maintained properly. It was observed during viewing ofCCTV clippings of TT Gantry during loading operations that the TT crew are not fixing the front clip of the harness provided while they access the TT top for gauging/ other related operations. | 3.15 | Housekeeping & PPE usage checked | 1221 | DELHI TERMINAL | Proper usage of double harness should be ensured thru training to TT crew and importance of securing the front clip of the harness should be explained to them during training. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141160 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141160 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141160 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141160 |  | AUD-2026-06-2000014036ACN-2026-06-4000141160 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141161 | Open |  |  | - Earth Pits - Total 247 Earth pits are there at the location. Earth Pit No 95 & 154 Checked and following observations were madew.r.t. displayed/ observed readings during the visit. EP 95 (Product Pump House): Individual Reading (Displayed on Board/ Physically Observed- 1.53 Ω / 0.84 Ω Grid Reading (Displayed on Board/ Physically Observed- 0.45 Ω / 0.25 Ω EP 154 (TK06): Individual Reading (Displayed on Board/ Physically Observed- 1.65 Ω / 0.53 Ω Grid Reading (Displayed on Board/ Physically Observed- 0.52 Ω / 0.02 Ω However, from both the earth-pits, flexible wires were found taken directly from the earth pit connections to the nearby electrical equipment which is not a correct engineering practice. - Boundary- Condition of Boundary wall is found satisfactory, However painting is required, also at some places and Concertina coil needs replacement along with Provision of broken glass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. -Vegetation Control - No Encroaching/Overgrown vegetation was observed across the boundary wall. | 3.16 | Earth pits / boundary / vegetation control checked | 1221 | DELHI TERMINAL | #NAME? | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141161 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141161 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141161 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141161 |  | AUD-2026-06-2000014036ACN-2026-06-4000141161 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141162 | Open |  |  | In 2025-26, a total of 27 MOCs were initiated with the following status reflecting in the system: Closed: 15, Approved-1, In preparation- 1, Rejected- 7 & Incomplete- 3. In the year 2026-27, as on 25.05.2026, only 3 MOCs are reflecting in the system with 1 approved and 2 in submitted status. | 3.17 | MOC status reviewed | 1221 | DELHI TERMINAL | 1. Approved MOC of 2025-26 to be closed suitably. 2. For 2026-27 MOCs, approval for submitted MOCs to be obtained and closure tobe ascertained in time bound manner. | SOD | Marketing | NZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000014036ACN-2026-06-4000141162 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141162 | 2026-08-27 | 53.7538 | 302 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141162 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141162 |  | AUD-2026-06-2000014036ACN-2026-06-4000141162 | 21 |  | 27 | 80 | 3 | 3 | 44
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141163 | Open |  |  | 1. OISD Status - All Observations complied and Nil pending. 2. Comprehensive/MDSA status - Total 115 Observations were there and113 closed. Pending observations are as below 1. Pipeline sun set approval 2. Tank Emergency drain Blind (OISD Guideline) 3. Self Safety Audit Status - Total 43 Observations were there and 42 observations were closed. Pending points are as below 1. TankEmergency drain Blind (OISD Guideline) 4. T4S Audit Status - Pending. Scheduled in June'26. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1221 | DELHI TERMINAL | 2. Comprehensive/MDSA pending points to be complied in a time bound manner. 3. Self Safety Audit pending Point to be complied ina time bound manner. | SOD | Marketing | NZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-06-2000014036ACN-2026-06-4000141163 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141163 | 2026-08-27 | 53.7538 | 486 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141163 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141163 |  | AUD-2026-06-2000014036ACN-2026-06-4000141163 | 21 |  | 27 | 80 | 3 | 3 | 70
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141164 | Open |  |  | 1. In MS Pump no. 1, it was observed that the suction gauge was showing negative pressure reading. 2. Looping of earthing connections was observed at many places including Foam Storage shed, HVLRs, .... Similarly, at some places, multiple earthing connections toequipment were found originating from a single point of the nearby earthing strip. 3. Emergency Trolley placed in front of TT Gantry under the shed was checked. Stretcher was found not kept at the designated place. 4. DFMD installed at the main gate doesn't show indication on one side and its multizone functionality didn't seem accurate. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1221 | DELHI TERMINAL | 1. Root cause for the observation made should be found out like strainer choking, constriction in suction flow, etc... and necessary rectification should be ensured. 2. Independent earthing should be ensured for all electrical equipment and all 3 phase electrical equipment to be provided with double independent earthing connections. 3. Emergency trolley should be maintained with its equipment stored in the designated place. Display of the equipment should be made in hindi as well. 4. DFMD to be attended to for intended functionality. | SOD | Marketing | NZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014036ACN-2026-06-4000141164 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141164 | 2026-08-27 | 53.7538 | 333 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141164 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141164 |  | AUD-2026-06-2000014036ACN-2026-06-4000141164 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141165 | Open |  |  | Routine maintenance activities are being carried out at the location as per the SAP-generated Preventive Maintenance work orders, and compliance is being ensured. Maintenance reports were reviewed. Discussions were held with maintenance officer to sensitize on timely closure of all work orders along with preparation of GRNs. There is delay of 15 day in earthpit schedule maintenance. Location has been advised to complete the same and confirm | 4.2 | Maintenance activities reviewed | 1221 | DELHI TERMINAL | Earthpit schedule maintenance to be expedite and completed | SOD | Marketing | NZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000014036ACN-2026-06-4000141165 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141165 | 2026-08-27 | 53.7538 | 302 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141165 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141165 |  | AUD-2026-06-2000014036ACN-2026-06-4000141165 | 21 |  | 27 | 80 | 3 | 3 | 44
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141166 | Open |  |  | Project status were discussed along with concerned officers in the presence of LICs for time bound closure of all the ongoing projects.Currently Projects are under hold due to Budget Hoiwever location has been advised to float the tender for 4 Nos NPCB Project sothat work can be started on allocation of Budget | 4.3 | Project progress reviewed | 1221 | DELHI TERMINAL | Tender for NPCB Projects to floated and to be brought in ready to place PO stage | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014036ACN-2026-06-4000141166 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141166 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141166 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141166 |  | AUD-2026-06-2000014036ACN-2026-06-4000141166 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141167 | Open |  |  | Only few misc scrap valuing less that Rs 10000/- available. Location will dispose the same after accumulation of sizable quantity to justify surveyor fees. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1221 | DELHI TERMINAL | Location of ensure disposal of the scrap within reasonable time to avoid accumulation. | SOD | Marketing | NZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000014036ACN-2026-06-4000141167 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141167 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141167 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141167 |  | AUD-2026-06-2000014036ACN-2026-06-4000141167 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141168 | Open |  |  | 1) Foldable stretcher inside emergency trolley was found in the compartment not labled for it. 2) Suction pressure gauge of MS Pump 2 in TLF pump house was found indicating negative pressure resulting in potential risk of inaccurate monitoring or suction line abnormality. 3) Water was found dipping from the HVLR-4 nozzle. 4) On operation of TK 6 sprinkler system, inadequate water discharge was observed from sprinkler nozzles 651, 652, 653, 615, 617, 618, 573, 616, 571, 572 resulting into reduced cooling efficiency. 5) Many electrical equipment were found having earthing connections from single point from the earthing strip. 6) In the scrap yard, surplus and scrap materials were found stored together without clear segregation. 7) Emergency escape route board near TK 1 & TK2 was found faded and unclear. 8) TK 01 roof plate was found with visible corrosion during inspection. | 6 |  | 1221 | DELHI TERMINAL | 1) Labeling (in hindi & english) of each chamber of emergency trolley should be done as per the material to be stored in it. 2) Pressure gauge to be checked and recalibrated /replaced. Strainer to be inspected for blockage causing negative pressure. 3) Isolation valve to be inspected for sealing integrity. 4) Sprinkler nozzles to be inspected for blockages to ensure adequate water supply and distribution pressure to sprinkler nozzles. 5) Double independent earthing to be ensured for all 3 phase electrical equipment. 6) Provide clear segregation between surplus and scrap materials in scrap yard with proper signage boards. 7) Replace faded board with new board to improve visibility and effectiveness during emergencies. 8) Affected areas to be recoated with corrosion resistant paint to prevent further deterioration. | SOD | Marketing | NZ | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-06-2000014036ACN-2026-06-4000141168 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141168 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141168 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141168 |  | AUD-2026-06-2000014036ACN-2026-06-4000141168 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141169 | Open |  |  | Two invertors out of 11 invertors are down since last two months . Location to expedite rectification and confirm Grass Cutting required in Solar Plant Area . | 6.1 |  | 1221 | DELHI TERMINAL | Solar invertor to be rectified. Grass Cutting to be expedited . | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141169 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141169 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141169 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141169 |  | AUD-2026-06-2000014036ACN-2026-06-4000141169 | 21 |  | 27 | 80 | 3 | 3 | 48
[5 empty] | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141170 | Open |  |  | 1) Identification labels are not provided for pressure transmitters installed on gantry headers. 2) Near Miss Reporting Point: NILnear miss reporting during 2026-27 till 26th May'26. 3) Alcohal checking register for TT Crew, Contract workmen. 4) Nil Accidentsduring 2026-27 as of 26th May'26. | 6.2 |  | 1221 | DELHI TERMINAL | 1) Install proper identification labels on all pressure transmitters. 2) Near miss reporting/ unsafe acts & conditions reporting to be encouraged amongst working personnel in field. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141170 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141170 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141170 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141170 |  | AUD-2026-06-2000014036ACN-2026-06-4000141170 | 21 |  | 27 | 80 | 3 | 3 | 48
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-26 | 2 Contract Engineers have reported at location. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125470 | Closed | KUMAR NITISH | 2026-06-26 | Yes discussed. During discussion with location, location has expressed the constraints faced wrt available manpower for ensuring vessel unloading and other major ongoing activities. Zone is currently arranging the manpower from other locations’ within zone as perrequirement. | 1.5 | HQO / Zonal support required identified | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125470 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125470 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125470 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125470 | AUD-2026-03-2000010720ACN-2026-03-4000125470 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 43
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-26 | Weekly progress report for all ongoing projects is shared with Zone. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125471 | Closed | KUMAR NITISH | 2026-06-26 | Planned major projects at location have been disucssed in details and advised location to complete the activities within timelines. | 1.8 | Improvement plans discussed | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-12-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-30 | AUD-2026-03-2000010720ACN-2026-03-4000125471 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125471 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125471 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125471 | AUD-2026-03-2000010720ACN-2026-03-4000125471 | 21 | 21 | 26 | 80 | 5 | 5 | 70 | 43
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-26 | HCD in TF02 repaired. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125475 | Closed | KUMAR NITISH | 2026-06-26 | HCD in tank farm no 2 (near TK8) was checked and found there was an error of mis-alignment due to ongoing project work in TK9. Location has been advised to explore the alternate positioning of HCD so as to cover the intended hazard. Functionality of HVLR No-05& HVLR No-08 was checked and found to be functional. RSPS of TK08 was checked and found functional as intended. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125475 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125475 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125475 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125475 | AUD-2026-03-2000010720ACN-2026-03-4000125475 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 43
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-27 | Weekly progress report for all ongoing projects is shared with Zone. Location is monitoring all projects closely so as to ensure all projects are completed within timelines. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125479 | Closed | KUMAR NITISH | 2026-06-27 | Yes reviewed. Project works were going on in TK1, TK4 & TK9 for tank repair works under supervision of officers from E&P Dept. 1. ITT LINE REVAMPING AT MUNDRA TERMINAL 2. SLOP TANKS IFR CONVERSION 3. MOV ACTUATOR FOR MUNDRA TERMINAL 4. AUDIT COMPLIANCE-MUNDRA TERMINAL 5. WATER TANK REVAMPING AT MUNDRA TERMINAL 6. Mundra_Revamp Augment. Sour HSD 7. Control Room Upgradation Mundra Terminal 8.TAS UPS AT MUNDRA TERMINAL 9. VHF SETS-MUNDRA TERMINAL 10. Mundra_Solar Invertor Revamping | 4.3 | Project progress reviewed | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125479 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125479 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125479 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125479 | AUD-2026-03-2000010720ACN-2026-03-4000125479 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 43
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-27 | Scrap Disposal complete. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125480 | Closed | KUMAR NITISH | 2026-06-27 | Yes done. 8 RFD proposals are approved and physically disposed and 1 No RFD is under physical disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125480 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125480 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125480 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125480 | AUD-2026-03-2000010720ACN-2026-03-4000125480 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 43
MANKAR PRAFULLA | 2026-06-27 | KUMAR NITISH | 2026-06-27 | Location is ensuring SKO stock loss to be within AOP targets. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125481 | Closed | KUMAR NITISH | 2026-06-27 | Location to ensure stock loss for SKO to be within AOP Targets | 6.1 | Stockloss | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000010720ACN-2026-03-4000125481 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125481 | 2026-09-18 | 31.7538 | 299 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125481 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125481 | AUD-2026-03-2000010720ACN-2026-03-4000125481 | 21 | 21 | 26 | 80 | 5 | 5 | 30 | 43
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141177 | Open |  |  | Senior Management Inspection March 2026 - 8/12 - Complied | 1.4 | Earlier action points status checked | 1845 | IRUMPANAM TERMINAL | Pending points to be complied in time bound manner. 1. Follow-up with KSEB for refund of 25lakhs under Security Deposit 2. Budgetfor compound wall repair 3. Bay no. 2 to be made functional at the earliest 4. Audit points to be complied in time bound manner Current Status: OISD - 39/43 SSA - 42/47 MDSA 2025 - 46/50 Comprehensive - 19/26 | SOD | Marketing | CZR | 2026-08-31 |  | 4 |  | S2 | F2 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141177 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141177 | 2026-09-02 16:30 | 47.0663 | 364 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141177 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013833ACN-2026-06-4000141177 |  | AUD-2026-06-2000013833ACN-2026-06-4000141177 | 21 |  | 27 | 80 | 1 | -4 | 52
|  |  |  | Scaffolding work commenced for tank repair. UT inspection lined up | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141178 | Open | Sreelal P P | 2026-07-30 | Repair of TK19 to be completed as per HQO recommendation | 1.5 | HQO / Zonal support required identified | 1845 | IRUMPANAM TERMINAL | Location to expedite Tank repair safely as only two tanks are available for operations | SOD | Marketing | CZR | 2026-08-31 |  | 8 |  | S4 | F2 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141178 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141178 | 2026-09-02 16:30 | 47.0663 | 364 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141178 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141178 |  | AUD-2026-06-2000013833ACN-2026-06-4000141178 | 21 |  | 27 | 80 | 1 | -4 | 52
|  |  |  | Action taken 1. Gaps observed in the Fire Engine base area has been rectified. 2. Fire engines diesel return line is in rusted condition; necessary restoration and preventive maintenance to be carried out to maintain them in good operational condition. - work assigned to Mechanical contractor. 3. Extension of the water line for gland packing arrangement to be further extended outside the Fire Pump House - work under progress 4. Panels that are not in use to be identified and removed from the Fire Pump House - work under progress 5. Proper maintenance of the mechanical seal of the Jockey Fire Water Pump is carried out. | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141179 | Open | Sreelal P P | 2026-07-30 | Clear guidelines given on maintenance of fire engines and associated facilities. 1. Gaps observed in the Fire Engine base area to be rectified. 2. Fire engines diesel return line is in rusted condition; necessary restoration and preventive maintenance to be carried out to maintain them in good operational condition. 3. Extension of the water line for gland packing arrangement to be furtherextended outside the Fire Pump House. 4. Panels that are not in use to be identified and removed from the Fire Pump House. 5. Proper maintenance of the mechanical seal of the Jockey Fire Water Pump to be carried out | 1.6 | Expectations clearly communicated to officers | 1845 | IRUMPANAM TERMINAL | Clear guidelines communicated to concerned officers | SOD | Marketing | CZR | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141179 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141179 | 2026-09-02 16:30 | 47.0663 | 333 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141179 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141179 |  | AUD-2026-06-2000013833ACN-2026-06-4000141179 | 21 |  | 27 | 80 | 1 | -4 | 48
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141180 | Open |  |  | Circulars discussed | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1845 | IRUMPANAM TERMINAL | Sustence of dip elimination, HLSA compliance, close monitoring of safety critical equipments, e Dairy observations and timely resolution etc. were discussed | SOD | Marketing | CZR | 2026-08-31 |  | 6 |  | S2 | F3 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141180 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141180 | 2026-09-02 16:30 | 47.0663 | 364 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141180 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141180 |  | AUD-2026-06-2000013833ACN-2026-06-4000141180 | 21 |  | 27 | 80 | 1 | -4 | 52
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141181 | Open |  |  | 1.Faded signboards, nameplates, and safety stickers to be replaced. Radium reflective stickering work to be undertaken wherever required. 2. Process drain and storm water drain lines to be properly identified and nomenclature boards provided for all the tanks and everywhere. | 1.8 | Improvement plans discussed | 1845 | IRUMPANAM TERMINAL | Clear guidelines communicated to concerned officers | SOD | Marketing | CZR | 2026-08-31 |  | 6 |  | S2 | F3 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141181 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141181 | 2026-09-02 16:30 | 47.0663 | 364 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141181 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141181 |  | AUD-2026-06-2000013833ACN-2026-06-4000141181 | 21 |  | 27 | 80 | 1 | -4 | 52
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141184 | Open |  |  | Unused assets and surplus materials updated in surplus portal. | 3.9 | Abnormal variations / unused assets reviewed | 1845 | IRUMPANAM TERMINAL | Pending Top loading vapor recovery arms to be quantified, removed, and declared as surplus. | SOD | Marketing | CZR | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141184 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141184 | 2026-09-02 16:30 | 47.0663 | 333 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141184 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013833ACN-2026-06-4000141184 |  | AUD-2026-06-2000013833ACN-2026-06-4000141184 | 21 |  | 27 | 80 | 1 | -4 | 48
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141185 | Open |  |  | K factor changed in bay No.2 due to power card issue. Bay is still kept offline due to earthing relay issue. Highlighted in last audit | 3.13 | K-factor changes reviewed (if any) | 1845 | IRUMPANAM TERMINAL | Bay no. 2 is to be made online at the earliest possible time after stamping by legal meteorology | SOD | Marketing | CZR | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141185 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141185 | 2026-09-02 16:30 | 47.0663 | 333 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141185 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141185 |  | AUD-2026-06-2000013833ACN-2026-06-4000141185 | 21 |  | 27 | 80 | 1 | -4 | 48
[5 empty] | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141190 | Open |  |  | Reviewed maintenance of Ethanol tank TK19. | 4.2 | All activies are being performed with Permits and with all PPE in place. | 1845 | IRUMPANAM TERMINAL | Maintenance job is under progress for TK19. Advised to expedite Tk19 repair works as only two tanks are available for regular PLT and loading operations. | SOD | Marketing | CZR | 2026-07-31 |  | 6 |  | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141190 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141190 | 2026-09-02 16:30 | 47.0663 | 333 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141190 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013833ACN-2026-06-4000141190 |  | AUD-2026-06-2000013833ACN-2026-06-4000141190 | 21 |  | 27 | 80 | 1 | -4 | 48
SUJEET KUMAR | 2026-06-27 | SAXENA UMESH CHANDRA | 2026-06-22 | Dips of TK3 are now getting posted automatically and TK3 is getting auto-reconciled too. System generated auto-reco email of 21.06.2026 is enclosed confirming auto-reco of TK3. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135381 | Closed | SAXENA UMESH CHANDRA | 2026-06-22 | Auto dips are posted for all tanks except TK 12, 22 and 03. TK 03 was under exception as no product was present earlier, exception has now been removed and dip for TK03 to be posted. TK 12 and 22 are not in use and are being disposed off. | 3.8 | Auto vs Manual reconciliation checked | 1457 | INDORE DEPOT | Exception of TK 03 has been removed and location to ensure posting dip for TK03. | SOD | Marketing | CEN | 2026-06-09 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-09 | AUD-2026-06-2000012547ACN-2026-06-4000135381 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135381 | 2026-09-09 19:00 | 39.9622 | 299 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135381 | 532 | 8294 | 21 | 8294 | 132 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135381 | AUD-2026-06-2000012547ACN-2026-06-4000135381 | 21 | 21 | 27 | 80 | 0 | -3 | 41 | 43
SUJEET KUMAR | 2026-06-27 | SAXENA UMESH CHANDRA | 2026-06-27 | MOC for PCC beneath pipeline has been closed on 27.06.2026 (MOC copy enclosed) | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135384 | Closed | SAXENA UMESH CHANDRA | 2026-06-27 | 1 MOC is open - (PCC beneath Pipeline to be closed) | 3.17 | MOC status reviewed | 1457 | INDORE DEPOT | MOC for PCC to be closed as work has been completed. | SOD | Marketing | CEN | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135384 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135384 | 2026-09-09 19:00 | 39.9622 | 299 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135384 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135384 | AUD-2026-06-2000012547ACN-2026-06-4000135384 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 43
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141718 | Open |  |  | Yes, to be closed. | 1.4 | Earlier action points status checked | 1435 | GWALIOR DEPOT | Previous visit open points to be closed on priority. | SOD | Marketing | CEN | 2026-12-30 |  | 8 |  | S2 | F4 | 2026-12-30 | AUD-2026-06-2000015012ACN-2026-06-4000141718 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141718 | 2026-08-22 19:00 | 57.9622 | 485 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141718 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000015012ACN-2026-06-4000141718 |  | AUD-2026-06-2000015012ACN-2026-06-4000141718 | 21 |  | 27 | 80 | 2 | 2 | 70
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141724 | Open |  |  | 2 MOC are open - (TFMS and Dip Elimination) | 3.17 | MOC status reviewed | 1435 | GWALIOR DEPOT | MOC's to be closed immediately after TAS Revamp | SOD | Marketing | CEN | 2026-12-30 |  | 8 |  | S2 | F4 | 2026-12-30 | AUD-2026-06-2000015012ACN-2026-06-4000141724 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141724 | 2026-08-22 19:00 | 57.9622 | 485 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141724 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000015012ACN-2026-06-4000141724 |  | AUD-2026-06-2000015012ACN-2026-06-4000141724 | 21 |  | 27 | 80 | 2 | 2 | 70
[5 empty] | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141867 | Open |  |  | 1. Land registration to be completed and AR closed. Approval pending with KIADB 2. Dip Elimination is pending. File note is initiated, approval to be accorded | 1.3 | Pending issues reviewed | 1775 | BENGALURU TERMINAL | 1. Land registration & AR closure to be expedited on top priority. 2. To follow-up with HQO for approval of dip elimination filenote | SOD | Marketing | SWZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141867 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141867 | 2026-09-24 17:00 | 25.0455 | 333 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141867 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014499ACN-2026-06-4000141867 |  | AUD-2026-06-2000014499ACN-2026-06-4000141867 | 21 |  | 27 | 80 | 0 | 0 | 48
[5 empty] | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141869 | Open |  |  | Budget requested for railway siding revamping work has been allocated by HQO. | 1.5 | HQO / Zonal support required identified | 1775 | BENGALURU TERMINAL | Jobs to be expedited and AR shall be closed within timelines. | SOD | Marketing | SWZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-06-2000014499ACN-2026-06-4000141869 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141869 | 2026-09-24 17:00 | 25.0455 | 425 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141869 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014499ACN-2026-06-4000141869 |  | AUD-2026-06-2000014499ACN-2026-06-4000141869 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141882 | Open |  |  | OISD audit 42/42 are complied, 29/31 of SSA are complied,MDSA 2025-26: 26/32 points are complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1775 | BENGALURU TERMINAL | Balance points of SSA to be complied by 30.06.2026 & MDSA by 30.09.2026 | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141882 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141882 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141882 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014499ACN-2026-06-4000141882 |  | AUD-2026-06-2000014499ACN-2026-06-4000141882 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141884 | Open |  |  | Close monitoring and compliance is required. 2 nos Schedules of RFDs under re-auctioning because of failure in earlier auctions | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1775 | BENGALURU TERMINAL | All scrap identified so far to be disposed off by H1 and balacne scrap to be disposed off by Dec'26 | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141884 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141884 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141884 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014499ACN-2026-06-4000141884 |  | AUD-2026-06-2000014499ACN-2026-06-4000141884 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141888 | Open |  |  | Rack Monitoring Units were observed not integrated with TAS | 6.3 | Additional Observations | 1775 | BENGALURU TERMINAL | To be integrated with TAS | SOD | Marketing | SWZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141888 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141888 | 2026-09-24 17:00 | 25.0455 | 333 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141888 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014499ACN-2026-06-4000141888 |  | AUD-2026-06-2000014499ACN-2026-06-4000141888 | 21 |  | 27 | 80 | 0 | 0 | 48
AILAVARAPU VENKATA KRISHNA MURTY | 2026-07-01 | DIWAKAR KAMLESH KUMAR | 2026-06-15 | Tanks are reconciled with manual dips before PLT/before rake loading to avoid AIM holds. TK101 is under outage reconciled with manual dip on daily basis. TK203 & 212 reconciled with manual dips as tanks custody transfer is pending to VR. Month end reco is being done with manual dips as per HQO circular, 12A &12B tanks are not having TAS equipment, Rake invoicing is time taking process as SAPinvoicing to the direct sale customers are possible only after Railway RR/Invoice generation, more than 1 day time taken by railwayfor invoicing, there is density issue with Bitumen tanks, etc manual dips are put in system). A total of 5 tanks out of 21 tanks per day are reconcilled on manual dips amounting to24.40% reco on manual dips. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125091 | Closed | DIWAKAR KAMLESH KUMAR | 2026-06-15 | TAS- TFMS reco is 76% against target of 95% | 3.10 | TFMS/SAP reconciliation checked | 3708 | VISAKH NBOT | TAS-TFMS reco to be improved and to meet target | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125091 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125091 | 2026-09-18 17:30 | 31.0247 | 303 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125091 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125091 | AUD-2026-03-2000011315ACN-2026-03-4000125091 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 44
[5 empty] | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142950 | Open |  |  | 1) Long pending matter of GST Consignment note to be issued with Invoices was discussed. Matter with SZ-Retail Commercial, who in turn are discussing the same with HQO Tax group. 2) Conversion of Bonded 2000 KL ATF tank into Duty paid was discussed. As informed,location has taken up the case with Excise dept and submitted letter last month. | 1.3 | Pending issues reviewed | 1856 | COIMBATORE DEPOT | 1) Continued follow-up by location with Retail-Commercial, SZ. 2) Location to maintain constant follow-up with Excise Authorities. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015339ACN-2026-07-4000142950 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142950 | 2026-08-28 17:00 | 52.0455 | 394 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142950 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015339ACN-2026-07-4000142950 |  | AUD-2026-07-2000015339ACN-2026-07-4000142950 | 21 |  | 27 | 80 | 0 | 1 | 57
[5 empty] | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142958 | Open |  |  | Location has disposed Rs 14.5 Lakhs value scrap in FY 25-26. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1856 | COIMBATORE DEPOT | Location to arrange for seggreation of material in Warehouse and scrap materials if any to be identified and disposed off. | SOD | Marketing | SZ | 2026-10-31 |  | 2 |  | S1 | F2 | 2026-10-31 | AUD-2026-07-2000015339ACN-2026-07-4000142958 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142958 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142958 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015339ACN-2026-07-4000142958 |  | AUD-2026-07-2000015339ACN-2026-07-4000142958 | 21 |  | 27 | 80 | 0 | 1 | 61
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142962 | Open |  |  | a. Fire engine replacement project tender failed due to high quotes by vendors. Retendering to be done. b. Additional 15 TT for ATF to be inducted in view of enhanced ATF demand and Jewar Airport requirement. c. ATF issue: Transporter M/s. Rajesh Kumar not being allowed to decant at T3. Causing disparity among transporter’s RTKM. Issued raised to Aviation HQO for taking up with IOSL. d.Matter of ATF DP/Bonded segregation in TAS/SAP, TT waiting parameter has been already taken up with HQO thru zone. e. Tank repairs, Tank painting, ATF/MTO Pipeline repair and Boundary wall repairs to be carried out expeditiously. f. Pipeline thickness survey/ hydrotesting of pipelines to be carried out to ensure integrity of the pipeline system in the view of frequent leakages in product lines. g. Grass cutting in Process area/Pipeline area on priority and other areas subsequently to be expedited. h. Budget to be soughtfor PCC below Pipelines to identify leakages and take expedious action for repairs. | 1.3 | Pending issues reviewed | 1216 | BAHADURGARH TERMINAL | a to f. All pending issues to be complied in a time bound manner. | SOD | Marketing | NZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013589ACN-2026-07-4000142962 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142962 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142962 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142962 |  | AUD-2026-06-2000013589ACN-2026-07-4000142962 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142963 | Open |  |  | Following jobs to be expedited : 1. Leakages in TT gantry to be avoided. If required spares like couplers etc to be replaced. 2.Two Valves in TT Gantry strainer drain point to be provided. 3. Leakage from Mechnical seal of MS Pump no 5 in Product pumphouse to be arrested. There were total of 51 recommendations during the previous Sr. Management Audit done during Mar'26 which remain to be closed in SAP. | 1.4 | Earlier action points status checked | 1216 | BAHADURGARH TERMINAL | Necessary corrective action to be taken. Location to close the previous recommendations physically as well as update the status in SAP. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013589ACN-2026-07-4000142963 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142963 | 2026-09-05 | 44.7538 | 486 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142963 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142963 |  | AUD-2026-06-2000013589ACN-2026-07-4000142963 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142965 | Open |  |  | Double contingency fire mock drill was conducted on 21/05/2026 at 17:11 hours at Bahadurgarh Terminal, considering the scenario of a leakage & fire from bottom loading HSD coupler while loading of TT at Bay#13 of Gantry and a leakage with fire from flange of MTO loading pump no. 3 at TT Gantry Pump house. Following observations were made for improvement. 1. ESDs were operated at both the emergencies scenarios, however, siren did not operate on both the ocassions. 2. At the product pump house, sprinklers were operated in the entire pump house instead of the adjoining section of the facility for cooling purposes as water sprinkling in the affected area would result in spreading of the leaked product and spreading of the fire. 3. Mega phone taken at site was not operational. 4. There is only one indicator/ needle on the fire clock which doesn't indicate the secondary scenario of the double contingency. 5. CBAC turnstile did not drop after operation of ESD at license area entry near the Admin building and at the Tank Farm entry gate. 6. Leakage observed from a fire hose lined up on the eastern side of TLF gantry. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1216 | BAHADURGARH TERMINAL | 1. Refer recommendations made under Audit No. AUD-2026-03-2000011128 for ESD testing. 2. Training to be given to all concerned about tackling of various emergency scenarios. 3. Mega Phones should be kept in prime working condition and should be used during the drills. 4. Fire clock to be suitably modified to represent double contingency scenarios. 5. Corrective action to be taken. 6. Periodic testing of fire hoses as per norm to be carried out to ensure no failure of hoses during fire drills/ actual scenarios. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142965 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142965 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142965 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142965 |  | AUD-2026-06-2000013589ACN-2026-07-4000142965 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142967 | Open |  |  | Location is supposed to carry out one night inspection every month. Last inspection record available at the location is for 21st March'26 that too in soft form with no review by LIC. While entry is available in gate register of the officer visiting the location on 21st Mar'26, the remarks column is blank against the entry. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1216 | BAHADURGARH TERMINAL | Location to perform Surprise Night Inspections and maintain record of Inspection along with entries in Gate register about visits done. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142967 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142967 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142967 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142967 |  | AUD-2026-06-2000013589ACN-2026-07-4000142967 | 21 |  | 27 | 80 | 9 | 9 | 48
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142968 | Open |  |  | Some discrepancies were observed during cursory review of the ERDMP document. 1. All products being handled are not part of the abbreviations list- ATF & MTO are missing from the list. (page no. 20) 2. Receiving line from jetty full bore failure for (i) MS (ii) MTO & (iii) HSD (iv) SKO is considered as a failure case for ERDMP (Page No. 30). 3. Naptha Tank on Fire (TK-8, TK-9, TK-10 & TK-26) is considered as failure scenario (page no. 44) 4. Naptha tank has a mention on page no. 51 & 53 whereas location is currently Naptha free and no handling of Naptha is planned at the location. 5. Off-Shift Organogram during off-office hours (including holidays) which is covered on page no. 100 has mention of Security In-Charge as the Chief Incident Controller whereas in the organogram displayed on board in the premises, Shift In-charge is shown as the Chief Incident Controller. As such, the location has a manned control room on all the 365 days of the year. | 2.5 | Emergency response preparedness reviewed | 1216 | BAHADURGARH TERMINAL | ERDMP to be thoroughly reveiwed and modified as per the actual site conditions and personnel available. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013589ACN-2026-07-4000142968 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142968 | 2026-09-05 | 44.7538 | 486 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142968 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142968 |  | AUD-2026-06-2000013589ACN-2026-07-4000142968 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142969 | Open |  |  | There are total 122 + 13 new CCTV cameras in the installation. All the cameras are working. Out of the 122 old cameras, 4 cameras which were replaced in April'26 are offline and not appearing in SCORE software screen. Similarly, the 13 new cameras are not added in the SCORE system due to no port available in the exisitng NAS (100TB) available. A new NAS device with additional ports will be supplied by the vendor M/s. Hexa Tech who is carrying out the supply, installation & hooking up of the new 13 cameras installed with the exisitng SCORE system. | 2.6 | CCTV functioning checked | 1216 | BAHADURGARH TERMINAL | All cameras to be hooked to the SCORE system | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142969 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142969 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142969 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142969 |  | AUD-2026-06-2000013589ACN-2026-07-4000142969 | 21 |  | 27 | 80 | 9 | 9 | 57
|  |  |  | HVLRs were repaired and check for proper functionality, AMC PO placement is under progress | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142971 | Open | ANKIT KUMAR | 2026-10-02 | HVLR - Total 16 Nos of HVLR is available at the Location. HVLR No. 14 – Vegetation was found coming out of its elevated platform.SOP for the HVLR was not in sync with the actual buttons provided on the HVLR panel. HVLR No. 11 was operated and found to be working OK. HVLR No. 10 had no power in its control panel at site. | 2.11.01 | HVLR/RSFPS/HCD/ESD functionality checked | 1216 | BAHADURGARH TERMINAL | Proper preventive maintenance of all HVLR's shall be ensured to maintain their operational readiness at all times. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142971 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142971 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142971 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142971 |  | AUD-2026-06-2000013589ACN-2026-07-4000142971 | 21 |  | 27 | 80 | 9 | 9 | 48
|  |  |  | ESD made functional and turnstile deactivation during ESD also checked | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142972 | Open | ANKIT KUMAR | 2026-10-02 | HVLR No. 14: (i) Vegetation found grown above the operating platform. (ii) SOP is not in sync with the actual buttons on its operating panel (iii) The HVLR operate remotely from its panel- it could finally be operated thru manual intervention at the HVLR. Further, the movements were happening only in right and down directions thru the panel whereas the movements in up & left direction could not be performed thru remote operations. The direction of the HVLR was found not kept towards the Ethanol tank for which it is provided. HVLR No. 11: Operated as intended both in jet & fog modes with movements happening in all directions remotely. HVLR No. 10: Itwas found that there was no Power in this HVLR's operating panel. RSFPS: Physical operation of RSFPS for tank no. 8 was checked and found that on activating the facility thru the panel avaiable besides its dyke, local hooter got actuated, pneumatically operated rotary actuator switches on the RSFPS facilities got opened and alarm was sounded in the TAS room. Nitrogen pressure in the three foam tanks was found to be 15.5 kg/sqcm as per the requirement and all the foam tanks of capacity 200L were found topped up to theirlimits as per the requirement. HCD - Total 22 Nos of HCD available at the location. Out of which 12 nos are Open path and 10 Nos are Point type HCD. Record of HCD testing was verified and found to be maintained. ESDs of TLF Gantry and Product Pump House for TLF Gantry were actuated during the fire drill. However, both of them did not function and no siren with wailing was sounded during the drill. Turnstile at the entrance of Licensed area from Administrative Building did not go down after ESD activation during thefire drill. | 2.11.03 | HVLR/RSFPS/HCD/ESD functionality checked | 1216 | BAHADURGARH TERMINAL | Corrective action to be taken for faulty HVLRs, ESDs & turnstiles. | SOD | Marketing | NZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-06-2000013589ACN-2026-07-4000142972 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142972 | 2026-09-05 | 44.7538 | 333 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142972 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142972 |  | AUD-2026-06-2000013589ACN-2026-07-4000142972 | 21 |  | 27 | 80 | 9 | 9 | 48
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142977 | Open |  |  | Check for 5% EM locks on daily basis and all locks on monthly basis is being carried out by the location and record is being maintained. However, location to get additional EM locks to avoid TT detention inside the premises due to EM lock issues. | 3.5 | EM Lock SOP compliance verified | 1216 | BAHADURGARH TERMINAL | Location to identify the nos. of spare EM locks required to streamline daily operations and initiate action to get them. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142977 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142977 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142977 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142977 |  | AUD-2026-06-2000013589ACN-2026-07-4000142977 | 21 |  | 27 | 80 | 9 | 9 | 48
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142983 | Open |  |  | Earth Pits - Total 456 Nos of Earth pits are there at the location. Earth Pit No 59 & 60 were Checked and Found Individual and Grid Reading as mentioned here below: Individual Reading (Displayed/ Observed) of EP 59 - 1.97 Ω / 2.08 Ω Grid Reading (Displayed/ Observed) of EP-59 - 0.73 Ω / 0.08 Ω Individual Reading (Displayed/ Observed) of EP 60 - 1.86 Ω / 1.90 Ω Grid Reading (Displayed/ Observed) of EP-59 - 0.53 Ω / 0.38 Ω | 3.16.01 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | All earth-pits having individual resistance more than 2 Ω to be maintained as per standard practice to bring down the EP resistancebelow 2 Ω as per requirement. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142983 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142983 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142983 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142983 |  | AUD-2026-06-2000013589ACN-2026-07-4000142983 | 21 |  | 27 | 80 | 9 | 9 | 48
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142984 | Open |  |  | Boundary Wall - The boundary wall requires civil repair and repainting. At several locations, the plaster has deteriorated and is found to be dislodged. The concertina coil placed along the periphery and is intact. However, provision of broken glass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. At some places, adjoining properties structure have been found erected just near the location's boundary wall which is undesirable. | 3.16.02 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | Civil work and painting of boundary wall to be ensured. Wherever, adjoining properties have got erected too close to the location'sboundary wall, suitable protection with double concertina coil should be provided. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013589ACN-2026-07-4000142984 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142984 | 2026-09-05 | 44.7538 | 486 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142984 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142984 |  | AUD-2026-06-2000013589ACN-2026-07-4000142984 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142986 | Open |  |  | MDSA - Last MDSA/Comprehensive audit was conducted on 02 -05 Dec 2024 - Communication of MOV's with MCS is not established in field due to MCS obsolution | 3.18.02 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | Communication between the MOVs and the MCS should be re-established by upgrading or replacing the obsolete MCS system to ensure proper monitoring and control from the control room. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142986 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142986 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142986 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142986 |  | AUD-2026-06-2000013589ACN-2026-07-4000142986 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142987 | Open |  |  | MDSA - Last MDSA/Comprehensive audit was conducted on on 24- 28 Nov 2025 - Tot 43 observation were there, out of which 21 points are remaining to be complied | 3.18.03 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | The remaining observations should be addressed and complied with at the earliest to ensure full closure. | SOD | Marketing | NZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-06-2000013589ACN-2026-07-4000142987 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142987 | 2026-09-05 | 44.7538 | 425 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142987 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142987 |  | AUD-2026-06-2000013589ACN-2026-07-4000142987 | 21 |  | 27 | 80 | 9 | 9 | 61
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142991 | Open |  |  | Heavy rusting was observed on the EFR surface of TK01 (HSD tank). Heavy rusting was found on the top wind girder walkway of tank no. TK01. Some gratings of stairs were also observed to be highly rusted. Oil spillage was observed on the surface of EFR of TK01. | 4.1.03 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Necessary corrective action to be taken. Inspection of all other product tanks on similar lines to be carried out by the location and prepare an elaborate plan for rectification including re-painting and patch works as per requirement. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013589ACN-2026-07-4000142991 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142991 | 2026-09-05 | 44.7538 | 486 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142991 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142991 |  | AUD-2026-06-2000013589ACN-2026-07-4000142991 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142992 | Open |  |  | The 12 ATF line laid in the Tank Farm area is observed to have corrosion at the 6 o’clock position, with clamping done at several locations to prevent leakage. | 4.1.04 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The pipeline should be thoroughly inspected and the affected section repaired or replaced as required. | SOD | Marketing | NZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013589ACN-2026-07-4000142992 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142992 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142992 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142992 |  | AUD-2026-06-2000013589ACN-2026-07-4000142992 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142993 | Open |  |  | Pitting corrosion has been observed at several locations on the roof of A/G Tank No. 10. Five pinholes were also identified and temporarily repaired using cold welding. | 4.1.05 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | A detailed inspection should be carried out and permanent repairs to the tank roof should be undertaken. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142993 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142993 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142993 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142993 |  | AUD-2026-06-2000013589ACN-2026-07-4000142993 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142994 | Open |  |  | Pitting corrosion was observed on the HSD line at the Tank Wagon Gantry. | 4.1.06 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The line should be inspected and necessary corrective actions, including repair or replacement of the affected section, should be carried out. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142994 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142994 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142994 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142994 |  | AUD-2026-06-2000013589ACN-2026-07-4000142994 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142995 | Open |  |  | 1. Single isolation is available in Strainer drain line in TT Gantry. 2. Location reported that there are frequent issues of leakages from TT loading couplers. | 4.1.07 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | 1. Double isolation should be provided in the strainer drain line at the TT Gantry to enhance operational safety and maintenance flexibility. 2. Location to identify nos. of damaged couplers in the TT loading arms and develop comprehensive proposal for their replacement. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142995 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142995 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142995 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142995 |  | AUD-2026-06-2000013589ACN-2026-07-4000142995 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142996 | Open |  |  | All generated scrap to be disposed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1216 | BAHADURGARH TERMINAL | Location to work towards declaring it scrap free by 31.12.2026. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-06-2000013589ACN-2026-07-4000142996 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142996 | 2026-09-05 | 44.7538 | 486 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142996 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142996 |  | AUD-2026-06-2000013589ACN-2026-07-4000142996 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | POST-VISIT REPORTING | ACN-2026-07-4000142997 | Open |  |  | Interaction was made with the QC officer along with LIC and Ch. Mgr. Opns. advising them to carry out self QC audit of the locationjointly to ensure QC compliance & improving of the QC index score. | 5 |  | 1216 | BAHADURGARH TERMINAL | Location to carry out self QC Audit immediately. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142997 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142997 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142997 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142997 |  | AUD-2026-06-2000013589ACN-2026-07-4000142997 | 21 |  | 27 | 80 | 9 | 9 | 48
[5 empty] | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142608 | Open |  |  | 1) Shortfall in number of TTs currently engaged with depot due termination of multiple agreements. 2) Ratio of top loading TTs to bottom loading TTs is still high and conversion rate is not as expected. | 1.3 | Pending issues reviewed | 1183 | NALGARH DEPOT | 1).Location to co ordinate with HQO and initiate process for suplementary transportation tender to meet shortfall due termination of multiple agreements. 2) Location to complete conversion of top loading TTs to bottom loading TTs in a phased manner keeping dailysales in consideration without further delay. | SOD | Marketing | NFZ | 2026-07-30 |  | 4 |  | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142608 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142608 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142608 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015564ACN-2026-07-4000142608 |  | AUD-2026-07-2000015564ACN-2026-07-4000142608 | 21 |  | 27 | 80 | 1 | 1 | 48
[5 empty] | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142609 | Open |  |  | 1) All cameras to be made functional 2) Scrap lying in depot to be disposed on priority | 1.4 | Earlier action points status checked | 1183 | NALGARH DEPOT | Location to take action on pending points 4.5 Scrap disposal progress reviewed / scrap-free environment checked 2.6 CCTV functioning checked | SOD | Marketing | NFZ | 2026-07-30 |  | 4 |  | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142609 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142609 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142609 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015564ACN-2026-07-4000142609 |  | AUD-2026-07-2000015564ACN-2026-07-4000142609 | 21 |  | 27 | 80 | 1 | 1 | 48
[5 empty] | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142613 | Open |  |  | SOP boards and euipment details displayed are not in good condition | 3.5 | EM Lock SOP compliance verified | 1183 | NALGARH DEPOT | Location to carry out replacement of all worn out boards | SOD | Marketing | NFZ | 2026-08-15 |  | 1 |  | S1 | F1 | 2026-08-15 | AUD-2026-07-2000015564ACN-2026-07-4000142613 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142613 | 2026-08-27 | 53.7538 | 348 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142613 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015564ACN-2026-07-4000142613 |  | AUD-2026-07-2000015564ACN-2026-07-4000142613 | 21 |  | 27 | 80 | 1 | 1 | 50
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Siren testing is carried on every wednesday by security guards. We have implemented improvement measure by sending 1/2 security guards outside premises 3 KM away to witness the sound of the siren. Started from 10.06.2026 | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-05-4000131506 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Siren at the location was tested every week, however there was no person being sent outside to confirm the siren being audible at 3kms range. | 6.1 | Quarterly Inspection | 1723 | PATNA DEPOT | One person needs to be sent to 3 km range to confirm siren audibility | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131506 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131506 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131506 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131506 | AUD-2026-05-2000012310ACN-2026-05-4000131506 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The Name of all the guards have been updated in the duty register in the month start. Hence point complies. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-05-4000131507 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Armed guard name was not updated in the register. | 6.2 | Quarterly Inspection | 1723 | PATNA DEPOT | Name to be updated in the register | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131507 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131507 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131507 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131507 | AUD-2026-05-2000012310ACN-2026-05-4000131507 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Gate pass reconciled on daily basis by security.Verification of record by HSE officer on the next day. Verification of the record by LIC on weekly basis. Hence point complies. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-05-4000131508 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Material gate pass was not upto date. Last entry was for 19-5-26. Officer sign was missing. | 6.3 | Quarterly Inspection | 1723 | PATNA DEPOT | HPCL Location Officer to sign the register | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131508 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131508 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131508 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131508 | AUD-2026-05-2000012310ACN-2026-05-4000131508 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | There are currently 3 contracts active at Patna New IRD. Contract workman entry/exit register is reconciled on daily basis by security.Verification of record by HSE officer on the next day. Verification of the record by LIC on weekly basis. Hence point complies. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-05-4000131509 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In / Out entry registry for contract workman not update since 16-5-26 | 6.4 | Quarterly Inspection | 1723 | PATNA DEPOT | register to be updated daily or when ever there is any entry | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131509 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131509 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131509 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131509 | AUD-2026-05-2000012310ACN-2026-05-4000131509 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The emergecny contact details have been updated taking care of transfers of officers in DPC. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-05-4000131510 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Updating of phones nos. such as RM, M&I, Location In charge needs to done at the entry gate. | 6.5 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to upodate the details | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131510 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131510 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131510 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131510 | AUD-2026-05-2000012310ACN-2026-05-4000131510 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Silica gel have been replaced. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-05-4000131653 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Random checking of PM schedule compliance was done. As per PM schedule, checking of silica gel of UG Ethanol tanks have been done, but in field, old Silicsa gel which has lost its utility, found | 6.5 | Quarterly Inspection | 1723 | PATNA DEPOT | PM to be carried in true spirit | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131653 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131653 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131653 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131653 | AUD-2026-05-2000012310ACN-2026-05-4000131653 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | There are currently 3 contracts active at Patna New IRD. Contract workman entry/exit register is reconciled on daily basis by security.Verification of record by HSE officer on the next day. Verification of the record by LIC on weekly basis. Hence point complies. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-05-4000131511 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In / Out entry registry for contract workman not update since 16-5-26 | 6.6 | Quarterly Inspection | 1723 | PATNA DEPOT | Registers to be updated on daily basis | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131511 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131511 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131511 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131511 | AUD-2026-05-2000012310ACN-2026-05-4000131511 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The concerned security guards have been trained to not use correction pen. If required, they have to maka a single line cut. The notice has also been issued by HSE officer dated 28.05.2026. The register is updated on daily basis. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-05-4000131512 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In Material gate pass had correction pen marks. Register was updated till 18-5-26 only. | 6.7 | Quarterly Inspection | 1723 | PATNA DEPOT | Correctionpen needs to be discontinued and any wrong entry to be strike off. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131512 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131512 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131512 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131512 | AUD-2026-05-2000012310ACN-2026-05-4000131512 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Identification boards for all earth pits near the gate entry office have been installed. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-05-4000131513 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Earth pit signages missing at depot entry near admin building.Even the electrodes and connections found improper | 6.8 | Quarterly Inspection | 1723 | PATNA DEPOT | Pit nos to be mentioned. Pits to be maintained as per IS3043 | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131513 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131513 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131513 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131513 | AUD-2026-05-2000012310ACN-2026-05-4000131513 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The records have been signed by HSE officer. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-05-4000131514 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Tokens with RFID tag to be usedb security guards during Night patrol started form 2-5-26. Earlier depot had a manual system where the guards were supposed to enter the time of patrolling, confirmed by the safety officer in the next day via CCTV footage, but thereis no signature of the HPCL officer in the slips | 6.9 | Quarterly Inspection | 1723 | PATNA DEPOT | Safety officer to sign the slip for confirmation. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131514 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131514 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131514 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131514 | AUD-2026-05-2000012310ACN-2026-05-4000131514 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The RFID tags are placed in camera View. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-05-4000131515 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Reviewed 6 random CCTV footages (Night) for Railway Siding, Lube Godowns, ETP, Rail Gate, Ethanol gantry, MS/HSD Gantry. Guards were seen only at Rail Gate and Ethanol gantry during the time captured as per the Patrol report. | 6.10 | Quarterly Inspection | 1723 | PATNA DEPOT | Footage missing. Safety officer to ensure the readrer tags are placed in camera view OR security to visit the spot and tag the reader while on patrol | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131515 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131515 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131515 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131515 | AUD-2026-05-2000012310ACN-2026-05-4000131515 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Ethanol TT as well as materials are being received as well as released by gate pass system. The gate passes are reconciled by security on daily basis and verified by HSE officer on the next day. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-05-4000131516 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Ethanol TTs are not being released as per gate passes. Neither are material being received as per gate passes. Though material have been received after 18/05/26, as of 21/05/26, no records are there at gate. Officers not verifying records periodically | 6.11 | Quarterly Inspection | 1723 | PATNA DEPOT | HPCL officers to verify the records periodically and LIC too should be informed and registers to be shown | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131516 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131516 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131516 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131516 | AUD-2026-05-2000012310ACN-2026-05-4000131516 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | On few instances, the contract wokers had forgot to sign. Now the security is cross checking as well as reconciling the register ondaily basis. The same register is verified by HSE officer on next day. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-05-4000131517 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Contract workmen entry and exit also not getting recorded. There are instances of contract workmen not gone out as per gate record, but the contract workmen have actually gone out, as evident from gate entry register of next date. Security supervisor is not checking the records daily, rather doing on a later date. | 6.12 | Quarterly Inspection | 1723 | PATNA DEPOT | Recording of contract workmen to be madatorialy done in register. The same to be checked by security supervisior and safety officer | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131517 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131517 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131517 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131517 | AUD-2026-05-2000012310ACN-2026-05-4000131517 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The system of CCTV monitoring with record for the same has been started by security guards from 28.05.2026. Currently 8 no. of security guards have been trained to monitor CCTV. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-05-4000131518 | Closed | JHA RAJAN KUMAR | 2026-06-30 | There is no record of monitoring of CCTV cameras by Security. | 6.13 | Quarterly Inspection | 1723 | PATNA DEPOT | Proper record to be maintained at location for CCTV footage. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131518 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131518 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131518 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131518 | AUD-2026-05-2000012310ACN-2026-05-4000131518 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Identification boards for all earth pits near the gate entry office have been installed. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-05-4000131519 | Closed | JHA RAJAN KUMAR | 2026-06-30 | A number of Earth pits near Gate entry office, found without identification board. | 6.14 | Quarterly Inspection | 1723 | PATNA DEPOT | Pit nos to be mentioned | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131519 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131519 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131519 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131519 | AUD-2026-05-2000012310ACN-2026-05-4000131519 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Strainer cleaning of fire engines have been completed on 11.06.26. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-05-4000131520 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Strainer cleaning of Fire engines were claimed to have been carried out on 18.03.26, but the same was not visible in CCTV footage. | 6.15 | Quarterly Inspection | 1723 | PATNA DEPOT | Physical work to be ensured in maintenance and false record generation to be stopped immediately | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131520 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131520 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131520 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131520 | AUD-2026-05-2000012310ACN-2026-05-4000131520 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | There was leakage of lube oil from Fire engine no. 4 from pipe. The pipe has been changed. Leak arrested. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-05-4000131521 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Leak of oil found from Fire Engine no 4. | 6.16 | Quarterly Inspection | 1723 | PATNA DEPOT | Leaks to be arrested and regular cleaning of area surrounding fire engines to be done | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131521 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131521 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131521 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131521 | AUD-2026-05-2000012310ACN-2026-05-4000131521 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Job completed. Bolts tightened. Houskeeping completed. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-05-4000131522 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Valve no V-No 4 of Fire engine 2 found leaking. Housekeeping of Fire engine room is poor | 6.17 | Quarterly Inspection | 1723 | PATNA DEPOT | Leak to be arrested and proper housekeeping Fire engine room to be ensured | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131522 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131522 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131522 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131522 | AUD-2026-05-2000012310ACN-2026-05-4000131522 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Training provided to new securities. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-05-4000131523 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Security found not aware fully of Fire Engine operation. | 6.18 | Quarterly Inspection | 1723 | PATNA DEPOT | Security to made aware of the Fire engion operation. Training to be imparted by location safety officer. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131523 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131523 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131523 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131523 | AUD-2026-05-2000012310ACN-2026-05-4000131523 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The vegetation has been cleared from all the Tankfram and around tankfarm area. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-05-4000131524 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Vegetation found tank farm on tank apron and dyke floor of tanks Tk2, Tk5 and Tk6 | 6.19 | Quarterly Inspection | 1723 | PATNA DEPOT | Proper and regualr cleaning to be done and regualr visit to tank farm areas to be ensured, for early detection of vegetation growth | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131524 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131524 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131524 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131524 | AUD-2026-05-2000012310ACN-2026-05-4000131524 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The same has been made available. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24QUARTERLY INSPECTION | ACN-2026-05-4000131529 | Closed | JHA RAJAN KUMAR | 2026-06-30 | All level Sampler being used for taking tank samples is without lid, hence not effective for intended purpose. | 6.24 | Quarterly Inspection | 1723 | PATNA DEPOT | Proper sampler to be used | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131529 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131529 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131529 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131529 | AUD-2026-05-2000012310ACN-2026-05-4000131529 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The reference Height of 1352.5 cm is updated. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25QUARTERLY INSPECTION | ACN-2026-05-4000131530 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Against mentioned reference height of 1354 cm of TK6, actual reference height observed was 1352.5 cm. | 6.25 | Quarterly Inspection | 1723 | PATNA DEPOT | Reading of TAS needs to be corrected as per the actual. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131530 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131530 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131530 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131530 | AUD-2026-05-2000012310ACN-2026-05-4000131530 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The Physical Dips were checked on 04.06.26. Water about 2.1 cm was drained and all the parameters TAS vs Physical are within allowable limit. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26QUARTERLY INSPECTION | ACN-2026-05-4000131531 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Observed dips of tanks were: Tk6: Ref ht: 1352.5 cm, Gross dip: 170.9 cm, water dip 1.1 cm, product density 815 at 38 deg Cent. | 6.26 | Quarterly Inspection | 1723 | PATNA DEPOT | Corrective action to be taken Location to confirm Physical reading vs TAS | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131531 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131531 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131531 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131531 | AUD-2026-05-2000012310ACN-2026-05-4000131531 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The Physical Dips were checked on 10.06.26. Water about 1.8 cm was drained and all the parameters TAS vs Physical are within allowable limit. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27QUARTERLY INSPECTION | ACN-2026-05-4000131532 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Tk2: Ref ht: 1385 cm, Gross dip: 208.2 cm, water dip 1.2 cm, product density 728 at 36.5 deg Cent. | 6.27 | Quarterly Inspection | 1723 | PATNA DEPOT | Corrective action to be taken Location to confirm Physical reading vs TAS | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131532 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131532 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131532 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131532 | AUD-2026-05-2000012310ACN-2026-05-4000131532 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The Toolbox talk format changed as per HQO format. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.29QUARTERLY INSPECTION | ACN-2026-05-4000131533 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Toolbox talks are not being carried out as per HQO circular. Lack of awareness on points mentioned in Work permits found in Ms Aradhya, Junior Executive- Operations | 6.29 | Quarterly Inspection | 1723 | PATNA DEPOT | Tool box talks to be done as per HQO circular and reported in the format provided. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131533 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131533 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131533 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131533 | AUD-2026-05-2000012310ACN-2026-05-4000131533 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Issues of TT crew in TT parking and rest room resolved. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.30QUARTERLY INSPECTION | ACN-2026-05-4000131534 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Crew interaction: Basic amenities viz, fan at the waiting area, inside amenities block, cold drinking water facility not available.TT crew interacted with were found unaware of utility of emergency button of VTS unit. 4 TT helper were found not aware of how to operate Fire extinguishers. They were provided hands on training | 6.30 | Quarterly Inspection | 1723 | PATNA DEPOT | Basic amenity to be provided for the TT Crew such as fan, drinking water at the rest area and from time to time crew to be trained on operating Fire extinguishers | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131534 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131534 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131534 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131534 | AUD-2026-05-2000012310ACN-2026-05-4000131534 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | All identification and safety boards in the electrical panel room are being updated/replaced to reflect the latest equipment details and safety information. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.31QUARTERLY INSPECTION | ACN-2026-05-4000131535 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Boards to be updated in the electrical panel room. | 6.31 | Quarterly Inspection | 1723 | PATNA DEPOT | Details on the board at the EPR to be updated. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131535 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131535 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131535 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131535 | AUD-2026-05-2000012310ACN-2026-05-4000131535 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Panel doors have been closed immediately. Instructions have been issued to operating and maintenance personnel to keep all MCC panel doors closed and properly secured except during authorized maintenance activities. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.32QUARTERLY INSPECTION | ACN-2026-05-4000131536 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In MCC room, in twp Panels, doors were found kept open | 6.32 | Quarterly Inspection | 1723 | PATNA DEPOT | Doors of the Panels to be kept closed. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131536 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131536 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131536 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131536 | AUD-2026-05-2000012310ACN-2026-05-4000131536 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The floor with with oil stain in DG has been cleaned . | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.33QUARTERLY INSPECTION | ACN-2026-05-4000131537 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Oil spillages found on floor inside both the DG sets. | 6.33 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure regular cleaning gets done of the spot and visit by the locations safety officer and LIC | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131537 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131537 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131537 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131537 | AUD-2026-05-2000012310ACN-2026-05-4000131537 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | LOTO tags have been corrected as per the approved HPCL procedure, ensuring proper information is displayed in the designated format. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.34QUARTERLY INSPECTION | ACN-2026-05-4000131538 | Closed | JHA RAJAN KUMAR | 2026-06-30 | LOTO: Electrician's name is mentioned on LOTO tag | 6.34 | Quarterly Inspection | 1723 | PATNA DEPOT | updation required with correct name | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131538 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131538 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131538 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131538 | AUD-2026-05-2000012310ACN-2026-05-4000131538 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The name of tank has been updated on HVLR panels. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.35QUARTERLY INSPECTION | ACN-2026-05-4000131539 | Closed | JHA RAJAN KUMAR | 2026-06-30 | HVLR operating panel did not have mention of tanks, which are covered by the HVLR. | 6.35 | Quarterly Inspection | 1723 | PATNA DEPOT | Display the tank nos that are covered by the HVLR | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131539 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131539 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131539 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131539 | AUD-2026-05-2000012310ACN-2026-05-4000131539 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The oil spillage has been cleaned and currentky no leak is there. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.36QUARTERLY INSPECTION | ACN-2026-05-4000131540 | Closed | JHA RAJAN KUMAR | 2026-06-30 | TLF Pump House: Oil spillages were found in 3 MS and HSD pumps and also 2 Ethanol pumps | 6.36 | Quarterly Inspection | 1723 | PATNA DEPOT | Leakage to be arrested. Pump houses to be visited daily by LIC and other officers to detect leak, if any and corrective action | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131540 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131540 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131540 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131540 | AUD-2026-05-2000012310ACN-2026-05-4000131540 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The leakage has been cleared. The valve has also been tighteneed. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.37QUARTERLY INSPECTION | ACN-2026-05-4000131541 | Closed | JHA RAJAN KUMAR | 2026-06-30 | leakage observed from HSD pump 2 air release outlet , which reportedly is used for collecting sample | 6.37 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure leakage is arrested and sampling point is made at TT gantry as per IQCM. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131541 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131541 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131541 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131541 | AUD-2026-05-2000012310ACN-2026-05-4000131541 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The sealing has been corrected and checked on daily basis. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.38QUARTERLY INSPECTION | ACN-2026-05-4000131542 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Improper sealing of air release point of MS pumps at TLF pump house. Product could be taken out with seals intact. | 6.38 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure proper sealing in officers presence and visit by the locations safety officer and LIC | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131542 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131542 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131542 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131542 | AUD-2026-05-2000012310ACN-2026-05-4000131542 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Double-bolt connection has been provided at Earth Pit No. 5 to ensure reliable earthing continuity as per the applicable standard. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.40QUARTERLY INSPECTION | ACN-2026-05-4000131544 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In Earth pit no 5, double bolt connection was not there | 6.40 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure proper double bolt connections are in place in all earthpits. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131544 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131544 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131544 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131544 | AUD-2026-05-2000012310ACN-2026-05-4000131544 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The exceess soil has been cleared from the earthpit. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.41QUARTERLY INSPECTION | ACN-2026-05-4000131545 | Closed | JHA RAJAN KUMAR | 2026-06-30 | In Earth pit No.4, excessive mud accumulation inside the pit. Even connections were not visible | 6.41 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure regular checking and cleaning gets done of the spot and visit by the locations safety officer and LIC | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131545 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131545 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131545 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131545 | AUD-2026-05-2000012310ACN-2026-05-4000131545 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The earth pit has been cleaned, and the earthing connection has been rectified. Housekeeping around the earth pit has also been improved to facilitate future inspection and maintenance. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.42QUARTERLY INSPECTION | ACN-2026-05-4000131546 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Earth pit at the entrance had mud and improper connection. | 6.42 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure regular claening gets done of the spot and visit by the locations safety officer and LIC | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131546 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131546 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131546 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131546 | AUD-2026-05-2000012310ACN-2026-05-4000131546 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The eating space has been provided. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.43QUARTERLY INSPECTION | ACN-2026-05-4000131547 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Dialogue with Contract workmen and security was done and issues raised was for providing proper eating space. | 6.43 | Quarterly Inspection | 1723 | PATNA DEPOT | Basic amenity to be provided for the contract men such as fan, and proper the eating area | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131547 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131547 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131547 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131547 | AUD-2026-05-2000012310ACN-2026-05-4000131547 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Appraised the team. Will be observed in next fire drill. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.44QUARTERLY INSPECTION | ACN-2026-05-4000131548 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Fire Drill :showcasing all possibilities for rescue and auxiliary team. | 6.44 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC to ensure all senarios are showcased in any fire drill | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131548 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131548 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131548 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131548 | AUD-2026-05-2000012310ACN-2026-05-4000131548 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Appraised the team. Will be observed in next fire drill. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.45QUARTERLY INSPECTION | ACN-2026-05-4000131549 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Guidance/ directions were not being taken form LIC during fire instances. | 6.45 | Quarterly Inspection | 1723 | PATNA DEPOT | To be ensured. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131549 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131549 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131549 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131549 | AUD-2026-05-2000012310ACN-2026-05-4000131549 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Appraised the team. Will be observed in next fire drill. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.46QUARTERLY INSPECTION | ACN-2026-05-4000131650 | Closed | JHA RAJAN KUMAR | 2026-06-30 | LEL was not checked. | 6.46 | Quarterly Inspection | 1723 | PATNA DEPOT | Ensure LEL to be checked after fire drill | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131650 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131650 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131650 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131650 | AUD-2026-05-2000012310ACN-2026-05-4000131650 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Appraised the team. Will be observed in next fire drill. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.47QUARTERLY INSPECTION | ACN-2026-05-4000131651 | Closed | JHA RAJAN KUMAR | 2026-06-30 | The person spotting the fire did not operate the fire extinguisher and waited after sounding the alarm on the walkie talkie. Even the fire was reported to Security not all persons | 6.47 | Quarterly Inspection | 1723 | PATNA DEPOT | Propoer training to be given to the manpower staff for emergency situation. Safety officer to ensure the same. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131651 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131651 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131651 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131651 | AUD-2026-05-2000012310ACN-2026-05-4000131651 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | Appraised the team. Will be observed in next fire drill. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.48QUARTERLY INSPECTION | ACN-2026-05-4000131652 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Emergency trolley found to be not maintained with all facilities. Even some of the compartment doors could not be opened. Compartments were having material different from what was mentioned on display tag | 6.48 | Quarterly Inspection | 1723 | PATNA DEPOT | Emergency trolley to be maintained properly | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131652 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131652 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131652 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131652 | AUD-2026-05-2000012310ACN-2026-05-4000131652 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | End blind plate has been installed at the roof drain outlet. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-05-4000131525 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Roof drain valve of Tk5 found to be having single valve at outlet, with even end blind plate not fixed. | 6.20 | Quarterly Inspection | 1723 | PATNA DEPOT | Double valves to be provided at outlet and end blinds to be fixed and secured. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131525 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131525 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131525 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131525 | AUD-2026-05-2000012310ACN-2026-05-4000131525 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-30 | The vegetation has been cleared around the tank and below pipelines. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-05-4000131528 | Closed | JHA RAJAN KUMAR | 2026-06-30 | Vegetation found on approaches to some walkways of tank farm | 6.23 | Quarterly Inspection | 1723 | PATNA DEPOT | Walkways need to be clear of any vegetaion. Regular trimming needs to be done | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131528 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131528 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131528 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131528 | AUD-2026-05-2000012310ACN-2026-05-4000131528 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Offcers being groomed by field experience and Training programs by cororation. Nothing to comply in this point. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124854 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Interaction done . | 1.1 | Interaction with all officers (1–1.5 hrs) | 1723 | PATNA DEPOT | Location is having good number of young officers and they need to be groomed for all depot operations by LIC | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011074ACN-2026-03-4000124854 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124854 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124854 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124854 | AUD-2026-03-2000011074ACN-2026-03-4000124854 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Stock loss has improved from Previous year. Gantry augmentation job is under process. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124855 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1723 | PATNA DEPOT | Major project of 6 BAY Ganty augmentation to be expedited . Stock loss , though improved , need to be further enhanced | SOD | Marketing | PZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-12-31 | AUD-2026-03-2000011074ACN-2026-03-4000124855 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124855 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124855 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124855 | AUD-2026-03-2000011074ACN-2026-03-4000124855 | 21 | 21 | 26 | 80 | 0 | 0 | 70 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | The activity was carried on at the location in marchincluding Tank line up, electrical line up. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124856 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Top management expectations and improvement in working of officers clearly advised | 1.6 | Expectations clearly communicated to officers | 1723 | PATNA DEPOT | LIC advised to check readiness of officers in operating TT loading activity without contract worker support | SOD | Marketing | PZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011074ACN-2026-03-4000124856 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124856 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124856 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124856 | AUD-2026-03-2000011074ACN-2026-03-4000124856 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Critical issues covered in HOTO. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124857 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Improvement plan with smooth transition of all major activities discussed for HOTO to new Patna zone | 1.8 | Improvement plans discussed | 1723 | PATNA DEPOT | LIC is advised to prepare the list of all critical issues of location required to be told to new zone | SOD | Marketing | PZR | 2026-04-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-15 | AUD-2026-03-2000011074ACN-2026-03-4000124857 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124857 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124857 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124857 | AUD-2026-03-2000011074ACN-2026-03-4000124857 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | PA systems being used by security in all the drills. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124858 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Usage of sprinklers , foam monitors in railway siding areas checked and found okay during single contingency fire | 2.2 | Double contingency scenario simulated; observations recorded | 1723 | PATNA DEPOT | Usage of PA system during drill and more alertness by security required | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011074ACN-2026-03-4000124858 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124858 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124858 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124858 | AUD-2026-03-2000011074ACN-2026-03-4000124858 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-07-02 | Access control system is working in control room. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124860 | Closed | JHA RAJAN KUMAR | 2026-07-02 | Control room access control system to be rectified | 2.8 | Access control systems checked | 1723 | PATNA DEPOT | to be rectify | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011074ACN-2026-03-4000124860 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124860 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124860 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124860 | AUD-2026-03-2000011074ACN-2026-03-4000124860 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Multiple routes corrected in last 3 months. TT crew have been advised to take shelter on any HPC pump en route. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124863 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Mostly route deviations (because of lot of road projects are working in Bihar), night driving (due to no suitable place nearby to depot for parking) | 3.3 | VTS deviations reviewed | 1723 | PATNA DEPOT | Location need to correct all routes of areas where project work in progress. Also HP pumps locations where night stay or parking available to be shared with TT crew | SOD | Marketing | PZR | 2026-04-15 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-15 | AUD-2026-03-2000011074ACN-2026-03-4000124863 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124863 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124863 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124863 | AUD-2026-03-2000011074ACN-2026-03-4000124863 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Bay checked with Prover in May-June 2026. Deviations reduced. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124864 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Checked and found okay . Bay 3 for HSD to be checked with prover as diff. between invoice qty and MFM/BCU is coming slightly higherin double digit) | 3.11 | MFM vs BCU totalizer comparison checked | 1723 | PATNA DEPOT | to be rectify | SOD | Marketing | PZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011074ACN-2026-03-4000124864 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124864 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124864 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124864 | AUD-2026-03-2000011074ACN-2026-03-4000124864 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Action has been taken for grass cutting in the admin lawn. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124865 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Checked . Gardening improvement advised infront of office | 3.15 | Housekeeping & PPE usage checked | 1723 | PATNA DEPOT | yes | SOD | Marketing | PZR | 2026-05-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-30 | AUD-2026-03-2000011074ACN-2026-03-4000124865 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124865 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124865 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124865 | AUD-2026-03-2000011074ACN-2026-03-4000124865 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Vegetation removed and regulary cut. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124866 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1723 | PATNA DEPOT | yes | SOD | Marketing | PZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011074ACN-2026-03-4000124866 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124866 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124866 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124866 | AUD-2026-03-2000011074ACN-2026-03-4000124866 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | As of 22.06.2026. 17 points have been complied. Expected that except 1-2 points, all points will be complied by 15.07.2026. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124867 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Compliance status reviewed . OISD compliances of 24 nos. pending , to be expedited (out of 26) . | 3.18 | OISD/MDSA/SSA compliance reviewed | 1723 | PATNA DEPOT | Compliance to be expedited | SOD | Marketing | PZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-30 | AUD-2026-03-2000011074ACN-2026-03-4000124867 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124867 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124867 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124867 | AUD-2026-03-2000011074ACN-2026-03-4000124867 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | ALl the issues have been resolved. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124868 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Transporter meet done on 18.3.26 & following osbervations found : 1. Fire screen between tank & cabin need to be provided 100% & else no load will be given 2. Transporter complaint of road jam due to sand laden truck , suggested for alterante route 3. TT reporting messages are not being received 4. Toll claim on certain routes | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1723 | PATNA DEPOT | All these issues to be resolved by location but advised to ensure safe TT loading with zero tolerance | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011074ACN-2026-03-4000124868 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124868 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124868 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124868 | AUD-2026-03-2000011074ACN-2026-03-4000124868 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Grass cutting completed around Tank farm roads and other roads and are regulary cut. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124869 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1723 | PATNA DEPOT | Housekeeping, grass removal , road repair at certain point. One layer of recarpeting needed for all internal roads. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000011074ACN-2026-03-4000124869 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124869 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124869 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124869 | AUD-2026-03-2000011074ACN-2026-03-4000124869 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Gantry augmentation job under progress. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124870 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Reviewed . | 4.3 | Project progress reviewed | 1723 | PATNA DEPOT | location advised to speed up all jobs of Gantry augmentation | SOD | Marketing | PZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-12-31 | AUD-2026-03-2000011074ACN-2026-03-4000124870 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124870 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124870 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124870 | AUD-2026-03-2000011074ACN-2026-03-4000124870 | 21 | 21 | 26 | 80 | 0 | 0 | 70 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | H & HH change/simulation menu is with LIC only login only as per FDS. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-03-4000124871 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Locations officers are not able to show H & HH level hooter working during simulation . | 5.2 | Functioning of all Hooters in control room | 1723 | PATNA DEPOT | LIC to ensure proper tarining to all officers by CAMC vendor | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011074ACN-2026-03-4000124871 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124871 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124871 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124871 | AUD-2026-03-2000011074ACN-2026-03-4000124871 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Half cut drums placed in Railway siding for keeping seals/nut/ bolts. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124873 | Closed | JHA RAJAN KUMAR | 2026-06-23 | found nut-bolts, gaskets lying in open | 6.4 | Railway siding | 1723 | PATNA DEPOT | suggested to have Hald cut drums at every 4 bays for keeping these items | SOD | Marketing | PZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011074ACN-2026-03-4000124873 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124873 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124873 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124873 | AUD-2026-03-2000011074ACN-2026-03-4000124873 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Available in color format | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124862 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1723 | PATNA DEPOT | advised to procure the same urgently | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011074ACN-2026-03-4000124862 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124862 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124862 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011074ACN-2026-03-4000124862 | AUD-2026-03-2000011074ACN-2026-03-4000124862 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Calculation available and water volume is sufficient. | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124861 | Closed | JHA RAJAN KUMAR | 2026-06-23 | Tank 15 - 1760 KL , Tank 16 - 1760 KL , TANK 21 - 1762 KL Total water 5394 KL , against the requirement of 4920 kl | 2.10 | Fire water levels verified | 1723 | PATNA DEPOT | Location advised to check the dead stock of each tank ( physically verify in field ) and calculate the pumpable stock | SOD | Marketing | PZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011074ACN-2026-03-4000124861 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124861 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124861 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011074ACN-2026-03-4000124861 | AUD-2026-03-2000011074ACN-2026-03-4000124861 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Vents have been separated for all the 3 diesel tanks of fire engine shed. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123563 | Closed | JHA RAJAN KUMAR | 2026-03-06 | One issue of Fire engine fuel tank exhaust was pending from earlier visit recommendation. | 1.3 | Pending issues reviewed | 1723 | PATNA DEPOT | Location to separate the exhaust lines of all the fire engine fuel tanks. | SOD | Marketing | PZR | 2025-11-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2025-11-30 | AUD-2026-03-2000011122ACN-2026-03-4000123563 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123563 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123563 | 532 | 8294 | 21 | 8294 | 323 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123563 | AUD-2026-03-2000011122ACN-2026-03-4000123563 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Additional lights installed behind gantry. LuX level is meeting behind gantry. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123564 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Lux level was checked and found less on secondary road behind gantry. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1723 | PATNA DEPOT | Location to take corrective action for ensuring Lux level as per OISD STD 244. | SOD | Marketing | PZR | 2025-11-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2025-11-30 | AUD-2026-03-2000011122ACN-2026-03-4000123564 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123564 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123564 | 532 | 8294 | 21 | 8294 | 323 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123564 | AUD-2026-03-2000011122ACN-2026-03-4000123564 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Access control system restored and is now working. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123565 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Access control system was checked and found working except control room. | 2.8 | Access control systems checked | 1723 | PATNA DEPOT | Access control of control room to be made active | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123565 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123565 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123565 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123565 | AUD-2026-03-2000011122ACN-2026-03-4000123565 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | The area cleaned. No vegetation, unwanted material in these areas. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123566 | Closed | JHA RAJAN KUMAR | 2026-03-06 | All the perosns were found using PPE.Housekeeping around dyke 3 and behind fire engine shed to be improved. | 3.15 | Housekeeping & PPE usage checked | 1723 | PATNA DEPOT | Location to take corrective actions to improve housekeeping in these areas. | SOD | Marketing | PZR | 2025-11-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2025-11-30 | AUD-2026-03-2000011122ACN-2026-03-4000123566 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123566 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123566 | 532 | 8294 | 21 | 8294 | 323 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123566 | AUD-2026-03-2000011122ACN-2026-03-4000123566 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Exhaust fan installed in the Battery room. Batteries cover have been provided. Acid proof tiles have been laid in the battery room. Tiles certificate for acid resistance is available and displayed. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123567 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Battery room: flp exhaust fan, rubber cap for all batteries terminals , certificate of acid proof tiles laid | 6.1 | Battery room condition | 1723 | PATNA DEPOT | Location to take corrective action for deficiencies observed in the battery room. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123567 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123567 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123567 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123567 | AUD-2026-03-2000011122ACN-2026-03-4000123567 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Driver rest room water cooler has been reapired. Now working fine. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123576 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Driver amenity water cooler to be made active | 6.1 | TT Parking area | 1723 | PATNA DEPOT | Driver amenity water cooler to be made active | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123576 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123576 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123576 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011122ACN-2026-03-4000123576 | AUD-2026-03-2000011122ACN-2026-03-4000123576 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Vents have been separated for all the 3 diesel tanks of fire engine shed. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123568 | Closed | JHA RAJAN KUMAR | 2026-03-06 | 3 diesel fuel tanks connected with one common vent pipe header without any valve. Isolation valve for each tank needed to isolate any tank during repair | 6.2 | Fire engine Shed observation | 1723 | PATNA DEPOT | Location to provide separate venting arrangement for all the fuel tanks. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123568 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123568 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123568 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123568 | AUD-2026-03-2000011122ACN-2026-03-4000123568 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | The TRV valve has been replaced and leakage arrested. The TRV is set at pressure of 8.5 kg/cm2. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123569 | Closed | JHA RAJAN KUMAR | 2026-03-06 | TRV provided in header line , leaking perhaps set pressure is wrong . shift the same to farthest point with setting of 10 kg | 6.3 | Fire engine Shed observation | 1723 | PATNA DEPOT | Location to take corrective action for leak arraest and pressure setting of TRV. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123569 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123569 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123569 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123569 | AUD-2026-03-2000011122ACN-2026-03-4000123569 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Gland rope has been changed for JP and fire engine. Leakage has been contained. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123570 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Water leak from jockey pumps & one engine to be stopped | 6.4 | Fire engine Shed observation | 1723 | PATNA DEPOT | Location to check the reason of leakage and take corrective action. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123570 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123570 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123570 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123570 | AUD-2026-03-2000011122ACN-2026-03-4000123570 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | All the TSV have been numbered. Tagged and selaed with details of TSV, date of calibration, due date of calibration and pressure setting. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123571 | Closed | JHA RAJAN KUMAR | 2026-03-06 | All TSVs/SRVs/TRVs should be numbered, selaed and set pressure/ calibration status to be displayed | 6.5 | Field observation | 1723 | PATNA DEPOT | Location to seal the safety valves and display the details of calibration, set pressure. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123571 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123571 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123571 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011122ACN-2026-03-4000123571 | AUD-2026-03-2000011122ACN-2026-03-4000123571 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | License area resgister updated. c-BACS is also working at licensed gate. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123572 | Closed | JHA RAJAN KUMAR | 2026-03-06 | License area register to have entry /exit every time . Also matching of daily IN/OUT to be done and reviewed by safety officer | 6.6 | Security | 1723 | PATNA DEPOT | License area register to have entry /exit every time . Also matching of daily IN/OUT to be done and reviewed by safety officer | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123572 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123572 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123572 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011122ACN-2026-03-4000123572 | AUD-2026-03-2000011122ACN-2026-03-4000123572 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Separate static earthpits have been identified in which wagon earthing is connected. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123573 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Wagon siding wagon earthing is also connected with structure . remove structure earthing and give separate earthing for structure .heavy duty clamp to be provided for wagon earthing | 6.7 | Railway siding | 1723 | PATNA DEPOT | Wagon siding wagon earthing is also connected with structure . remove structure earthing and give separate earthing for structure .heavy duty clamp to be provided for wagon earthing | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123573 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123573 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123573 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011122ACN-2026-03-4000123573 | AUD-2026-03-2000011122ACN-2026-03-4000123573 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | ETP flow chart and SOP displayed. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123574 | Closed | JHA RAJAN KUMAR | 2026-03-06 | ETP - flow chart and SOP to be displayed | 6.8 | ETP area | 1723 | PATNA DEPOT | ETP - flow chart and SOP to be displayed | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123574 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123574 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123574 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011122ACN-2026-03-4000123574 | AUD-2026-03-2000011122ACN-2026-03-4000123574 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
MONISH KUMAR | 2026-07-04 | JHA RAJAN KUMAR | 2026-06-23 | Cables of end flange has been aligned. | SENIOR MANAGEMENT INSPECTION- PATNA IRD | 2025-11-20 | AUD-2026-03-2000011122 | 2025-11-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123575 | Closed | JHA RAJAN KUMAR | 2026-03-06 | Pipeline end flange earthing wires to be aligned in cable trey in pump house manifold. | 6.9 | TWD pump house | 1723 | PATNA DEPOT | Pipeline end flange earthing wires to be aligned in cable trey in pump house manifold. | SOD | Marketing | PZR | 2025-11-25 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2025-11-25 | AUD-2026-03-2000011122ACN-2026-03-4000123575 | BR | [11 empty] | 2025 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011122ACN-2026-03-4000123575 | 2026-08-03 | 77.7538 | 306 | >20 | AUD-2026-03-2000011122 - ACN-2026-03-4000123575 | 532 | 8294 | 21 | 8294 | 328 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011122ACN-2026-03-4000123575 | AUD-2026-03-2000011122ACN-2026-03-4000123575 | 13 | 21 | 26 | 80 | 0 | 0 | 13 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142292 | Open |  |  | bottom loading facility commisioned. Top loading trucks to be converted, Scrap liquidation | 1.3 | Pending issues reviewed | 1953 | RAJAHMUNDRY TERMINAL | Balance 39 Top loading trucks to be converted to bottom loading in timebound manner, RFD to be made for the misc scrap lying in thescrap yard | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015529ACN-2026-07-4000142292 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142292 | 2026-07-22 18:30 | 88.983 | 394 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142292 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000142292 |  | AUD-2026-07-2000015529ACN-2026-07-4000142292 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142293 | Open |  |  | Recent review recommendations were reviewed along with pending audit points of T4S ,SSA & MDSA | 1.4 | Earlier action points status checked | 1953 | RAJAHMUNDRY TERMINAL | Pending audit points of T4 S audit, SSA & MDSA to be completed by 30.09.2026 | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015529ACN-2026-07-4000142293 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142293 | 2026-07-22 18:30 | 88.983 | 394 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142293 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000142293 |  | AUD-2026-07-2000015529ACN-2026-07-4000142293 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142297 | Open |  |  | Checked . 4 cameras are not working. Cameras are hazy at Emergency exit gate, TT parking,ETP,watch tower 3,PTZ camera tank 3B & 3C centre. Tk 3C back side PTZ camera is not rotating. Camera angle to be corrected for cameras at HT structure corner and TT exit gate. | 2.6 | CCTV functioning checked | 1953 | RAJAHMUNDRY TERMINAL | Location to ensure the 4 nos CCTV put back into service on priority basis. To take with AMC vendor to rectify the CCTV cameras appearing hazy. | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015529ACN-2026-07-4000142297 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142297 | 2026-07-22 18:30 | 88.983 | 302 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142297 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000142297 |  | AUD-2026-07-2000015529ACN-2026-07-4000142297 | 21 |  | 27 | 80 | 1 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143354 | Open |  |  | ESA , MDSA, TAS , SSA compliances are reviewed .Advised location to ensure 100 % compliance as per target date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1953 | RAJAHMUNDRY TERMINAL | 100% Compliance as per target dates | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015529ACN-2026-07-4000143354 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143354 | 2026-07-22 18:30 | 88.983 | 394 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143354 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143354 |  | AUD-2026-07-2000015529ACN-2026-07-4000143354 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143356 | Open |  |  | Maintenance activities reviewed. Tank 6B recommissioning pending for a long time. Tank 3B, Tank 1B , Tank 2A repair is pending. | 4.2 | Maintenance activities reviewed | 1953 | RAJAHMUNDRY TERMINAL | Tank 6B recommissioning to be done by 15.07.2026. PO to be placed for Tank 3B , Tank 1B, Tank 2A repair by 31.07.2026 | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015529ACN-2026-07-4000143356 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143356 | 2026-07-22 18:30 | 88.983 | 333 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143356 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143356 |  | AUD-2026-07-2000015529ACN-2026-07-4000143356 | 21 |  | 27 | 80 | 1 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143357 | Open |  |  | Yes. The 3 nos ongoing NPCB projects are reviewed & advised location to complete the jobs within target dates i.e. by Sept 2026 | 4.3 | Project progress reviewed | 1953 | RAJAHMUNDRY TERMINAL | Completion of the three carryover NPCB projects within timelines | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015529ACN-2026-07-4000143357 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143357 | 2026-07-22 18:30 | 88.983 | 394 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143357 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143357 |  | AUD-2026-07-2000015529ACN-2026-07-4000143357 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143359 | Open |  |  | Misc scrap and scrap generated from the ongoing project of hydrant line replacement is available | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1953 | RAJAHMUNDRY TERMINAL | RFD to be made for the misc scrap lying in the scrap yard | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015529ACN-2026-07-4000143359 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143359 | 2026-07-22 18:30 | 88.983 | 333 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143359 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143359 |  | AUD-2026-07-2000015529ACN-2026-07-4000143359 | 21 |  | 27 | 80 | 1 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-07-4000143360 | Open |  |  | MFM based accounting being done for OMC(IOC) PLTs. | 5.1 | MFM based accounting at Pipeline and OMC location | 1953 | RAJAHMUNDRY TERMINAL | To follow up with VVSPL for MFM calibration for implementing MFM based accounting. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015529ACN-2026-07-4000143360 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143360 | 2026-07-22 18:30 | 88.983 | 394 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143360 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143360 |  | AUD-2026-07-2000015529ACN-2026-07-4000143360 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143362 | Open |  |  | For bay conversion from top loading to bottom loading , railing removed on one side at all bays which is a unsafe condition. | 6.2 |  | 1953 | RAJAHMUNDRY TERMINAL | Railing to be provided at all bays for fall prevention | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015529ACN-2026-07-4000143362 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143362 | 2026-07-22 18:30 | 88.983 | 302 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143362 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143362 |  | AUD-2026-07-2000015529ACN-2026-07-4000143362 | 21 |  | 27 | 80 | 1 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143363 | Open |  |  | E-Diary observations not being recorded | 6.3 |  | 1953 | RAJAHMUNDRY TERMINAL | E-Diary minimum 5 observations to be recorded on daily basis | SOD | Marketing | SCR | 2026-06-22 |  | 5 |  | S1 | F5 | 2026-06-22 | AUD-2026-07-2000015529ACN-2026-07-4000143363 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143363 | 2026-07-22 18:30 | 88.983 | 294 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143363 | 532 | 8294 | 21 | 8294 | 119 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143363 |  | AUD-2026-07-2000015529ACN-2026-07-4000143363 | 21 |  | 27 | 80 | 1 | 2 | 42
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143364 | Open |  |  | Cost savings under samridhi 2.0 are nil | 6.4 |  | 1953 | RAJAHMUNDRY TERMINAL | Cost savings under samridhi 2.0 to be made. | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015529ACN-2026-07-4000143364 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143364 | 2026-07-22 18:30 | 88.983 | 333 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143364 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143364 |  | AUD-2026-07-2000015529ACN-2026-07-4000143364 | 21 |  | 27 | 80 | 1 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143365 | Open |  |  | TT cycle time upto May 2026 is high | 6.5 |  | 1953 | RAJAHMUNDRY TERMINAL | TT cycle time to be improved to meet the given target | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015529ACN-2026-07-4000143365 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143365 | 2026-07-22 18:30 | 88.983 | 333 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143365 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015529ACN-2026-07-4000143365 |  | AUD-2026-07-2000015529ACN-2026-07-4000143365 | 21 |  | 27 | 80 | 1 | 2 | 48
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-04 | Interaction with individual officers carried out for disussing roles and responsibilities as per protfolio and goals and targets.AOP targets also discussed | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138566 | Closed | ROY TAVARES | 2026-07-04 | Reviewed performance of all Officers and officers were found focussed on the Goals and Targets with emphasis on process/efficiency improvement | 1.2 | Performance review conducted | 1797 | GULBARGA NEW IRD | Team to focus on G&T for the year and come up with improvements process and work efficency. LIC advised to review the individual performance and advise officers to ensure 100% achievement. | SOD | Marketing | SWZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-06-2000013300ACN-2026-06-4000138566 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138566 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138566 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138566 | AUD-2026-06-2000013300ACN-2026-06-4000138566 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-04 | Proposal of 5000KL tank has been forwarded to zone for approval | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138570 | Closed | ROY TAVARES | 2026-07-04 | HSD tankage Is inadequate | 1.8 | Improvement plans discussed | 1797 | GULBARGA NEW IRD | Location advised to submit proposal for additional tankage | SOD | Marketing | SWZ | 2026-06-25 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | ASSET INTEGRITY | S3 | F2 | 2026-06-25 | AUD-2026-06-2000013300ACN-2026-06-4000138570 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138570 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138570 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138570 | AUD-2026-06-2000013300ACN-2026-06-4000138570 | 21 | 21 | 27 | 80 | 5 | 5 | 43 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-04 | Platform provided for foam monitor no 22 | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138575 | Closed | ROY TAVARES | 2026-07-04 | During the visit, a hands-on equipment trial was conducted without contractual assistance. The following officers demonstrated successful.New Officers Rohit operated HVLR, Shubham operated WCF Monitor and Rupesh operated Sprinkler for TK-02 operation: FM 22: No platform available, Monitor operation done by Shubham. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1797 | GULBARGA NEW IRD | Platform got Foam Monitor:22 to be provided | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138575 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138575 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138575 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138575 | AUD-2026-06-2000013300ACN-2026-06-4000138575 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-04 | All bays have been rechecked and issue of viariation resolved. Being monitored on daily basis | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138580 | Closed | CHANDRAKANTH JOSHI | 2026-07-06 | Location is regaularly reviewing MFM Vs BCU totaliser report and the same is attested by LIC. | 3.11 | MFM vs BCU totalizer comparison checked | 1797 | GULBARGA NEW IRD | Bay:07 MS and Ethanol variations observed on many days to identify RCA and rectify the same. | SOD | Marketing | SWZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138580 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138580 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138580 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138580 | AUD-2026-06-2000013300ACN-2026-06-4000138580 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-04 | Scrap has disposed Details attached | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138583 | Closed | ROY TAVARES | 2026-07-04 | Scrap upliftment is in progress. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1797 | GULBARGA NEW IRD | Location to expedite the disposal of scrap at the earliest. | SOD | Marketing | SWZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013300ACN-2026-06-4000138583 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138583 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138583 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138583 | AUD-2026-06-2000013300ACN-2026-06-4000138583 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143367 | Open |  |  | 1. CP System not working. PO placed vendor not responding. 2. Smoke detector 1 loop is not working- Admin building/Control room/Battery room. 3. Smoke detector integration with TAS not available 4. SAP-TFMs performance very low. Tanks not put in AIM HOLD exception | 1.3 | Pending issues reviewed | 3708 | VISAKH NBOT | 1. To follow up with the vendor and expedite work completion 2. Smoke detector 1 loop to be made functional 3. Smoke detector integration with TAS to be completed 4. Tanks to be put in AIM HOLD exception with disussion with Zone Operations | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015047ACN-2026-07-4000143367 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143367 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143367 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143367 |  | AUD-2026-07-2000015047ACN-2026-07-4000143367 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143368 | Open |  |  | Smoke detector integration still pending. Location has hold the vendor bill. Vendor has to respond immediately | 1.4 | Earlier action points status checked | 3708 | VISAKH NBOT | Smoke detector integration to be expedited. | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143368 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143368 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143368 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143368 |  | AUD-2026-07-2000015047ACN-2026-07-4000143368 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143369 | Open |  |  | Tanks not put in AIM HOLD exception by zone. TT accident irregularity filenote to be approved by zone | 1.5 | HQO / Zonal support required identified | 3708 | VISAKH NBOT | Zone operations to extend help. | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143369 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143369 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143369 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143369 |  | AUD-2026-07-2000015047ACN-2026-07-4000143369 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143381 | Open |  |  | Checked TT fitting and discpline of TT No AP39UD3767. Fire extinguisher of the TT was operated. | 3.1 | TT fittings & discipline checked | 3708 | VISAKH NBOT | ID card to be issued to all Delivered TT Crew after obtaining valid police verification. | SOD | Marketing | SCR | 2026-07-30 |  | 5 |  | S1 | F5 | 2026-07-30 | AUD-2026-07-2000015047ACN-2026-07-4000143381 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143381 | 2026-09-18 17:30 | 31.0247 | 332 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143381 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143381 |  | AUD-2026-07-2000015047ACN-2026-07-4000143381 | 21 |  | 27 | 80 | 2 | 1 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143383 | Open |  |  | Auto vs Manual reconciliation checked. Approx 24.40% reco is done on manual dips for tanks 12A , 12B , 101, 203 and 212 tank reco is done on manul dips daily, | 3.8 | Auto vs Manual reconciliation checked | 3708 | VISAKH NBOT | 12A , 12B , 101, 203 and 212 to be put in AIM HOLD exception with the help of zone | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143383 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143383 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143383 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143383 |  | AUD-2026-07-2000015047ACN-2026-07-4000143383 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143385 | Open |  |  | TFMS/SAP reconciliation checked & performance is approx 74% vs target of 95% | 3.10 | TFMS/SAP reconciliation checked | 3708 | VISAKH NBOT | Empty tank & Tank under VR use to be put in AIM HOLD exception with the help of zone to maximize the TFMS/SAP reconciliation % | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143385 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143385 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143385 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143385 |  | AUD-2026-07-2000015047ACN-2026-07-4000143385 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143388 | Open |  |  | T4S Date of Audit: 12-03-26 TO 14-03-26, Total no of points: 12, Complied: 5, Pending: 7 MDSA Date of Audit: 29-12-25 TO 31-12-25,Total no of points: 71, Complied: 39, Pending: 32 SSA Date of Audit: 03-09-2025 to 08-09-2025, Total no of points: 17, Complied: 14, Pending: 3 HLSA Date of Audit: 31-03-2026, Total no of points: 25, Complied: 20, Pending: 5 GM O&D Visit Date of Audit: 31-03-2026, Total no of points: 23, Complied: 06, Pending: 17 | 3.18 | OISD/MDSA/SSA compliance reviewed | 3708 | VISAKH NBOT | All pending points to be complied in a time bound manner | SOD | Marketing | SCR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143388 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143388 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143388 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015047ACN-2026-07-4000143388 |  | AUD-2026-07-2000015047ACN-2026-07-4000143388 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143390 | Open |  |  | Maintenance activities reviewed.CP system, Weigh Bridge, Smoke Detector, High Mast projects to be expedited. | 4.2 | Maintenance activities reviewed | 3708 | VISAKH NBOT | All jobs to be completed in a time bound manner | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143390 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143390 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143390 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143390 |  | AUD-2026-07-2000015047ACN-2026-07-4000143390 | 21 |  | 27 | 80 | 2 | 1 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143391 | Open |  |  | CP system, Weigh Bridge, Smoke Detector, High Mast projects to be expedited | 4.3 | Project progress reviewed | 3708 | VISAKH NBOT | All NPCB projects to be completed without time overruns | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143391 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143391 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143391 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143391 |  | AUD-2026-07-2000015047ACN-2026-07-4000143391 | 21 |  | 27 | 80 | 2 | 1 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-06 | 1. Product was made available and MDS distributed to other lcoations 2. Received Full HSD rake from VJA and wagons given back to IOC. 3. Details sent to HR 4. CSR activity started along with all approvals 5. Meeting with municpality scheduled on 08.07.2026 6. Additional budget proposal for TK-03 inspection submitted to zone/. | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138569 | Closed | ROY TAVARES | 2026-07-06 | 1. Product availability for execution of indents. Distribution of MDP to other locations. 2. One Full HSD rake as OPM for giving back 40 wagons of HSD to IOC. 3. One GAT resigned and replacement not provided. Issue taken up with Zonal HR 4. Assistance in CSR activity for completion of sale deed 5. Way forward for 0.25 Acre old Gulbarga Depot land 6. Additional budget required for inlinetank inspection of TK-03(HSD) and TK-14(MS) | 1.5 | HQO / Zonal support required identified | 1797 | GULBARGA NEW IRD | LIC to follow up for same | SOD | Marketing | SWZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013300ACN-2026-06-4000138569 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138569 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138569 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138569 | AUD-2026-06-2000013300ACN-2026-06-4000138569 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-06 | All above ground tank dips taken in June'26 by LIC | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138579 | Closed | ROY TAVARES | 2026-07-06 |  | 3.7 | Inventory physical dip of minimum two tanks taken | 1797 | GULBARGA NEW IRD | Minimum one dip of all tanks monthly to be taken by LIC. | SOD | Marketing | SWZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138579 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138579 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138579 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138579 | AUD-2026-06-2000013300ACN-2026-06-4000138579 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-06 | Works related to two projects completed and closed | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138582 | Closed | ROY TAVARES | 2026-07-06 | Reviewed progress of 2 current projects related to Bottom Loading and VHF sets procurement. | 4.3 | Project progress reviewed | 1797 | GULBARGA NEW IRD | All 2 ongoing projects to be expedited before 30.06.2026 | SOD | Marketing | SWZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138582 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138582 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138582 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138582 | AUD-2026-06-2000013300ACN-2026-06-4000138582 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 44
CHANDRAKANTH JOSHI | 2026-07-06 | ROY TAVARES | 2026-07-06 | Two NPCB projects work completed and closed | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122843 | Closed | ROY TAVARES | 2026-07-06 | As on date location has completed and verified the Supply and Installation of FMP JB and Gulbarga_S&I of Lights. Bottom loading project is under execution | 4.3 | Project progress reviewed | 1797 | GULBARGA NEW IRD | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | SOD | Marketing | SWZ | 2026-03-30 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-03-30 | AUD-2026-03-2000010764ACN-2026-03-4000122843 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122843 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122843 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122843 | AUD-2026-03-2000010764ACN-2026-03-4000122843 | 21 | 21 | 26 | 80 | 5 | 5 | 30 | 44
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143155 | Open |  |  | Individual review of officer carried out with respect to KPI and overall location performance | 1.2 | Performance review conducted | 1644 | KOLKATA-I TERMINAL | Officers were advised to have hand on exercise for operating all the fire fighting equipment. DSO to provide the safety training asper OISD 154 to the newly reported officers. Further, all officers should have the knowledge w.r.t positioning of all the safety critical equipment and ESD. LIC to closely monitor the losses booked in ethanol and to arrest the losses by suitable actions. Officer handling ethanol must ensure that the ethanol loss in each TT is booked in SAP. Officer to be extra vigilant on qty./ temp etc while processing ethanol GRN. All officers to be included in FOC and role to be clearly clarified to the officers. TT planning officers should be aware about the bottom loading TT fittings, VRU functioning, TT calibration modalities. All sensitive operations are not to be down deligated to GAT, CEs or Contract employees. | SOD | Marketing | EZ | 2026-07-20 |  | 5 |  | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143155 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143155 | 2026-09-18 | 31.7538 | 322 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143155 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143155 |  | AUD-2026-07-2000015090ACN-2026-07-4000143155 | 21 |  | 27 | 80 | 0 | -7 | 46
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143156 | Open |  |  | 1.DGR Sponsorship list to be expedited for early tendering 2. Regular E M Lock checking by LIC Master key and records to be maintained 3. Adequate E M Locks & Key inventory at location to be maintained 4. EBMS 20% blending check at TT Gantry to be ensured and records to be maintained 5. Off Spec FO/ LDO to be liquidated. MTO Hexane also to be liquidated. LSHFHSD to be supplied to DS customers in coordination DS RM. TK210 to be put in service after PESO approval. | 1.3 | Pending issues reviewed | 1644 | KOLKATA-I TERMINAL | Expeditious action / compliance to be taken | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143156 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143156 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143156 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143156 |  | AUD-2026-07-2000015090ACN-2026-07-4000143156 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143157 | Open |  |  | 1. Safety PLC Switchover job to be expedited in close coordination with vendor. 2. TT Dip elimination file note - Pending (This point was also discussed in last inspection) 3. Upon review, it was observed that NIL Near Miss, UCs and UAs are being recorded at location (This point was also discussed in last inspection) 4. All pending payments of M/s AST to be reviewed and cleared | 1.4 | Earlier action points status checked | 1644 | KOLKATA-I TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143157 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143157 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143157 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143157 |  | AUD-2026-07-2000015090ACN-2026-07-4000143157 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143158 | Open |  |  | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1644 | KOLKATA-I TERMINAL | 1. Location to upload the 100%TT dip checking data in SAP. 2. Location to ensure the recovery w.r.t VTS equipment charges & SAP V/s VTS RTKM difference 3. Location to monitor and take action line with ITDS for the deviations (route/ speed/ night halting etc). 4. All open HLSA points to be closed 5. ERDMP of BB-II is due in Feb'27. All purchase activity to be done well in advance. 6. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 7. Manual allocation of TT in IMS to be minimised and records with justification to be maintained for all such cases. 8. EM lock handling and Monitoring : Part load must not be executed without prior approval of zonal O&D head,Post decantation OTP to be ensured, programming key usages to be ensured for all TT within a period of max. 1 month. 9. All RTGPs to be reviewed periodically and closed 10. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL cases of scope change in any AR to be done without prior approval. | SOD | Marketing | EZ | 2026-07-31 |  | 10 |  | S2 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143158 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143158 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143158 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015090ACN-2026-07-4000143158 |  | AUD-2026-07-2000015090ACN-2026-07-4000143158 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143159 | Open |  |  | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1644 | KOLKATA-I TERMINAL | 1. CBAC to be made operational in Tank Farm, TT Gantry.(This was also observed in last inspection) 2. Calibration verification forTTs to be done and records maintained. 3. TT Dip elimination FN to be processed at the earliest. | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143159 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143159 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143159 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143159 |  | AUD-2026-07-2000015090ACN-2026-07-4000143159 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143160 | Open |  |  | Location has to prepare the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1644 | KOLKATA-I TERMINAL | Location to ensure to complete all the fire scenario as per ERDMP in the mock drills. Drill in BB-II to be conducted when empty rake (after unloading) is present with scenario of flash fire on dome cover while product getting unloaded. | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143160 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143160 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143160 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143160 |  | AUD-2026-07-2000015090ACN-2026-07-4000143160 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143162 | Open |  |  | Location has total of 110 CCTV Camera and 94 found as functional. Random video recording of the CCTV at main gate area were checked. CCTV back up of only 60 days was found. | 2.6 | CCTV functioning checked | 1644 | KOLKATA-I TERMINAL | 1. Installation of new CCTV job to be expedited 2. CCTV back up of 92 days must be ensured without fail 3. Security check at TT in gate to be strengthened 4. No other vehicle (apart from TTs designated for loading at TTG) should enter the TT Gantry area for weighment / parking. | SOD | Marketing | EZ | 2026-07-20 |  | 5 |  | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143162 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143162 | 2026-09-18 | 31.7538 | 322 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143162 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143162 |  | AUD-2026-07-2000015090ACN-2026-07-4000143162 | 21 |  | 27 | 80 | 0 | -7 | 46
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143170 | Open |  |  | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1644 | KOLKATA-I TERMINAL | MS and Ethanol losses to be brought under control | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143170 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143170 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143170 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143170 |  | AUD-2026-07-2000015090ACN-2026-07-4000143170 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143176 | Open |  |  | OISD - NIL pending Point HLSA : 15 pending points T4S : 25 pending points SSA - 1 Pending point MDSA - 41 pending point Comprehensive Audit - 6 pending points Premonsoon Checks for tanks : 11 pending points Sr. management Inspection in Q4 FY 25-26 : 7 pending points | 3.18 | OISD/MDSA/SSA compliance reviewed | 1644 | KOLKATA-I TERMINAL | Location to close the open points at the earliest and also closure in SAP | SOD | Marketing | EZ | 2026-08-31 |  | 8 |  | S2 | F4 | 2026-08-31 | AUD-2026-07-2000015090ACN-2026-07-4000143176 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143176 | 2026-09-18 | 31.7538 | 364 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143176 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015090ACN-2026-07-4000143176 |  | AUD-2026-07-2000015090ACN-2026-07-4000143176 | 21 |  | 27 | 80 | 0 | -7 | 52
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143178 | Open |  |  | 1. CCTV Inspatalltion job to be expedited 2. BB-II close loop line project to be closed at the earliest 3. TFMS project PO to be expedited followed by field work | 4.3 | Project progress reviewed | 1644 | KOLKATA-I TERMINAL | To be expedited | SOD | Marketing | EZ | 2026-07-31 |  | 4 |  | S1 | F4 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143178 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143178 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143178 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143178 |  | AUD-2026-07-2000015090ACN-2026-07-4000143178 | 21 |  | 27 | 80 | 0 | -7 | 48
[5 empty] | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143179 | Open |  |  | Scrap Disposal to be expedited. Scrap [Fire Extingusher, Unloading hose] found in Kolkata Terminal-II. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1644 | KOLKATA-I TERMINAL | All scrap items to be identified by H-1 and disposal in H-2 | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-07-2000015090ACN-2026-07-4000143179 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143179 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143179 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015090ACN-2026-07-4000143179 |  | AUD-2026-07-2000015090ACN-2026-07-4000143179 | 21 |  | 27 | 80 | 0 | -7 | 57
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143185 | Open |  |  | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1656 | DURGAPUR DEPOT | 1. Pending Scrap disposal to be expedited 2. Calibration verification for TTs to be done and records maintained | SOD | Marketing | EZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015091ACN-2026-07-4000143185 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143185 | 2026-08-07 13:00 | 73.2122 | 394 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143185 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143185 |  | AUD-2026-07-2000015091ACN-2026-07-4000143185 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143194 | Open |  |  | TT fitting check carried for TT no. WB19J7191 and found satisfactory. Monkey ladder in TT no. WB39B6131 found not in alignment with the approved PESO drawing. Rear Crash Guard from left side for TT no. WB37D5926, WB55B3855, WB41J2548, WB39B6231 | 3.1 | TT fittings & discipline checked | 1656 | DURGAPUR DEPOT | Corrective action to be taken. | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143194 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143194 | 2026-08-07 13:00 | 73.2122 | 302 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143194 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143194 |  | AUD-2026-07-2000015091ACN-2026-07-4000143194 | 21 |  | 27 | 80 | 0 | 0 | 44
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143195 | Open |  |  | Random checking of the dip for TT no. WB19J7191 & WB37D5926 post loading done and found satisfactory. There was difference in DL for 5 KL chamber no. 1&3 and PL for 5 KL chamber no. 3 & 4 for TT no. WB39B6231 | 3.2 | Post-loading dip checks verified | 1656 | DURGAPUR DEPOT | Corrective action to be taken. | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143195 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143195 | 2026-08-07 13:00 | 73.2122 | 302 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143195 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143195 |  | AUD-2026-07-2000015091ACN-2026-07-4000143195 | 21 |  | 27 | 80 | 0 | 0 | 44
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143400 | Open |  |  | 100 % Reco done through Manual dips due to WDM issue and dip not getting posted. It was given to understand that the WDMs to Durgapur is planned to be dispatched from Hassan. | 3.8 | Auto vs Manual reconciliation checked | 1656 | DURGAPUR DEPOT | Location to closely coordinate with Hassan and vendor M/s AST for early installation and functioning of the dip posting. | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-07-2000015091ACN-2026-07-4000143400 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143400 | 2026-08-07 13:00 | 73.2122 | 394 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143400 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143400 |  | AUD-2026-07-2000015091ACN-2026-07-4000143400 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143401 | Open |  |  | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1656 | DURGAPUR DEPOT | Ethanol losses to be brought under control | SOD | Marketing | EZ | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-07-2000015091ACN-2026-07-4000143401 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143401 | 2026-08-07 13:00 | 73.2122 | 364 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143401 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143401 |  | AUD-2026-07-2000015091ACN-2026-07-4000143401 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143408 | Open |  |  | MOC is being reviewed at zonal level on regular basis. 3 no. of open obsolete MOC not closed. | 3.17 | MOC status reviewed | 1656 | DURGAPUR DEPOT | Location to review the open MOC periodically and get the needful done for timely closure in system | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143408 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143408 | 2026-08-07 13:00 | 73.2122 | 302 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143408 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143408 |  | AUD-2026-07-2000015091ACN-2026-07-4000143408 | 21 |  | 27 | 80 | 0 | 0 | 44
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143411 | Open |  |  | NIL ongoing Project. BG receipt from NHAI to be expedited (This is a repeat point vis-a-vis last quarterly audit). | 4.3 | Project progress reviewed | 1656 | DURGAPUR DEPOT | To be expedited | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143411 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143411 | 2026-08-07 13:00 | 73.2122 | 302 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143411 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143411 |  | AUD-2026-07-2000015091ACN-2026-07-4000143411 | 21 |  | 27 | 80 | 0 | 0 | 44
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143412 | Open |  |  | Location disposed off the scrap in last FY However, Scraps (MS scrap) found lying in the scrap yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1656 | DURGAPUR DEPOT | Location to complete the scrap disposal and make location scrap free | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-07-2000015091ACN-2026-07-4000143412 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143412 | 2026-08-07 13:00 | 73.2122 | 394 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143412 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143412 |  | AUD-2026-07-2000015091ACN-2026-07-4000143412 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143413 | Open |  |  | 1. Double safety harness to be used by all the stakeholders at TTG for TT dip checking, TT locking and TT security checking platform 2. Wear and tear found w.r.t Insulation rubber on the swing ladder at TTG, TT locking shed, TT security checking platform 3. Itis advised to use non sparking tool only in the licenced area. 4. Open Path HCD at pump house found non functional 5. It was given to understand that the power dosing is being done manually sometime. Location to get MOC approval prior to such irregular activity. 6. Emergency Escape ladder TTG pathway found blocked with plants in plastic drums. To be removed. Flammable materials not to be used at all inside the licenced area 7. Dry Grass at TTG to be removed periodically. LIC to personally monitor the same 8. Cableneeds to be dressed and cable tray to be used for cable going in BCU post bottom loading project 9. DCV cover at TTG was found open. All DCVs to be covered with tight box with lock and key management system 10. Cable dressing to be done near HVLR 2 Panel 11. Old AC found near the lube godown. To be disposed off. 12. Bonding / Electrical continuity of Ethanol unloading hose found not as per requirement. 13 All the 3 no. of Fire Engine found in local mode. DSO and LIC to ensure that the fire engine are in auto mode all the time 14. As per TAS screen, secondary link found non functional for TMPC, security PC 15. TK1 outlet ROSOV is not getting operated in remote mode 16. TK-2 and TK-5, inlet ROSOV not getting operated in remote mode 17. To case of Sick TT i.e. on 2nd Mar'26 and 6th Mar'26. Joint inspection record with the transporter was not maintained. 18. Leakage from the main suction header was found for water tank - To be arrested on priority 19. Lube Godown: Several leaky packages observed. Regular physical Inventory to be taken and necessary warehouse losses, if any to be booked for proper reconciliation. | 6.1 | Additional Observations | 1656 | DURGAPUR DEPOT | Corrective action to be taken | SOD | Marketing | EZ | 2026-07-15 |  | 5 |  | S1 | F5 | 2026-07-15 | AUD-2026-07-2000015091ACN-2026-07-4000143413 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143413 | 2026-08-07 13:00 | 73.2122 | 317 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143413 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143413 |  | AUD-2026-07-2000015091ACN-2026-07-4000143413 | 21 |  | 27 | 80 | 0 | 0 | 46
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143418 | Open |  |  | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1650 | HALDIA TERMINAL | 1. Location to upload the 100%TT dip checking data in SAP. 2. Location to ensure the recovery w.r.t VTS equipment charges 3. Location to monitor and take action line with ITDS for the deviations (route/ speed/ night halting etc). 4. All open HLSA points to beclosed 5. T4S Audit is due in Oct'26. All purchase activity to be done well in advance. 6. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 7. Manual allocation of TT in IMS to be minimised and records with justification. to be maintained for all such cases. 8. EM lock handling and Monitoring : Part load must not be executed without prior approval, Post decantation OTP to be ensured, programming keyusages to be ensured for all TT within a period of max. 1 month. 9. All RTGP to be reviewed periodically and closed 10. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL case of scope change in any AR to be done without prior approval. | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143418 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143418 | 2026-08-20 00:14 | 60.7441 | 302 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143418 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015092ACN-2026-07-4000143418 |  | AUD-2026-07-2000015092ACN-2026-07-4000143418 | 21 |  | 27 | 80 | 5 | 5 | 44
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143428 | Open |  |  | TT fitting check carried for TT no. WB29D9296 and found satisfactory. Monkey ladder in TT no. WB33D8985 found not in alignment withthe approved PESO drawing. | 3.1 | TT fittings & discipline checked | 1650 | HALDIA TERMINAL | Corrective action to be taken. | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143428 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143428 | 2026-08-20 00:14 | 60.7441 | 302 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143428 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015092ACN-2026-07-4000143428 |  | AUD-2026-07-2000015092ACN-2026-07-4000143428 | 21 |  | 27 | 80 | 5 | 5 | 44
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143431 | Open |  |  | 100 % Reco done through Manual dips due to WDM issue and dip not getting posted. It was given to understand that the WDMs to Haldiais planned to be dispatched from Hassan. | 3.8 | Auto vs Manual reconciliation checked | 1650 | HALDIA TERMINAL | Location to closely coordinate with Hassan and vendor M/s AST for early installation and functioning of the dip posting. | SOD | Marketing | EZ | 2026-07-31 |  | 4 |  | S1 | F4 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143431 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143431 | 2026-08-20 00:14 | 60.7441 | 333 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143431 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015092ACN-2026-07-4000143431 |  | AUD-2026-07-2000015092ACN-2026-07-4000143431 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143432 | Open |  |  | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1650 | HALDIA TERMINAL | Black oil losses to be brought under control | SOD | Marketing | EZ | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143432 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143432 | 2026-08-20 00:14 | 60.7441 | 333 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143432 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015092ACN-2026-07-4000143432 |  | AUD-2026-07-2000015092ACN-2026-07-4000143432 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143435 | Open |  |  | Local loading record maintained at location up to Dec'25. Observations : 1. TT no. is not being mentioned while making the order in BCU for local loading for all the local loads 2. Justification and records not maintained for local loading done in Jan'26 and Feb'26 3. It is noted that all the black oil TTs are being loaded thru local loading only | 3.14 | Local loading checks (if applicable) | 1650 | HALDIA TERMINAL | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-07-15 |  | 10 |  | S2 | F5 | 2026-07-15 | AUD-2026-07-2000015092ACN-2026-07-4000143435 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143435 | 2026-08-20 00:14 | 60.7441 | 317 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143435 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015092ACN-2026-07-4000143435 |  | AUD-2026-07-2000015092ACN-2026-07-4000143435 | 21 |  | 27 | 80 | 5 | 5 | 46
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143438 | Open |  |  | OISD - NIL pending Point SSA - 5 Pending point MDSA - 6 pending point Comprehensive Audit - 78 points | 3.18 | OISD/MDSA/SSA compliance reviewed | 1650 | HALDIA TERMINAL | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-07-31 |  | 8 |  | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143438 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143438 | 2026-08-20 00:14 | 60.7441 | 333 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143438 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015092ACN-2026-07-4000143438 |  | AUD-2026-07-2000015092ACN-2026-07-4000143438 | 21 |  | 27 | 80 | 5 | 5 | 48
[5 empty] | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143440 | Open |  |  | Location disposed off the scrap in last FY However, Scraps (MS scrap/ Cables etc) found lying in the scrap yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1650 | HALDIA TERMINAL | Location to complete the scrap disposal and make location scrap free | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-07-2000015092ACN-2026-07-4000143440 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143440 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143440 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015092ACN-2026-07-4000143440 |  | AUD-2026-07-2000015092ACN-2026-07-4000143440 | 21 |  | 27 | 80 | 5 | 5 | 57
CHANDRAKANTH JOSHI | 2026-07-06 | SHARMA SURAJ | 2026-07-06 | AR-AFFF foam is required for Ethanol Tanks. At Gulbarga IRD, only one above-ground Ethanol Tank of 500 KL Capacity is available in MS Dyke. As per foam calculation, 1.84 KL foam is required for AG Ethanol Tank. Calculation sheet is attached for reference. As on date 06.07.2026, 4 KL AR-AFFF foam is available which is more than requirement of 1.84 KL. | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122837 | Closed | SHARMA SURAJ | 2026-07-06 | AFFF - 11 KL, AR-AFFF – 3.7 KL are available. | 2.9 | Foam inventory verified | 1797 | GULBARGA NEW IRD | 1 kl AR AFFF is needed in case of UG tanks, location to access AR AFFF requirement | SOD | Marketing | SWZ | 2026-03-15 | POOR PLANNING OR RISK ASSESSMENT | 9 | PROCESS SAFETY | S3 | F3 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122837 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122837 | 2026-08-19 18:00 | 61.0038 | 308 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122837 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122837 | AUD-2026-03-2000010764ACN-2026-03-4000122837 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 44
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143111 | Open | G SADASIVAN | 2026-07-06 | 1. Met DRM on 3-6-26 and emphasised on the need to sort the land ownership as well as area for which railway lease rental to be paid dispute at the earliest. 2. Dip Elimination is pending. | 1.3 | Pending issues reviewed | 1777 | Hassan Terminal | 1. Already Hassan Railways have requested District Administration to appoint surveyors for carrying out comprehensive survey. Can expect a result within a month's time. To be completed by JUly 26. 2. Process already started and File Note will be processed by 15-07-26 | SOD | Marketing | SWZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-07-2000014942ACN-2026-07-4000143111 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143111 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143111 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143111 |  | AUD-2026-07-2000014942ACN-2026-07-4000143111 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143112 | Open | G SADASIVAN | 2026-07-06 | In Feb 2026 visit by RNR, 19 recommendations were made | 1.4 | Earlier action points status checked | 1777 | Hassan Terminal | 5 out of 19 complied. EDC: 31.8.2026 | SOD | Marketing | SWZ | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143112 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143112 | 2026-09-22 17:00 | 27.0455 | 364 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143112 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000014942ACN-2026-07-4000143112 |  | AUD-2026-07-2000014942ACN-2026-07-4000143112 | 21 |  | 27 | 80 | 1 | 2 | 52
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143121 | Open | G SADASIVAN | 2026-07-06 | Location needs to have one security guard with HVD | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1777 | Hassan Terminal | Location to get few persons trained and aid them to take HVD & HAZ license | SOD | Marketing | SWZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-07-2000014942ACN-2026-07-4000143121 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143121 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143121 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143121 |  | AUD-2026-07-2000014942ACN-2026-07-4000143121 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143132 | Open | G SADASIVAN | 2026-07-06 | All points of OISD audit are complied, pending MDSA/SSA points to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1777 | Hassan Terminal | To be complied at the earliest | SOD | Marketing | SWZ | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-07-2000014942ACN-2026-07-4000143132 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143132 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143132 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143132 |  | AUD-2026-07-2000014942ACN-2026-07-4000143132 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143133 | Open | G SADASIVAN | 2026-07-06 | 1. Patch painting work to be carried out for foam marks on TK-201,202,102 2. Survey to be carried out for ensuring flameproofness of all JBs 3. Double valves to be provided for strainers of TT gantry | 4.1 | Full Field round completed. | 1777 | Hassan Terminal | 1. Patch painting work to be carried out for foam marks on TK-201,202,102 2. Survey to be carried out for ensuring flameproofness of all JBs 3. Double valves to be provided for strainers of TT gantry | SOD | Marketing | SWZ | 2026-08-31 |  | 9 |  | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143133 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143133 | 2026-09-22 17:00 | 27.0455 | 364 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143133 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143133 |  | AUD-2026-07-2000014942ACN-2026-07-4000143133 | 21 |  | 27 | 80 | 1 | 2 | 52
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143135 | Open | G SADASIVAN | 2026-07-06 | Few lots were hetting disposed off. | 4.5 | Making Location Scrap Free | 1777 | Hassan Terminal | To make location scrap free by 30.09.2026. Monthly progress to be updated to Zone | SOD | Marketing | SWZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-07-2000014942ACN-2026-07-4000143135 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143135 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143135 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143135 |  | AUD-2026-07-2000014942ACN-2026-07-4000143135 | 21 |  | 27 | 80 | 1 | 2 | 57
|  |  |  | Pending | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 5.3 POST-VISIT-REPORTING | ACN-2026-07-4000143136 | Open | G SADASIVAN | 2026-07-06 | Hazard Validity, W&M and TT Gantry Bay calibration details to be updated in LIC cabin | 5.3 | Updation of various statutory renewal dates in formation in LIC cabin | 1777 | Hassan Terminal | To be done timely | SOD | Marketing | SWZ | 2026-08-31 |  | 9 |  | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143136 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143136 | 2026-09-22 17:00 | 27.0455 | 364 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143136 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000014942ACN-2026-07-4000143136 |  | AUD-2026-07-2000014942ACN-2026-07-4000143136 | 21 |  | 27 | 80 | 1 | 2 | 52
SUJEET KUMAR | 2026-07-06 | SAXENA UMESH CHANDRA | 2026-07-06 | The visual indicators installed near TK-2 are available and functional for HCD operations. While the effectiveness of visual indications may be reduced during daylight conditions, audible hooters with adequate sound levels are provided and are in line with the standard practice followed across POL depots. Additionally, HCD system at the TWD Pump House has been restored and is fully functional. Accordingly, the audit observation has been complied with. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000135379 | Closed | SAXENA UMESH CHANDRA | 2026-07-06 | Checked and found in working condition. Visual near TK-2 to be replaced. HCD in TWD P/H was not working to be checked and rectified. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1457 | INDORE DEPOT | Visual near TK-2 to be replaced. HCD in TWD Pump House was not working. This need to be checked and rectified. | SOD | Marketing | CEN | 2026-06-09 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S1 | F2 | 2026-06-09 | AUD-2026-06-2000012547ACN-2026-06-4000135379 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135379 | 2026-09-09 19:00 | 39.9622 | 308 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135379 | 532 | 8294 | 21 | 8294 | 132 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135379 | AUD-2026-06-2000012547ACN-2026-06-4000135379 | 21 | 21 | 27 | 80 | 0 | -3 | 41 | 44
[5 empty] | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143497 | Open |  |  | Structural painting in the tank farm area is observed to be deteriorated at various locations and should be undertaken to prevent corrosion and maintain asset integrity. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Undertake structural painting in the tank farm area on priority to arrest corrosion, improve asset condition, and maintain long-term structural integrity. | SOD | Marketing | NCR | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143497 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143497 | 2026-09-03 | 46.7538 | 363 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143497 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143497 |  | AUD-2026-06-2000013451ACN-2026-07-4000143497 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143499 | Open |  |  | The painting of the Railway Siding hydrant line is found to be faded/deteriorated at various locations. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Repaint the Railway Siding hydrant line as per the approved colour-coding scheme to ensure clear identification, regulatory compliance, and ease of maintenance. | SOD | Marketing | NCR | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143499 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143499 | 2026-09-03 | 46.7538 | 363 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143499 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143499 |  | AUD-2026-06-2000013451ACN-2026-07-4000143499 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143501 | Open |  |  | 1. Solar Project which was for FY 2025-26, is under progress. Initial End date was 31.03.2026, however extension is taken till 30.06.2026 2. TAS revamping activity is under progrtess and end date is 31.12.2026 3. Project work related to MDSA compliance is underprogress and end date is 30.06.2026 4. LPR for Multi Function Printer initiated and progress is reviewed | 4.3 | Project progress reviewed | 1292 | LUCKNOW DEPOT | 1. Expedite the completion of the Solar Project and ensure its commissioning within the approved extended timeline of 30.06.2026. Progress shall be closely monitored to avoid any further delays. 2. Ensure timely execution of the TAS Revamping Project and periodically review progress to achieve completion by the scheduled target date of 31.12.2026. 3. Closely monitor and expedite the projectactivities related to MDSA compliance to ensure completion within the stipulated timeline of 30.06.2026. 4. Continue regular follow-up and monitoring of the LPR for procurement of the Multi-Function Printer to ensure its timely approval and deployment. | SOD | Marketing | NCR | 2026-08-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143501 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143501 | 2026-09-03 | 46.7538 | 363 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143501 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143501 |  | AUD-2026-06-2000013451ACN-2026-07-4000143501 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143502 | Open |  |  | Various scrap items were observed lying in the Scrap Yard. Necessary RFDs shall be initiated and processed in accordance with the prescribed procedure to ensure timely disposal and proper housekeeping. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1292 | LUCKNOW DEPOT | Necessary RFDs shall be initiated and pursued for the disposal of scrap materials lying in the Scrap Yard in accordance with the prescribed procedures, so as to ensure timely disposal, optimize space utilization, and maintain good housekeeping standards. | SOD | Marketing | NCR | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143502 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143502 | 2026-09-03 | 46.7538 | 363 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143502 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143502 |  | AUD-2026-06-2000013451ACN-2026-07-4000143502 | 21 |  | 27 | 80 | 0 | 0 | 52
DINESH KUMAR | 2026-07-07 |  |  | Single with three side lighting provided for achiveing Lux levels in UG Tank farm UG 17,18,16 | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129951 | Closed | DINESH KUMAR | 2026-07-07 | Lux level checked at TT Gantry & Pump House, found in order. Lux level to be improved near ethanol UG tank area UG16,17 and UG18 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1254 | JALANDHAR DEPOT | Location to improve lux level near ethanol UG tank area UG16,17 and UG18 | SOD | Marketing | NFZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000011851ACN-2026-05-4000129951 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129951 | 2026-08-21 | 59.7538 | 309 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129951 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129951 | AUD-2026-05-2000011851ACN-2026-05-4000129951 | 21 | 21 | 27 | 80 | 0 | -21 | 44 | 45
VED PRAKASH | 2026-07-07 | DAS DARSHAN | 2026-07-06 | 3. Location has checked HCD with working 20% LEL found working satisfactory. 6. Leak has been arrested from gland of jockey pump no 1. 7. Audio alarm volume of dyke drain in field has been rectified and found satisfactory. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122653 | Closed | DAS DARSHAN | 2026-07-06 | 1. Testing of HVLR no . 4. HVLR performed satisfactorily 2. RSFPS of TK06: operated locally from roof control panel by Officer Sh.Tanmay joined in Jan'26. Module was discharged to pressure 14 KG/Cm2. Discharge was successful. 3. Testing of HCD of Pump house Open Path (Tested by Ms. Neha): Performed satisfactory with 40% LEL. Location to further check with working with 20% LEL. TK31 point type HCD checked and found working satisfactory. 4. Testing of ESD: Operated ESD no 10 Security cabin during mock drill: Performed successfully. 5. Testing carried of foam pourer of tank no 5,4 and TK2: Performed satisfactorily 6. Fire engine operational. Leak from gland observed from one of the jockey pump. 7. Dyke valve TK31 checked. Video alarm found working satisfactory and audio alarm volume found low. 8. Testing of MEFG of TK31 carried out and found satisfactory. 9. Sprinkler system of TK 6 & 7 found performing satisfactorily. 10. Fire break valves of TK6/5 and TK5/4 checked and found good. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011009ACN-2026-03-4000122653 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122653 | 2026-09-03 | 46.7538 | 309 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122653 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122653 | AUD-2026-03-2000011009ACN-2026-03-4000122653 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
VED PRAKASH | 2026-07-07 | DAS DARSHAN | 2026-07-06 | Temporary contractor material shed made near boundary wall has been modified and shifted. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122661 | Closed | DAS DARSHAN | 2026-07-06 | EP no 267 checked and found satisfactory. Boundary condition is satisfactory except paint peel off at few sections. Location to remove temporary contractor material shed made near boundary wall. Vegetation control is satisfactory. | 3.16 | Earth pits / boundary / vegetation control checked | 1292 | LUCKNOW DEPOT | Corrective action to be taken. | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122661 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122661 | 2026-09-03 | 46.7538 | 309 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122661 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122661 | AUD-2026-03-2000011009ACN-2026-03-4000122661 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Noted and trainings being imparted accordingly | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139161 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Interected with all officers posted in Depot.As informed Subal Ch Das,Manager-Opns. having medical problem.Job has been assigned accordingly.3 officers are joined in last year. | 1.1 | Interaction with officers (1–1.5 hrs) | 1677 | GUWAHATI DEPOT | All New officers to be given exposure in all operating area in rotation and to be trained to handle all operations. | SOD | Marketing | GZR | 2026-07-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013067ACN-2026-06-4000139161 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139161 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139161 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139161 | AUD-2026-06-2000013067ACN-2026-06-4000139161 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Compliance activities are being done in time bound manner. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139162 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Review of major KPIs including operational performance, cost leadership,scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1677 | GUWAHATI DEPOT | Improvement on cycle time,findout avenues for cost leadership particularly regular expenditure in M&I and inhouse capability building,Good progress made for Disposal of Scrap last year.Disposal of balalnce Scrap making Scrap free location,Completion of inspectionMajor equipments and compliances in time bound manner. | SOD | Marketing | GZR | 2026-09-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013067ACN-2026-06-4000139162 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139162 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139162 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139162 | AUD-2026-06-2000013067ACN-2026-06-4000139162 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Details shared with jon in 1st week of July 2026 | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139163 | Closed | BHUYAN PRARTHANA | 2026-07-07 | PCSA for TK-11 - and commissioning is pending due to pending safety equipments compliances and ROSOV,MOV and HCD integration pending as intimated by location. For OISD compliance for few items fund is required. | 1.3 | Pending issues reviewed | 1677 | GUWAHATI DEPOT | Location to share with full details of requirement item wise and budget requirement immediately with Zone to take up with HQO.Arrangement to be done for call for PCSA.Detailed requirement for pending compliance of OISD to be communicated to zone with Target date. | SOD | Marketing | GZR | 2027-03-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013067ACN-2026-06-4000139163 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139163 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139163 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139163 | AUD-2026-06-2000013067ACN-2026-06-4000139163 | 21 | 21 | 27 | 80 | 5 | 5 | 83 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Earlier all points complied for Senior management inspection | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139164 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Status Checked and 12 points pending,details attached. | 1.4 | Earlier action points status checked | 1677 | GUWAHATI DEPOT | Balalnce pending points to comply in Time bound manner. | SOD | Marketing | GZR | 2026-06-20 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-20 | AUD-2026-06-2000013067ACN-2026-06-4000139164 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139164 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139164 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139164 | AUD-2026-06-2000013067ACN-2026-06-4000139164 | 21 | 21 | 27 | 80 | 5 | 5 | 42 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Budget request is shared with Zone on 5th July 2026 | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139165 | Closed | BHUYAN PRARTHANA | 2026-07-07 | MEB budget in M&R CE needs to be reviewed. for OISD compliance and other M&I complrehensive Audit compliances Budget review required. | 1.5 | HQO / Zonal support required identified | 1677 | GUWAHATI DEPOT | Location to share detailed requirement and Budget estimate immediately. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139165 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139165 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139165 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139165 | AUD-2026-06-2000013067ACN-2026-06-4000139165 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | All necessary checks and system updation done on regular basis . | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139166 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Improvement plan and upkeep of the locations along with future infrustucture plan discussed.All equipments needs to be kept in running condition always. | 1.8 | Improvement plans discussed | 1677 | GUWAHATI DEPOT | All necessary checks and system updation to be done on regular basis . | SOD | Marketing | GZR | 2026-06-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139166 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139166 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139166 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139166 | AUD-2026-06-2000013067ACN-2026-06-4000139166 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Training imparted on 02.07.2026 | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139167 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Single Contingency complied Location.Checked Fire engine operations,HVLR,Sprinkler and MEFG operations operated by security,Safety and M&R officer. | 2.2 | Double contingency scenario simulated; observations recorded | 1677 | GUWAHATI DEPOT | All new officers are to be trained on handling of safety equipments. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139167 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139167 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139167 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139167 | AUD-2026-06-2000013067ACN-2026-06-4000139167 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Training imparted on 02.07.2026 | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139168 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Checked ESD at Gantry and its operations found Ok. | 2.5 | Emergency response preparedness reviewed | 1677 | GUWAHATI DEPOT | All new officers to be trained on Emergency protocol. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139168 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139168 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139168 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139168 | AUD-2026-06-2000013067ACN-2026-06-4000139168 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Training is conducted for freshly joined officer on 2nd July 2026 | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139170 | Closed | BHUYAN PRARTHANA | 2026-07-07 | FE No-1 tested and operated by M&R officer. MEFG of MS Tank Farm tested and operated by Safety officer. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1677 | GUWAHATI DEPOT | Advised to conduct training session for all New officers alongwith workman for operation of the fire Engine/other safety equipmentson regular interval. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139170 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139170 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139170 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139170 | AUD-2026-06-2000013067ACN-2026-06-4000139170 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Same is being done on regular basis based on VTS and Novex data and inputs from stakeholders | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139172 | Closed | BHUYAN PRARTHANA | 2026-07-07 | VTS deviation are done on regular basis from zone. Location is taking action on VTS deviation basis alerts in NOVEX. | 3.3 | VTS deviations reviewed | 1677 | GUWAHATI DEPOT | Secodary route creation to be completed as per applicability.Repeated deviations are to be alanysed properly and for corrective action. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139172 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139172 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139172 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139172 | AUD-2026-06-2000013067ACN-2026-06-4000139172 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Monthly reconcilation is being ensured in time bound manner. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139174 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Monthly reconcialltion checked and is ok | 3.10 | TFMS/SAP reconciliation checked | 1677 | GUWAHATI DEPOT | Officer advised to do daily reconciallation | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139174 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139174 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139174 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139174 | AUD-2026-06-2000013067ACN-2026-06-4000139174 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | Training to Security/Workman strenthen on use of Various PPEs. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139175 | Closed | BHUYAN PRARTHANA | 2026-07-07 | Housekeeping is ok.However on regular basis grass cutting to be done near UG Tank farm area.PPE usage are ensured. | 3.15 | Housekeeping & PPE usage checked | 1677 | GUWAHATI DEPOT | Training to Security/Workman to be strenthen on use of Various PPEs. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139175 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139175 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139175 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139175 | AUD-2026-06-2000013067ACN-2026-06-4000139175 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
TAPAS RANJAN PANDA | 2026-07-07 | BHUYAN PRARTHANA | 2026-07-07 | List of critical equipment maintained in history card file. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000139178 | Closed | BHUYAN PRARTHANA | 2026-07-07 | AMCs are valid.Critical equipment list not available. | 4.2 | Maintenance activities reviewed. | 1677 | GUWAHATI DEPOT | List of critical equipment needs to be maintained. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139178 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139178 | 2026-09-01 | 48.7538 | 309 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139178 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139178 | AUD-2026-06-2000013067ACN-2026-06-4000139178 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 45
[5 empty] | LOCATION VISIT-BATHINDA_18.06.26 | 2026-06-19 | AUD-2026-07-2000015240 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142892 | Open |  |  | Additional TTs to be inducted. Differential payment to be given to transporters. | 1.3 | Pending issues reviewed | 1164 | BHATINDA TERMINAL | Location to coordinate with Zonal Transportation for expediting the jobs. | SOD | Marketing | NFZ | 2026-07-31 |  | 12 |  | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015240ACN-2026-07-4000142892 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015240ACN-2026-07-4000142892 | 2026-09-28 19:00 | 20.9622 | 333 | >20 | AUD-2026-07-2000015240 - ACN-2026-07-4000142892 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015240ACN-2026-07-4000142892 |  | AUD-2026-07-2000015240ACN-2026-07-4000142892 | 21 |  | 27 | 80 | 1 | -2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142671 | Open |  |  | Ensure updation of E diary observations daily 5 nos in portal | 1.3 | Pending issues reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Ensure updation of E diary observations daily 5 nos in portal | SOD | Marketing | SCR | 2026-06-25 |  | 5 |  | S1 | F5 | 2026-06-25 | AUD-2026-07-2000015701ACN-2026-07-4000142671 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142671 | 2026-09-17 20:00 | 31.9205 | 297 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142671 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142671 |  | AUD-2026-07-2000015701ACN-2026-07-4000142671 | 21 |  | 27 | 80 | 3 | 2 | 43
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142672 | Open |  |  | Complied 16/22 action points of previous Senior Management Inspection observations. | 1.4 | Earlier action points status checked | 1992 | VISAKH WHITE OIL TERMINAL | to Comply the pending observations in time bound manner within target dates | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-07-2000015701ACN-2026-07-4000142672 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142672 | 2026-09-17 20:00 | 31.9205 | 394 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142672 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142672 |  | AUD-2026-07-2000015701ACN-2026-07-4000142672 | 21 |  | 27 | 80 | 3 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142673 | Open |  |  | Ensure updation of TT crew data and approval by June end | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Ensure updation of TT crew data and approval by June end | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142673 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142673 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142673 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142673 |  | AUD-2026-07-2000015701ACN-2026-07-4000142673 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142674 | Open |  |  | Action to be taken for NRD TT in line with ITDG guildelines Chalk out plan for improving CO TT trips per day to 3 | 1.8 | Improvement plans discussed | 1992 | VISAKH WHITE OIL TERMINAL | Action to be taken for NRD TT in line with ITDG guildelines Chalk out plan for improving CO TT trips per day to 3 | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015701ACN-2026-07-4000142674 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142674 | 2026-09-17 20:00 | 31.9205 | 333 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142674 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142674 |  | AUD-2026-07-2000015701ACN-2026-07-4000142674 | 21 |  | 27 | 80 | 3 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142675 | Open |  |  | Mock Drill conducted on 05.06.2026 with Double contingency scenario. Mock Drill Observations for improvement i) In Scenario-1, it is recommended to remove shoes & helmet, to ensure the victim's comfort before transportation to the OHC. ii) n Scenario-2, the CO₂ fire extinguisher should be placed in a horizontal position until it is inspected and recharged. | 2.2 | Double contingency scenario simulated; observations recorded | 1992 | VISAKH WHITE OIL TERMINAL | The compliance of observations mentioned to be ensured in future mock drills. | SOD | Marketing | SCR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142675 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142675 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142675 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142675 |  | AUD-2026-07-2000015701ACN-2026-07-4000142675 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142676 | Open |  |  | LUX level observed: TTP - 25, TTG -120 (Bay 14), 33 (Bay 13), TK103 MOV-165, TK403 MOV - 89, Secondary road Dyke 1&4 - 8.3, PPH - 39/180/17, FWPH - 90/125 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1992 | VISAKH WHITE OIL TERMINAL | 2 lights not working in PPH, 1 light not working TTG Bay 13. To be rectified | SOD | Marketing | SCR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142676 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142676 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142676 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142676 |  | AUD-2026-07-2000015701ACN-2026-07-4000142676 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142677 | Open |  |  | Emergency response preparedness checked RIM Seal, HVLR , MEFG operated by location officers, Emergency Trolley checked. Emergency Gate hooter is coming at Visitor gate, however no local hooter at the gate is available. Also, possibility of TAS integration to be explored. | 2.5 | Emergency response preparedness reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Emergency Trolley items to be made available in slots as per displayed name plate - Medical kit, Electrical tester, SCABA set & Oxygen Cylinder etc. Requirement of local hooter at the emergency gate to be checked. | SOD | Marketing | SCR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-07-2000015701ACN-2026-07-4000142677 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142677 | 2026-09-17 20:00 | 31.9205 | 317 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142677 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142677 |  | AUD-2026-07-2000015701ACN-2026-07-4000142677 | 21 |  | 27 | 80 | 3 | 2 | 46
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142678 | Open |  |  | All 86 cameras are working, however 2 cameras - Main Gate IN OUT & Licensed Entry Gate view adjustment is required. Trimming of tree branches near boundary is required obstructing complete view of Camera TWG BS Perim Fxd 08 | 2.6 | CCTV functioning checked | 1992 | VISAKH WHITE OIL TERMINAL | Corrective action to be taken for CCTV nos mentioned in observation. | SOD | Marketing | SCR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-07-2000015701ACN-2026-07-4000142678 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142678 | 2026-09-17 20:00 | 31.9205 | 317 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142678 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142678 |  | AUD-2026-07-2000015701ACN-2026-07-4000142678 | 21 |  | 27 | 80 | 3 | 2 | 46
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142679 | Open |  |  | Functionality checked HVLR 3 for TK 205 & TK206, Rim Seal of TK 206, MEFG of TK 206, HCD of MS 011 Pump & Ethanol 061A pump, found ok. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1992 | VISAKH WHITE OIL TERMINAL | Pressure Transmitters, Pressure guages, Temp Transmitter, TSV Calibration pending. Last due since Feb'26. Tender floated with due date 26/06/2026. Callibration activity to be expedited. | SOD | Marketing | SCR | 2026-08-30 |  | 8 |  | S2 | F4 | 2026-08-30 | AUD-2026-07-2000015701ACN-2026-07-4000142679 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142679 | 2026-09-17 20:00 | 31.9205 | 363 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142679 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142679 |  | AUD-2026-07-2000015701ACN-2026-07-4000142679 | 21 |  | 27 | 80 | 3 | 2 | 52
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142680 | Open |  |  | Tank 101 and Tank 206 Physical dip checked. i) TK 101 physical dip 851 cm vs TAS dip of 851.2 cm; Temperature physical reading 39.5C vs TAS reading 38.9 C; and water dip of 3.6 cm vs TAS water dip of 3.9 cm & Density 814.29 standard ii) TK 206 physical dip 1391.3 cm vs TAS dip of 1390.6 cm; Temperature physical reading 35.5 C vs TAS reading 35.4 C; and water dip of 4.4 cm vs TAS water dip of 3.8 cm & Density 736.4 Ambient, 754.6 Standard | 3.7 | Inventory physical dip of minimum two tanks taken | 1992 | VISAKH WHITE OIL TERMINAL | Location to take up with TAS vendor for corrective action | SOD | Marketing | SCR | 2026-07-31 |  | 5 |  | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015701ACN-2026-07-4000142680 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142680 | 2026-09-17 20:00 | 31.9205 | 333 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142680 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142680 |  | AUD-2026-07-2000015701ACN-2026-07-4000142680 | 21 |  | 27 | 80 | 3 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142681 | Open |  |  | Critical alarms were reviewed. | 3.12 | Critical alarms checked & corrective actions reviewed | 1992 | VISAKH WHITE OIL TERMINAL | All critical alarms to be checked , root cause to be analysed , recorded before closing the alerts. | SOD | Marketing | SCR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142681 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142681 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142681 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142681 |  | AUD-2026-07-2000015701ACN-2026-07-4000142681 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-07-4000142682 | Open |  |  | Full field round completed (gantry/tank farm/Solar/product pump house/siding/control room/Fire Pump House/security/admin) | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1992 | VISAKH WHITE OIL TERMINAL | Bags checking to be done before DFMD, hand frisking not done | SOD | Marketing | SCR | 2026-06-20 |  | 8 |  | S2 | F4 | 2026-06-20 | AUD-2026-07-2000015701ACN-2026-07-4000142682 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142682 | 2026-09-17 20:00 | 31.9205 | 292 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142682 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142682 |  | AUD-2026-07-2000015701ACN-2026-07-4000142682 | 21 |  | 27 | 80 | 3 | 2 | 42
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-07-4000142683 | Open |  |  | Fire Engine Sequence checked - S2, 2B, 3C, A, S1 | 4.2 | Maintenance activities reviewed | 1992 | VISAKH WHITE OIL TERMINAL | FE 2B - DP observed 25 bar against 10-11 bar, FE 3C - CWP 0.5 bar against 1-2 bar, Mechanical seal issue observed in FE A | SOD | Marketing | SCR | 2026-07-31 |  | 8 |  | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015701ACN-2026-07-4000142683 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142683 | 2026-09-17 20:00 | 31.9205 | 333 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142683 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142683 |  | AUD-2026-07-2000015701ACN-2026-07-4000142683 | 21 |  | 27 | 80 | 3 | 2 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-07-4000142684 | Open |  |  | Projects 1) MOV with actuator at Jetty 2) Full Bore Valve to be completed & closed by June 26 | 4.3 | Project progress reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Projects 1) MOV with actuator at Jetty 2) Full Bore Valve to be completed & closed by June 26 | SOD | Marketing | SCR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142684 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142684 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142684 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015701ACN-2026-07-4000142684 |  | AUD-2026-07-2000015701ACN-2026-07-4000142684 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-07-4000142685 | Open |  |  | Cut pieces of plates , pipes lying in scrap yard | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1992 | VISAKH WHITE OIL TERMINAL | Scrap to be liquidated. RFDs to be initiated on priority | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015701ACN-2026-07-4000142685 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142685 | 2026-09-17 20:00 | 31.9205 | 394 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142685 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142685 |  | AUD-2026-07-2000015701ACN-2026-07-4000142685 | 21 |  | 27 | 80 | 3 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142686 | Open |  |  | Following corrections to be made in monthly MIS reporting : Average TT filling time, Average TT/Bay in 2 hrs, Online Density Performance of MS/HSD TTs only to be considered | 6.1 |  | 1992 | VISAKH WHITE OIL TERMINAL | Following corrections to be made in monthly MIS reporting : Average TT filling time, Average TT/Bay in 2 hrs, Online Density Performance of MS/HSD TTs only to be considered | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142686 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142686 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142686 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142686 |  | AUD-2026-07-2000015701ACN-2026-07-4000142686 | 21 |  | 27 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-19 14:30 | AUD-2026-07-2000015701 | 2026-06-18 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142687 | Open |  |  | LOTO register not updated | 6.2 |  | 1992 | VISAKH WHITE OIL TERMINAL | Location to ensure regular Updating of the LOTO register | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015701ACN-2026-07-4000142687 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015701ACN-2026-07-4000142687 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-07-2000015701 - ACN-2026-07-4000142687 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015701ACN-2026-07-4000142687 |  | AUD-2026-07-2000015701ACN-2026-07-4000142687 | 21 |  | 27 | 80 | 3 | 2 | 44
CHOPPA SANTHOSH KUMAR | 2026-07-07 | HUSSAIN BANOTHU | 2026-07-07 | Open irregularity is closed in cordination with HQO | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128217 | Closed | HUSSAIN BANOTHU | 2026-07-07 | Pending Issues reviewed. Irregularity pertaining TT accident submitted for closure . | 1.3 | Pending issues reviewed | 1937 | SURYAPET TERMINAL | To follow up and close the Open irregularity Land Mutation issue to be taken up with concerned authorities. MDSA pending points to be closed. | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128217 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128217 | 2026-08-04 18:45 | 75.9726 | 309 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128217 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128217 | AUD-2026-04-2000011400ACN-2026-04-4000128217 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 45
CHOPPA SANTHOSH KUMAR | 2026-07-07 | HUSSAIN BANOTHU | 2026-07-07 | 1. Camera angles near the pipeline area and lube warehouse need adjustment for improved supervision and visibility. 2. Camera clarity near FLM-8, TK-2B, and TK-1C is inadequate; corrective action to be taken. 3. Solar panel cleaning is being carried out fortnightly (last cleaned on 20-01-2026 using SolarOkare). Cleaning and inspection records to be maintained, and performance improvements to be analysed and documented. 4. Emergency exit signboards and floor stickers are provided in the conference room. 5. Disposal completed 6. Re conditioning of Earth pit activity for all earth pits in in progress. 7. Missing electrical hand gloves purchased and kept in Fire emergency trolley. All the items are placed in designated shelves and the details of items as per OISD 244 is attached. 8. Correspondence to be initiated with AST and zonal TAS for rectification and preventionof recurrence. 9. 400 KW solar project successfully commissioned. 10. A phased action plan to be prepared for releasing trucks for bottom-loading conversion. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123652 | Closed | HUSSAIN BANOTHU | 2026-07-07 | A Complete round of the Terminal was taken including Gantry, Tank Farm, Pump House, Conrol room, Scrap Area, Security and Admin. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1937 | SURYAPET TERMINAL | 1. Camera angles near the pipeline area and lube warehouse need adjustment for improved supervision and visibility. 2. Camera clarity near FLM-8, TK-2B, and TK-1C is inadequate; corrective action to be taken. 3. Solar panel cleaning is being carried out fortnightly (last cleaned on 20-01-2026 using SolarOkare). Cleaning and inspection records to be maintained, and performance improvements to be analysed and documented. 4. Emergency exit signboards and floor stickers to be provided in the conference room. 5. Immediate action to be taken for disposal of scrap material found in the scrap yard. 6. Gantry-2 structure earth pits (EP-224 & EP-225) showed varying resistance values. Earth resistance tester to be checked and reasons for variation to be identified. Earth pit readings tobe monitored frequently. 7. Items in the fire emergency trolley were found placed incorrectly. Non-sparking mechanical tool kit and electrical hand gloves were missing from the trolley and found in the safety store room. All designated items must be kept in the trolley and compliance ensured. 8. While checking control room reports, BCU K-factor was found populated erroneously for dates 11-12-2025 and 12-12-2025. Correspondence to be initiated with AST and zonal TAS for rectification and prevention of recurrence. 9. Action to be taken for early completion of the 400-kW solar project and bottom loading project. 10. A phased action plan to be prepared for releasing trucks for bottom-loading conversion. | SOD | Marketing | SCR | 2026-01-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123652 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123652 | 2026-08-04 18:45 | 75.9726 | 309 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123652 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123652 | AUD-2026-03-2000011061ACN-2026-03-4000123652 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 45
CHOPPA SANTHOSH KUMAR | 2026-07-07 | HUSSAIN BANOTHU | 2026-07-07 | All the items are kept in fire emegency trolley as per OISD-117 | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128222 | Closed | HUSSAIN BANOTHU | 2026-07-07 | Emergency response preparedness checked during fire drill. HVLRs , Foam Monitors , MEFGs , Tank Sprinklers operated by location officers, Emergency Trolley checked, Emergency exit gate checked. | 2.5 | Emergency response preparedness reviewed | 1937 | SURYAPET TERMINAL | Emergency Trolley items are not as per name plate. Some of the items viz FLP Search Lights are missing . To take corrective action for emergency trolley availability with all the required items. | SOD | Marketing | SCR | 2026-04-21 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-04-21 | AUD-2026-04-2000011400ACN-2026-04-4000128222 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128222 | 2026-08-04 18:45 | 75.9726 | 309 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128222 | 532 | 8294 | 21 | 8294 | 181 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128222 | AUD-2026-04-2000011400ACN-2026-04-4000128222 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 45
CHOPPA SANTHOSH KUMAR | 2026-07-07 | HUSSAIN BANOTHU | 2026-07-07 | i)Team wise training imparted to all contract workmens and security guards on fire fighting as oer Fire orgainisation chart ii) Tank 3A sprinkler ring holes repaired iii)All clear siren repaired and rectified v) regular monthly mockdrills are conducted and improved performance | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | REGULAR MONTHLY MOCKDRILLS ARE CONDUCTED | ACN-2026-04-4000128221 | Closed | HUSSAIN BANOTHU | 2026-07-07 | Fire drill with double contingency scenario conducted on 08.04.2026. Observations - Scenario 1 Roof Sinking and fire on tank 1A- i)Initially HVLR direction was pointed to Tank 1B instead of 1A ii) HVLR stopped when instruction was given to stop foam, delay in operating sprinklers of adjacent tanks , Sprinkler ring of Tank 3A leaking heaviliy form holes.iii) Casuality in Tank 1A was announcedbut Delay by rescue team in reaching site and initially rescue team going to Tank 1B instead of 1A, Delay in mobilizing Emergency trolley to site.iv) SCABA person LEL checking not done prior to rescue of casuality in dyke.v) SCABA person delayed and also rope wasshort and not wound properly.vi) All clear siren not proper vii) Scenario 2 - ETP pool fire - i) Fire hose operated from distance of 3.0 metres from pool fire ii) The stretcher used by rescue team of VVSPL was not propere and is not a standard one | 2.2 | Double contingency scenario simulated; observations recorded | 1937 | SURYAPET TERMINAL | 1. Communication needs to be improved among the teams ii) Tank 3A sprinkler ring holes to be repaired, iii)All clear siren to be rectified iv) Auxilliary team have to coordinate the safe removal of TTs from TT Gantry and direct them to the emergecy exit whereas resue team incharge was coordinating at TT gantry resulting in delay of rescue team to site. Short comings to be avoided by practicing the mock drills frequently. | SOD | Marketing | SCR | 2026-04-21 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-21 | AUD-2026-04-2000011400ACN-2026-04-4000128221 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128221 | 2026-08-04 18:45 | 75.9726 | 309 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128221 | 532 | 8294 | 21 | 8294 | 181 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128221 | AUD-2026-04-2000011400ACN-2026-04-4000128221 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 45
|  | CHANGMAI RAHUL | 2026-07-08 | 1. Pollution CTO renewed 2. Factory Lisence new operation online license received 3. PESO license renewed till 2030. Smaple room is temporary structure of Pota cabin where PESO license is not mandatory. Despite the drawing is ready and pESO amendment tobe applied. 4. Hazardous Waste applied and license received 5. ERDMP Certification Audit PO was provided to one TPIA and scheduled on 2nd April26 but party backed out. New PO placement process underway. 6. Mutual Aid Agreement printout kept at location now | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127072 | Completed | CHANGMAI RAHUL | 2026-07-08 | Yes pending issues reviewed and officer advised to take the needful early action. 1. CTO expired on 15.01.26 - It is given to undersand that the renewal application already made but there is no acknowledgeemnt available. 2. Factory Lisence expired on 31.12.25 - It is given to undersand that the renewal application already made but there is no acknowledgeemnt available. 3. PESO renewal with updated validity till 31.12.30 received on 08.01.26. However, even after 2 month, the amendment approval application not made. 4. Hazardous Waste handling Application Pending 5. ERDMP Certification Audit Pending 6. Mutual Aid Agreement not available at depot | 1.3 | Pending issues reviewed | 1708 | DIMAPUR DEPOT | Officer to take immediate needful corrective action on the points mentioned | SOD | Marketing | GZR | 2026-04-06 |  | 8 |  | S2 | F4 | 2026-04-06 | AUD-2026-03-2000010729ACN-2026-03-4000127072 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127072 | 2026-09-12 | 37.7538 | 217 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127072 | 532 | 8294 | 21 | 8294 | 196 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127072 |  | AUD-2026-03-2000010729ACN-2026-03-4000127072 | 21 |  | 26 | 80 | 7 | 7 | 31
|  | CHANGMAI RAHUL | 2026-07-08 | 1. Voltage fluctuation & irregular supply of electricity by SEB: After the replacement of the incoming cable with aluminium cables overhead. They supply voltage is ok. Sometimes in peak hours it drops which has been acknowledged by the Electricity department 2. All 27 CCTV down CCTV rectified by CCTV vendors during his visit from 8th to 12th June2026 3. Smoke Detector in Sample Room - Physical Installation completed, integration with TAS/ FAP is completed 4. VHF Procurement – VHF tender floated through CPO. As soon as budget is allotted procurement to be completed 5. Pipeline Qty. - FN approved and qty. updated in SAP. However, the pipeline qty. freezed in SAP 6. Water leakage observed in J/Pump suction line from blind flange & valve joints - Leakage arrested now. 7. Earth Pits Testing - It is given to understand that the testing completed. Few of the earthpit resistance found outside limit. Earth pit maintenance is done by putting industrial salt and water and removing the rust from the strips. 8. FLP Phone is non-functional: FLP phone is installed but EPABX machine is required to make it operational. Quotation sought from vendor for EPABX machine supply and installation. 9. Housekeeping in MCC room was not up to the mark and MCC room is unorganized.: No separate store room for keeping any old usable equipment or items. Now the non-functional equipment are shifted to scrapyard. 10. Own Use booking – Signed record hasbeen maintained for own use booking of HSD. 11. It was noted that hydrants, monitors, FF equipment are not being put to regular usage by weekly testing – Weekly record maintained. Installed WCFM is of min throw of 500 GPM [1893 LPM ]. Accordingly, min infeed flow required to maintain the sustained flow from WCFM is 115 KLPH which is not possible even with both the jockey pump running simultaneously. [18+18 KL/Hr.] This is Point 9.09 of OISD PCSA and not complied As per the MOM of the meeting held at HQO on 13-03-25 b/w SOD and E&P, as location is having a storage of 180 KL in 4 UG tanks, each of 45 KL, thus exempted for fire water requirement. However, as an additional measure, Fire Water Piping Network has been provided with pumping arrangement. 12. Nomination order on M/s IconControl – TAS manday PO 5200121749 dated 28/03/2026 is provided and executed for TAS activities at Dimapur Depot. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127073 | Completed | CHANGMAI RAHUL | 2026-07-08 | Yes reviewed : 1. Voltage fluctuation & irregular supply of electricity by SEB - It is given to understand that the application letter in this regard submitted but no acknowledgement available. 2. All 27 CCTV down - It is informed that needful coordination with vendor being done but no affirmative development. 3. Smoke Detector in Sample Room - Physical Installation completed, integration with TAS/ FAP is pending. 4. VHF Procurement - Fund not alloted yet. Approved LPR sent to GHRRO for tendering in Aug'25 but no further action taken till date. 5. Pipeline Qty. - FN approved and qty. updated in SAP. However, the pipeline qty. not freezed in SAP 6. Water leakage observed in J/Pump suction line from blind flange & valve joints - Leakage not arrested. 7. Earth Pits Testing - It is given to understand that the testing completed. Few of the earthpit resistance found outside limit. Corrective action to be taken. 8. FLP Phone is non functional 9. Housekeeping in MCC room was not up to the mark and MCC room is unorganized. 10. Own Use booking - Own use is being booked by officer on random basis. There is no signed register record for own use available at location. 11. It was noted that hydrants, monitors, FF equipment are not being put to regular usage by weekly testing - Depot failed toshow the records for the same. Upon physical operation of WCFM, it was found that 2 out of 4 WCFM is not at all throwing the water.Whereas, the flow of the other two WCFM is not reaching the TTG. 12. Nomination order on M/s Icon Control - It is given to understand that the order for rectification job for TAS system not yet completed in want of the the order. To be expedited | 1.4 | Earlier action points status checked | 1708 | DIMAPUR DEPOT | Officer to take immediate needful corrective action and coordinate with all concerned on the points mentioned | SOD | Marketing | GZR | 2026-04-10 |  | 10 |  | S2 | F5 | 2026-04-10 | AUD-2026-03-2000010729ACN-2026-03-4000127073 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127073 | 2026-09-12 | 37.7538 | 221 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127073 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127073 |  | AUD-2026-03-2000010729ACN-2026-03-4000127073 | 21 |  | 26 | 80 | 7 | 7 | 32
|  | CHANGMAI RAHUL | 2026-07-08 | ESD is integrated to TAS and is operational. WCFM:Installed WCFM is of min throw of 500 GPM [1893 LPM ]. Accordingly, min infeed flow required to maintain the sustained flow from WCFM is 115 KLPH which is not possible even with both the jockey pump running simultaneously. [18+18 KL/Hr.] This is Point 9.09 of OISD PCSA and not complied As per the MOM of the meeting held at HQO on 13-03-25 b/w SOD and E&P, as location is having a storage of 180 KL in 4 UG tanks, each of 45 KL, thus exempted for fire water requirement. However, as an additional measure, Fire Water Piping Network has been provided with pumping arrangement. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127075 | Completed | CHANGMAI RAHUL | 2026-07-08 | Fire drill carried out with the team. Water throw not adequate from 2 of the WCFM. The other two WCFM didn’t functioned well while operation. ESD is not operational. ESD has not been integrated with TAS | 2.1 | Fire drill conducted in last 6 months (surprise) | 1708 | DIMAPUR DEPOT | Officer is advised to have regualar fire drill and bridge the gaps identified. | SOD | Marketing | GZR | 2026-04-15 |  | 10 |  | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127075 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127075 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127075 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127075 |  | AUD-2026-03-2000010729ACN-2026-03-4000127075 | 21 |  | 26 | 80 | 7 | 7 | 33
|  | CHANGMAI RAHUL | 2026-07-08 | ESD is integrated to TAS and is operational. Fire Drill conducted every month now. WCFM:Installed WCFM is of min throw of 500 GPM [1893 LPM ]. Accordingly, min infeed flow required to maintain the sustained flow from WCFM is 115 KLPH which is not possible even with both the jockey pump running simultaneously. [18+18 KL/Hr.] This is Point 9.09 of OISD PCSA and not complied As per the MOM of the meeting held at HQO on 13-03-25 b/w SOD and E&P, as location is having a storage of 180 KL in 4 UG tanks, each of 45 KL, thus exempted for fire water requirement. However, as an additional measure, Fire Water Piping Network has been provided with pumpingarrangement. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127076 | Completed | CHANGMAI RAHUL | 2026-07-08 | Fire drill carried out with the team. Water throw not adequate from 2 of the WCFM. The other two WCFM didn’t functioned well while operation. ESD is not operational. ESD has not been integrated with TAS | 2.2 | Double contingency scenario simulated; observations recorded | 1708 | DIMAPUR DEPOT | Officer is advised to have regualar fire drill and bridge the gaps identified. | SOD | Marketing | GZR | 2026-04-15 |  | 10 |  | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127076 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127076 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127076 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127076 |  | AUD-2026-03-2000010729ACN-2026-03-4000127076 | 21 |  | 26 | 80 | 7 | 7 | 33
DEWADE SHAHAJI NAGORAO | 2026-07-08 | LAD SARTHAK DILIP | 2026-07-08 | Filter is changed in eye wash & body wash shower | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125730 | Closed | LAD SARTHAK DILIP | 2026-07-08 | Not enough flow for eye wash tap & body wash shower | 6.2 | Eye wash & body wash shower near ITT pump house | 1504 | MIRAJ TERMINAL | Filter to be changed in eye wash. Hand operated valve for body wash shower needs to be repaired | SOD | Marketing | WZ | 2026-04-07 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-07 | AUD-2026-03-2000010875ACN-2026-03-4000125730 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125730 | 2026-09-01 | 48.7538 | 310 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125730 | 532 | 8294 | 21 | 8294 | 195 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125730 | AUD-2026-03-2000010875ACN-2026-03-4000125730 | 21 | 21 | 26 | 80 | 0 | -1 | 32 | 45
DEWADE SHAHAJI NAGORAO | 2026-07-08 | LAD SARTHAK DILIP | 2026-07-08 | Leakage is stopped as a regular maintenance activity | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125732 | Closed | LAD SARTHAK DILIP | 2026-07-08 | HSD pumps in TLF pumps have slight leakage near NRV | 6.4 | HSD pumps in TLF pump house | 1504 | MIRAJ TERMINAL | Action to be taken to resist the leakage | SOD | Marketing | WZ | 2026-04-07 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-07 | AUD-2026-03-2000010875ACN-2026-03-4000125732 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125732 | 2026-09-01 | 48.7538 | 310 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125732 | 532 | 8294 | 21 | 8294 | 195 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125732 | AUD-2026-03-2000010875ACN-2026-03-4000125732 | 21 | 21 | 26 | 80 | 0 | -1 | 32 | 45
DEWADE SHAHAJI NAGORAO | 2026-07-08 | LAD SARTHAK DILIP | 2026-07-08 | Required items have been made available & list is displayed | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125736 | Closed | LAD SARTHAK DILIP | 2026-07-08 | Items list not available. Some items are missing as per names displayed. Upkeep of items available in trolley to be improved. | 6.8 | Emergency trolley | 1504 | MIRAJ TERMINAL | List of items required and available to be displayed. | SOD | Marketing | WZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010875ACN-2026-03-4000125736 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125736 | 2026-09-01 | 48.7538 | 310 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125736 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125736 | AUD-2026-03-2000010875ACN-2026-03-4000125736 | 21 | 21 | 26 | 80 | 0 | -1 | 35 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Surprise night inspections being done now and location shall ensure to carry out these on regular basis further. Report of inspection done attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000140176 | Closed | SINGH PREETI | 2026-06-27 | Surprise night inspection is not being done regularly by location. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140176 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140176 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140176 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140176 | AUD-2026-06-2000013929ACN-2026-06-4000140176 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Security guards and electricians in night shift being checked with breath analyzer. Records also being maintained. Attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140178 | Closed | SINGH PREETI | 2026-06-27 | Security guards and electricians in night shift to be checked with breath analyzer. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140178 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140178 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140178 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140178 | AUD-2026-06-2000013929ACN-2026-06-4000140178 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | CCTV Recordings being checked by Safety Officer/LIC and records also being maintained. Attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140180 | Closed | SINGH PREETI | 2026-06-27 | Total CCTV 42. Nil under breakdown. Back up available for 92 days. CCTV Records to be maintained by LIC/Safety officer. | 2.6 | CCTV functioning checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140180 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140180 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140180 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140180 | AUD-2026-06-2000013929ACN-2026-06-4000140180 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | TT fittings checked and corrective action taken. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140185 | Closed | SINGH PREETI | 2026-07-09 |  | 3.1 | TT fittings & discipline checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken in line with SOP and circular | SOD | Marketing | NWR | 2026-07-01 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140185 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140185 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140185 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140185 | AUD-2026-06-2000013929ACN-2026-06-4000140185 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | It shall be ensured without fail that all personnel wear the prescribed PPE on TT while Dip checking/sampling. The concerned personnel have been instructed strictly,and compliance shall be monitored regularly to prevent recurrence. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140189 | Closed | SINGH PREETI | 2026-07-09 | TT Harness not worn by TT gantry staff while taking out gasohol sample from top of TT. | 3.15 | Housekeeping & PPE usage checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140189 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140189 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140189 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140189 | AUD-2026-06-2000013929ACN-2026-06-4000140189 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | Current audit compliance is 98.72% for all audits, PM - MDSA Audit: 94.74%, PM - OISD- External Safety Audit:100%, PM - SAFE100 Self Safety Audit: 92.31%, PM - Security Inspection:100%, PM - Senior Management Inspection: 100%, PM - SOD TANK AG EFR: 100%, PM - SODTANKAG IFR: 100%, PM - SOD TANK UG: 100% We are ensuring now to attach supporting documents in all observations being closed in SAP. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140192 | Closed | SINGH PREETI | 2026-07-09 | As per SAP, audit compliance is 94% for all audits. PM - MDSA Audit: 93%, PM - OISD- External Safety Audit:100%, PM - SAFE100 Self Safety Audit: 92%, PM - Security Inspection:100%, PM - Senior Management Inspection: 0%, PM - SOD TANK AG EFR: 100%, PM - SOD TANKAG IFR: 100%, PM - SOD TANK UG: 100% Supporting document for audit observation closed in SAP are not attached by location | 3.18 | OISD/MDSA/SSA compliance reviewed | 1385 | PALANPUR TERMINAL | Observation scheduled for closure as of Jun'26 shall be closed. | SOD | Marketing | NWR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013929ACN-2026-06-4000140192 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140192 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140192 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140192 | AUD-2026-06-2000013929ACN-2026-06-4000140192 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | Location ensures to check dips of all TT Comp. post loading, records maintained at TT Gantry and also recorded in SAP. Any deviation found is promptly attended after TT calibration verification at Calibration and re-calibration is done if required. 5% TT checking in SAP ensured. TT Inspection% in SAP for Q1 for location is 5.17% | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140186 | Closed | SINGH PREETI | 2026-07-09 | 1. Bay no 2, GJ02AT5183 14 KL: Comp 1:Nil(HSD) Comp 2:Nil(HSD) Comp 3:Nil(HSD) 2.Bay no 3, GJ03BZ4446 20 KL: Comp 1: Nil(HSD) Comp2: 6(HSD - short) Comp 3:3mm (HSD - excess) Comp 4:Nil(HSD) 3. Bay no 4, GJ31T5862 14 KL: Comp 1: 3mm(MS - short), Comp 2: Nil(HSD)Comp 3: 3(HSD - excess) 4. Bay no 5, GJ02AT2900 14: Comp 1:Nil(HSD) Comp 2: 3(MS - excess) Comp 3: Nil(MS) 5. Bay no 8, GJ38TB0218 20 KL Comp 1: 3(MS - excess) Comp 2: Nil(HSD) Comp 3: Nil(HSD) Comp 4: 3(HSD - excess) 6. Bay no 12, GJ18BT6908 20 KL Comp 1: Nil(MS) Comp 2: 3(MS - short) Comp 3: (HSD - excess) Comp 4: Nil(HSD) | 3.2 | Post-loading dip checks verified | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140186 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140186 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140186 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140186 | AUD-2026-06-2000013929ACN-2026-06-4000140186 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Records being maintained now. Letters issued attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140187 | Closed | SINGH PREETI | 2026-06-27 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140187 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140187 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140187 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140187 | AUD-2026-06-2000013929ACN-2026-06-4000140187 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Water in portable eye wash being checked daily now. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140198 | Closed | SINGH PREETI | 2026-06-27 | Water in portable eye wash to be checked daily | 6.1 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140198 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140198 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140198 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140198 | AUD-2026-06-2000013929ACN-2026-06-4000140198 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | CCTV Camera for admin building provided now by shifting one of the existing CCTVs. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140807 | Closed | SINGH PREETI | 2026-06-27 | CCTV Camera for admin building to be provided by shifting one of the existing CCTVs | 6.10 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140807 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140807 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140807 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140807 | AUD-2026-06-2000013929ACN-2026-06-4000140807 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Daily day end MFM Reports made and being sent to zone now on daily basis. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140808 | Closed | SINGH PREETI | 2026-06-27 | Daily day end MFM records to be sent to zone. | 6.11 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140808 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140808 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140808 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140808 | AUD-2026-06-2000013929ACN-2026-06-4000140808 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Gland rope for Fire Engine 5 replaced, and water leakage issue has been resolved now. Fire engine working ok now. Permit attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140809 | Closed | SINGH PREETI | 2026-06-27 | Water leakage from Fire Engine FE-05 gland to be attended immediately | 6.12 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140809 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140809 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140809 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140809 | AUD-2026-06-2000013929ACN-2026-06-4000140809 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Trees near FE Shed trimmed. Photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140810 | Closed | SINGH PREETI | 2026-06-27 | Trees near FE Shed to be trimmed. | 6.13 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140810 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140810 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140810 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140810 | AUD-2026-06-2000013929ACN-2026-06-4000140810 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-07 | Emergency Contact nos. updated as per DPC. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140199 | Closed | SINGH PREETI | 2026-07-07 | Emergency contact nos. to be updated as per DPC | 6.2 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | OUTDATED OR COMPLEX SOPS | 1 | EMERGENCY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140199 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140199 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140199 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140199 | AUD-2026-06-2000013929ACN-2026-06-4000140199 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | Additive reconciliation being done monthly now. Signed monthly Reco attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140817 | Closed | SINGH PREETI | 2026-07-09 | Additive reconciliation to be done monthly. | 6.20 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140817 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140817 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140817 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140817 | AUD-2026-06-2000013929ACN-2026-06-4000140817 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-06-27 | Witnessing and cross verification of atleast 5% Earth Pit testing being ensured by officers now. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140818 | Closed | SINGH PREETI | 2026-06-27 | Cross verification of at least 5% earth pit testing to be done by officers. | 6.21 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140818 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140818 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140818 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140818 | AUD-2026-06-2000013929ACN-2026-06-4000140818 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-07 | Covers have been placed on all fire buckets now. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140804 | Closed | SINGH PREETI | 2026-07-07 | Fire bucket covers to be placed | 6.7 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | EMERGENCY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140804 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140804 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140804 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140804 | AUD-2026-06-2000013929ACN-2026-06-4000140804 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | Observations are being recorded in e-dairy by location now. Shall be ensured to record 5 obs. daily in e-diary and corrective action shall be taken for those. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140819 | Closed | SINGH PREETI | 2026-07-09 | Minimum 5 observations per day to be recorded in e-diary. | 6.22 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140819 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140819 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140819 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140819 | AUD-2026-06-2000013929ACN-2026-06-4000140819 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Fire Drill at ETP site conducted on 13.03.2026 | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122758 | Closed | ANAND RUPAK | 2026-07-06 | All fire drills are surprise mock drills | 2.1 | Fire drill conducted in last 6 months (surprise) | 1775 | BENGALURU TERMINAL | Firedrill in ETP to be conducted | SOD | Marketing | SWZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | EMERGENCY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122758 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122758 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122758 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122758 | AUD-2026-03-2000010965ACN-2026-03-4000122758 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Complied | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122759 | Closed | ANAND RUPAK | 2026-07-06 | Reviewed during visit; found satisfactory. Made suggestions for additional Fire monitor near the fabrication shed. | 2.5 | Emergency response preparedness reviewed | 1775 | BENGALURU TERMINAL | 1. One Fire Monitor/ Double Hydrant to be provided 15 m away from the Fabrication shed. | SOD | Marketing | SWZ | 2026-05-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S2 | F1 | 2026-05-31 | AUD-2026-03-2000010965ACN-2026-03-4000122759 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122759 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122759 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122759 | AUD-2026-03-2000010965ACN-2026-03-4000122759 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Blacklisting done for the entire fleet of M/s Kalika Liquid Carrier vide letter dt 17.04.2026. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122760 | Closed | ANAND RUPAK | 2026-07-06 | Checked EM locks using intelligent key for TTs KA53AC9899, KA53AA9671, KA40B3092, KA53AA9043, KA01AL3618 and found to be ok. Noted that One truck TT NO. WB11E8498 was found with Baby compartment ON 19.01.2026 by Location and action taken inline with TDG and Legalmetrology Rules. | 3.1 | TT fittings & discipline checked | 1775 | BENGALURU TERMINAL | Improvement to be brought in Tyre condition by continously checking and counselling drivers/ transporters. Blacklisting of transporter Kalika Liquid carriers. | SOD | Marketing | SWZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122760 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122760 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122760 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010965ACN-2026-03-4000122760 | AUD-2026-03-2000010965ACN-2026-03-4000122760 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Further fine tuning done to achieve blending ratio of 20 % on continuous basis. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122761 | Closed | ANAND RUPAK | 2026-07-06 | Location is dispatching 20% EBP Gasohol and is 100% ensuring the same. Checked the same in gantry , found the blending percentage varying from 15 to 20 in the second half of loading. Found that the final blending ratio is 20%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1775 | BENGALURU TERMINAL | Location to take corrective action to ensure ethanol blending as per HQO guidelines. | SOD | Marketing | SWZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122761 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122761 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122761 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122761 | AUD-2026-03-2000010965ACN-2026-03-4000122761 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Surplus portal Being uploaded after completion of Tank project job. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122762 | Closed | ANAND RUPAK | 2026-07-06 | Inventory verification done and found ok.03 Trucks are under disposal. Unused assets and surplus materials updated in surplus portal | 3.9 | Abnormal variations / unused assets reviewed | 1775 | BENGALURU TERMINAL | Location is advised to update the Surplus portal immediately after the completion of the Tank and Pipeline Project. | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-03-2000010965ACN-2026-03-4000122762 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122762 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122762 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122762 | AUD-2026-03-2000010965ACN-2026-03-4000122762 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Blacklisting done for the entire fleet of M/s Kalika Liquid Carrier. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122763 | Closed | ANAND RUPAK | 2026-07-06 | Daily report of MFM Vs BCU totalizer being maintained, K-Factor changes report checked and no abnormalities found. Local loading details being maintained. Checked seals of BCU,MFM and K-factors of MFMs matching with calibration certificate. Noted that instance of2 Sick TTs of Kalika Liquid Carriers were present in the month of January 2026 | 3.11 | MFM vs BCU totalizer comparison checked | 1775 | BENGALURU TERMINAL | Blacklisting of Kalika Liquid carriers who has committed fraud to be done | SOD | Marketing | SWZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S4 | F1 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122763 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122763 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122763 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122763 | AUD-2026-03-2000010965ACN-2026-03-4000122763 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | 1. Fire Hydrant provided near Mechanical Fabrication shed. 2. Sprinkler lines of Tk30 modified to avoid obstructions. 3. Toe guard and chain links provided on Tk30 top between gap of walkway and tank roof. 4. provision for tank 30 guaging provided with properplatform. 5. Dry Leaves to be removed 6. Gantry roof cleaning done. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122765 | Closed | ANAND RUPAK | 2026-07-06 | Full terminal round was taken with officers. Reviewed TK30 progress | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1775 | BENGALURU TERMINAL | 1. Fire Hydrant to be provided near Mechanical Fabrication shed. 2. Sprinkler lines of Tk30 to be modified to avoid obstructions. 3. Toe guard and chain links to be provided on Tk30 top between gap of walkway and tank roof. 4. provision for tank 30 guaging to be provided with proper platform. 5. Dry Leaves to be removed frequently from near Pipeline sampling shed. 6. Gantry roof cleaningto be done. | SOD | Marketing | SWZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122765 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122765 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122765 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122765 | AUD-2026-03-2000010965ACN-2026-03-4000122765 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 | ANAND RUPAK | 2026-07-06 | Capitalization done. | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122766 | Closed | ANAND RUPAK | 2026-07-06 | Project review done and changes suggested with safety and compliance of OISD in view. | 4.3 | Project progress reviewed | 1775 | BENGALURU TERMINAL | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | SOD | Marketing | SWZ | 2026-03-31 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122766 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122766 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122766 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122766 | AUD-2026-03-2000010965ACN-2026-03-4000122766 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
KUMAR CHAKRABORTI ALOK | 2026-07-09 |  |  | Scrap to be disposed | SENIOR MANAGEMENT INSPECTION BENGALURU | 2026-03-03 | AUD-2026-03-2000010965 | 2026-03-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122767 | Closed | KUMAR CHAKRABORTI ALOK | 2026-07-09 | Close monitoring and compliance is required. 2 nos Schedules of RFDs to be re-auctioned because of failure in earlier auctions | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1775 | BENGALURU TERMINAL | Completion of Scrap disposal by 31.03.2026 | SOD | Marketing | SWZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010965ACN-2026-03-4000122767 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010965ACN-2026-03-4000122767 | 2026-09-24 17:00 | 25.0455 | 311 | >20 | AUD-2026-03-2000010965 - ACN-2026-03-4000122767 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010965ACN-2026-03-4000122767 | AUD-2026-03-2000010965ACN-2026-03-4000122767 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 45
[5 empty] | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143858 | Open |  |  | Tot. 60 no of CCTV's are available at the location. 3 of the CCTV cameras are working as on date (02/07/2026). Also 92 days CCTV recording is available. Random recording checked for 12/03/2026 and found available. | 2.08 | CCTV functioning checked | 1341 | HISAR TERMINAL | Faulty cameras to be made functional. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143858 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143858 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143858 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015093ACN-2026-07-4000143858 |  | AUD-2026-07-2000015093ACN-2026-07-4000143858 | 21 |  | 27 | 80 | 0 | 0 | 48
SABLE RONAK MOHANKUMAR | 2026-07-09 | SINGH PREETI | 2026-07-09 | All available Biodiesel stock at the location has been fully exhausted through dispatches. Further POs are awaited from HQO/Zone. Biodiesel blending in TT dispatches will be resumed immediately upon receipt of product, and blending shall be ensured thereafter. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124905 | Closed | SINGH PREETI | 2026-07-09 | It was observed that location is not ensuring sufficient bio diesel blending in TT dispatches. Advised location to follow up and ensure improved performance. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ENVIRONMENTAL | S2 | F2 | 2026-03-30 | AUD-2026-03-2000011223ACN-2026-03-4000124905 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124905 | 2026-08-22 22:00 | 57.8372 | 311 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124905 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124905 | AUD-2026-03-2000011223ACN-2026-03-4000124905 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-04-21 | The battery has been topped up with distilled water and restored to the required level.Further, instructions have been given to theconcerned personnel to check and maintain the battery water level regularly as part of routine inspection to avoid recurrence. Alsogasket has been replaced in transformer | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122664 | Closed | DAS DARSHAN | 2026-04-21 | Sweating observed in transformer from gasket. Spilled Oil observed over floor of 250 KVA DG. Inspection of battery health (Fire engine) is not being carried out. Water Level of battery observed below required level for Fire Engine Number 2. | 4.2 | Maintenance activities reviewed | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122664 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122664 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122664 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122664 | AUD-2026-03-2000011009ACN-2026-03-4000122664 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-07-06 | Location has closed solar project as per revised time line. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122665 | Closed | DAS DARSHAN | 2026-07-06 | Project review done. Location to close solar project as per revised time line. | 4.3 | Project progress reviewed | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011009ACN-2026-03-4000122665 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122665 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122665 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122665 | AUD-2026-03-2000011009ACN-2026-03-4000122665 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-07-06 | Corrective action has been taken | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122666 | Closed | DAS DARSHAN | 2026-07-06 | Quality of PM shall be improved as per above observation. | 4.4 | Quality of PM compliance reviewed | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122666 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122666 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122666 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122666 | AUD-2026-03-2000011009ACN-2026-03-4000122666 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-07-06 | Net is provided over open roof water tank. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122668 | Closed | DAS DARSHAN | 2026-07-06 | Net to be provided over open roof water tank. | 6.1 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122668 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122668 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122668 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122668 | AUD-2026-03-2000011009ACN-2026-03-4000122668 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-04-21 | Toe guard has been be provided on catwalk of collection pit near TK-31. | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122678 | Closed | DAS DARSHAN | 2026-04-21 | Toe guard to be provided on catwalk of collection pit near TK-31. | 6.11 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122678 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122678 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122678 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122678 | AUD-2026-03-2000011009ACN-2026-03-4000122678 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-07-06 | Hand siren marking has been done for all siren | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122679 | Closed | DAS DARSHAN | 2026-07-06 | Hand siren marking to be done for all siren: Siren number/Total siren i.e. 1/10 or 2/10) | 6.12 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122679 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122679 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122679 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122679 | AUD-2026-03-2000011009ACN-2026-03-4000122679 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-07-06 | TW gantry structure Earth pit chamber has been repaired | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122673 | Closed | DAS DARSHAN | 2026-07-06 | TW gantry structure Earth pit brick wall found damaged. Repair required. | 6.6 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122673 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122673 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122673 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122673 | AUD-2026-03-2000011009ACN-2026-03-4000122673 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
VED PRAKASH | 2026-07-10 | DAS DARSHAN | 2026-04-21 | Arrow Marker has been provided on the slop line in siding area | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122675 | Closed | DAS DARSHAN | 2026-04-21 | Arrow marker to be provided on slop line. | 6.8 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122675 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122675 | 2026-09-03 | 46.7538 | 312 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122675 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122675 | AUD-2026-03-2000011009ACN-2026-03-4000122675 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 45
|  | CHANGMAI RAHUL | 2026-07-10 | Renewal of pending expired licenses completed 1.Factory license 2.PESO License 3. Pollution control CTO 4. Hazardous waste NOC | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136982 | Completed | CHANGMAI RAHUL | 2026-07-10 | Interected with only officer posted Shri Rahul Changmai,Depot Manager-Dimapur IRD.Depot is yet to be operational.He is looking after the pending Job of TAS activities and co-ordinating for other statutory licences including Depot upkeep. | 1.1 | Interaction with officers (1–1.5 hrs) | 1708 | DIMAPUR DEPOT | All statutory licence Pending for renewal to be expedited. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136982 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136982 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136982 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136982 |  | AUD-2026-06-2000012955ACN-2026-06-4000136982 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | TAS vendor has been coordinate and work done under Manday PO 5200121749. TAS service engineer visited from 02/05/26 to 14/05/26 andalso visited in 2nd phase from 22/06/26 to 01/07/26. All the available TAS equipments were installed like new Barrier gate panel, Bay-1 HSD MFM rectification. Recalibration of both MS and HSD of Bay-1 after DCV tuning. And Bay-2 MS and HSD DCV tuning and legal metrology calibration. LRC2 setup done.Remote support and SAP integration underway. All the 4 DCVs are tuned along with replacing faulty DCVs. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136983 | Completed | CHANGMAI RAHUL | 2026-07-10 | Review of pending TAS activities which are being penidng and M/S ICON is executing the Job and also faulty equipment list of TAS isdiscussed.Officer is coordianating with HQO/Zonal TAS team and TAS vendor for expediting the pending TAS activities.Work is under progress by newly placed Manday PO and also the work pending under old TAS PO. | 1.2 | Performance review conducted | 1708 | DIMAPUR DEPOT | TAS activities are being carried out by Vendor by M/S Icon under new Manday PO. Officer to monitor the progress as per time line and sent progress report on daily basis to concerned Zonal M&I/TAS . Also after arrangement of spare of the faulty equipment Officer to get the installation and commissioning of such equipment in 2nd Phase of Manday PO.Pending TAS activities to be completed immediately as per PO terms and conditions in co-ordination with TAS Vendor. | SOD | Marketing | GZR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-06-2000012955ACN-2026-06-4000136983 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136983 | 2026-09-12 | 37.7538 | 363 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136983 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136983 |  | AUD-2026-06-2000012955ACN-2026-06-4000136983 | 21 |  | 27 | 80 | 7 | 7 | 52
|  | CHANGMAI RAHUL | 2026-07-10 | AS vendor is coordinated for visit and has carried out TAS maintenance activity from 22nd June2026. Below activites completed 1. Bay2 DCV and metering unit Calibration and stamping by W&M 2. Bay-1 DCV and MFM rectification and also recalibration through W&M 3. Installation of new barrier Gate panel and sensor 4.LRC installation Since other equipment like MST for TK-3 and TK-4 , Density probe of all the tanks, TSI of TK-1 and TK-2 are not available for installation. Spare from other HPCL locations where dismanting is done to be coordinated and used at Dimapur Depot. Accordingly installation to be carried out. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136984 | Completed | CHANGMAI RAHUL | 2026-07-10 | Pending Issues is the TAS activities which is listed out and expected completion target date are mentioned. PO has been placed withVendor M/s ICON Control and work under progress. | 1.3 | Pending issues reviewed | 1708 | DIMAPUR DEPOT | Officer to monitor TAS vendor M/s ICON work and complete the pending work as per PO T&C | SOD | Marketing | GZR | 2026-06-15 |  | 1 |  | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012955ACN-2026-06-4000136984 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136984 | 2026-09-12 | 37.7538 | 287 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136984 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136984 |  | AUD-2026-06-2000012955ACN-2026-06-4000136984 | 21 |  | 27 | 80 | 7 | 7 | 41
|  | CHANGMAI RAHUL | 2026-07-10 | All faulty equipments are identified and shared with Zonal M&I/TAS officer | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136986 | Completed | CHANGMAI RAHUL | 2026-07-10 | Arragngement of spare materials from other HPCL loactions to replace the faulty TAS instrument diagnosed during TAS activity by Vendor | 1.5 | HQO / Zonal support required identified | 1708 | DIMAPUR DEPOT | Location to share detailed list of faulty equipments which require arrangement from other locations. Anythings add up in the list should be immediately intimated to Zonal M&I/TAS and to arrange | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136986 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136986 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136986 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136986 |  | AUD-2026-06-2000012955ACN-2026-06-4000136986 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | The development of green areas is being carried out progressively, keeping in view the constraints of a limited budget. All equipment is being maintained through timely upkeep, along with the procurement of the necessary materials. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136987 | Completed | CHANGMAI RAHUL | 2026-07-10 | Improvement plan and upkeep of the locations along with greenary development plan is discussed.All necessary check and system to bekept ready for commencement of supplies. | 1.8 | Improvement plans discussed | 1708 | DIMAPUR DEPOT | XX | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136987 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136987 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136987 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136987 |  | AUD-2026-06-2000012955ACN-2026-06-4000136987 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | Safety training given to all contractual manpower including the security guards | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136990 | Completed | CHANGMAI RAHUL | 2026-07-10 | 6 security personnel available. 2 nos of security personnel duty in shift. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1708 | DIMAPUR DEPOT | Training to Security Guards to be strengthen. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136990 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136990 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136990 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136990 |  | AUD-2026-06-2000012955ACN-2026-06-4000136990 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | ESD commissioning and Testing done by the TAS vendor | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136991 | Completed | CHANGMAI RAHUL | 2026-07-10 | TAS-ESD commissioning under progress and hence checking couldn't be carried out. | 2.5 | Emergency response preparedness reviewed | 1708 | DIMAPUR DEPOT | ESD commissioning/Testing to be completed immediately | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136991 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136991 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136991 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136991 |  | AUD-2026-06-2000012955ACN-2026-06-4000136991 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | All the 27 CCTVs are functional now after rectification by CCTV service engineer from 08/06/26 to 12/06/26 | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136992 | Completed | CHANGMAI RAHUL | 2026-07-10 | CCTV sever down. Total 27 nos of CCTV are installed | 2.6 | CCTV functioning checked | 1708 | DIMAPUR DEPOT | Officer to follow up with CCTV vendor for resolution and resoration. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136992 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136992 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136992 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136992 |  | AUD-2026-06-2000012955ACN-2026-06-4000136992 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | ESD commissioning and Testing completed by the TAS vendor | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136993 | Completed | CHANGMAI RAHUL | 2026-07-10 | ESD integration pending at TAS Vendor /HCD not available. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1708 | DIMAPUR DEPOT | Officer to monitor the ESD commissioning by vendor and ensure completion | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136993 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136993 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136993 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136993 |  | AUD-2026-06-2000012955ACN-2026-06-4000136993 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-10 | TT loading/unloading operations has not started in Dimapur Depot | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000136996 | Completed | CHANGMAI RAHUL | 2026-07-10 | TT loading/unloading operations yet to start | 3.3 | VTS deviations reviewed | 1708 | DIMAPUR DEPOT | XX | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136996 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136996 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136996 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136996 |  | AUD-2026-06-2000012955ACN-2026-06-4000136996 | 21 |  | 27 | 80 | 7 | 7 | 44
DURGA NARAIN MEENA | 2026-07-13 | ASHISH KUMAR GUTHALIYAN | 2026-07-13 | CBAC has been repaired. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127483 | Closed | DURGA NARAIN MEENA | 2026-07-13 | A well-coordinated Double Contingency Fire Mock Drill was successfully conducted on 11/03/2026 at 1235 hours, simulating a scenarioof product leakage and spool fire in TK-04 along with a fire in the PLT section. The execution of the drill reflects the commendable preparedness and professionalism of the location team. The sprinklers of adjacent tanks, namely Tank No. 05 and Tank No. 06, operated effectively. The MEFG system of Tank No. 04 dyke functioned as intended, along with the satisfactory operation of HVLR No. 01 and 06. Overall, coordination among team members was found to be highly effective, demonstrating strong teamwork and readiness to handle emergency situations. However, it was observed that the CBAC system which was functional before the fire drill became disfunctional after the drill was over. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1341 | HISAR TERMINAL | Corrective action to be taken. | SOD | Marketing | NZ | 2026-04-15 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010926ACN-2026-03-4000127483 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127483 | 2026-09-30 17:00 | 19.0455 | 315 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127483 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127483 | AUD-2026-03-2000010926ACN-2026-03-4000127483 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 45
DURGA NARAIN MEENA | 2026-07-13 | ASHISH KUMAR GUTHALIYAN | 2026-07-13 | CBAC has been repaired. | SR MGMT INSPECTION HISAR TML | 2026-03-12 14:00 | AUD-2026-03-2000010926 | 2026-03-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127485 | Closed | DURGA NARAIN MEENA | 2026-07-13 | During the Visit Access control at main gate was checked and found that CBAC System was not fully functional at Main entry gate along with Entry to Licence area and Control room. | 2.8 | Access control systems checked | 1341 | HISAR TERMINAL | CBAC system to be made 100% operational | SOD | Marketing | NZ | 2026-04-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010926ACN-2026-03-4000127485 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010926ACN-2026-03-4000127485 | 2026-09-30 17:00 | 19.0455 | 315 | >20 | AUD-2026-03-2000010926 - ACN-2026-03-4000127485 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010926ACN-2026-03-4000127485 | AUD-2026-03-2000010926ACN-2026-03-4000127485 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 45
PURANAM PRAKASH | 2026-07-13 | G SADASIVAN | 2026-07-10 | All 86 cameras are working now | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143117 | Closed | G SADASIVAN | 2026-07-10 | 4 CCTVs are not working | 2.6 | CCTV functioning checked | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 8 | EMERGENCY | S4 | F2 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143117 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143117 | 2026-09-22 17:00 | 27.0455 | 315 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143117 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143117 | AUD-2026-07-2000014942ACN-2026-07-4000143117 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 45
PURANAM PRAKASH | 2026-07-13 |  |  | Pending | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124080 | Closed | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | 4 CCTVs are not working | 2.6 | CCTV functioning checked | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 8 | EMERGENCY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124080 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124080 | 2026-09-22 17:00 | 27.0455 | 315 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124080 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124080 | AUD-2026-03-2000011172ACN-2026-03-4000124080 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 45
RAHA ROY SUBRAJYOTI | 2026-07-13 | PATIL AMOD MOHANRAO | 2026-07-13 | Panel has been decommissioned and removed from Battery room on 14-06-2026 | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124839 | Closed | PATIL AMOD MOHANRAO | 2026-07-13 | one non-FLP panel of 50 KVA DGSET found in battery room. | 6.2 | Battery room of control room | 1630 | PARADEEP TERMINAL | Location either remove the panel or make it FLP | SOD | Marketing | ECZ | 2026-05-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-03-2000010823ACN-2026-03-4000124839 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124839 | 2026-08-20 17:50 | 60.0108 | 315 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124839 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124839 | AUD-2026-03-2000010823ACN-2026-03-4000124839 | 21 | 21 | 26 | 80 | 11 | 11 | 39 | 45
[5 empty] | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000144101 | Open |  |  | FO sludge formed during Tank 2 cleaning. Kept in barrels. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1973 | CASSIMODE BLACK OIL TERMINAL | To be disposed off through TNPCB registered vendors. Location to initiate RFD for dosposal. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000144101 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000144101 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000144101 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015706ACN-2026-07-4000144101 |  | AUD-2026-07-2000015706ACN-2026-07-4000144101 | 21 |  | 27 | 80 | 0 | 0 | 57
SUJEET KUMAR | 2026-07-13 | SAXENA UMESH CHANDRA | 2026-07-13 | Housekeeping is done regularly. Scrap area has been cleared by seggreagating scraps into metal scrap, plastic, pipes etc (picture enclosed). Location of the emergency trolley has been identified with a display board installed (picture of the display board is enclosed) | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135382 | Closed | SAXENA UMESH CHANDRA | 2026-07-13 | Housekeeping is being maintained. PPE usage is done. | 3.15 | Housekeeping & PPE usage checked | 1457 | INDORE DEPOT | House keeping still needs improvement. Emergency trolley key to placed at identified location and its location to be displayed on the trolley. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 3 | ENVIRONMENTAL | S1 | F3 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135382 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135382 | 2026-09-09 19:00 | 39.9622 | 315 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135382 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135382 | AUD-2026-06-2000012547ACN-2026-06-4000135382 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 45
SUJEET KUMAR | 2026-07-13 | SAXENA UMESH CHANDRA | 2026-07-13 | Vegetation is being removed regularly. Vegetation removal activity was last done vide release order number 5400431386 (June 2026).Picture of the area with vegegation height maintained to minimum is enclosed. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135383 | Closed | SAXENA UMESH CHANDRA | 2026-07-13 | Checked and found to be okay. Vegetation to be removed. | 3.16 | Earth pits / boundary / vegetation control checked | 1457 | INDORE DEPOT | Vegetation to be removed. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 3 | ENVIRONMENTAL | S1 | F3 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135383 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135383 | 2026-09-09 19:00 | 39.9622 | 315 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135383 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135383 | AUD-2026-06-2000012547ACN-2026-06-4000135383 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 45
|  |  |  | Work Under Progress | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137170 | Open | TAK MITHLESH KUMAR | 2026-07-14 | As per SAP, audit compliance is 31% for all audits (PM - High Level Security Audit (HLSA) 0%, PM - MDSA Audit 29%, PM - SAFE100 Self Safety Audit 82%, PM - Senior Management Inspection 14%, PM - SOD TANK AG CR 77%,PM - SOD TANK AG EFR 0%,PM - SOD TANK AG IFR 22%,PM - SOD TANK UG 81%). Supporting document for audit observation closed in SAP are not attached by location | 3.18 | OISD/MDSA/SSA compliance reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2027-12-31 | AUD-2026-06-2000012347ACN-2026-06-4000137170 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137170 | 2026-08-16 | 64.7538 | 302 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137170 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012347ACN-2026-06-4000137170 |  | AUD-2026-06-2000012347ACN-2026-06-4000137170 | 21 |  | 27 | 80 | 2 | 2 | 44
|  |  |  | 1. Hydrant Line works PO need to changed in revenue code. 2. Support works under progress . 3/4/5 Completed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137172 | Open | NEHARA AJAY | 2026-10-17 | Following are the observations 1. Hydrant line supports near dyke area are settled or tilted. 2. Support missing for pneumatic line. 3. Black oil dyke wall is having unblocked pipe line entry opening. 4. Lube oil for 250 KVA DG was found below minimum level and was leaking from chamber. 5. Air compressor daily checklist was filled last on date 24.04.2025 | 4.2 | Maintenance activities reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-06-2000012347ACN-2026-06-4000137172 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137172 | 2026-08-16 | 64.7538 | 302 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137172 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012347ACN-2026-06-4000137172 |  | AUD-2026-06-2000012347ACN-2026-06-4000137172 | 21 |  | 27 | 80 | 2 | 2 | 44
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Action has been taken and intimater to HR head EZ. (attached) | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124822 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Interaction done . However Anup Tirkey not doing any productive work and not able to understand any instructions given by LIC or zonal officers | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1630 | PARADEEP TERMINAL | Case to be build up against Anup KR Tirkey and take up with HR | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010823ACN-2026-03-4000124822 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124822 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124822 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124822 | AUD-2026-03-2000010823ACN-2026-03-4000124822 | 21 | 21 | 26 | 80 | 11 | 11 | 44 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Complied ( details covered in other observations also. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124823 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1630 | PARADEEP TERMINAL | Major project of tank conversion to be expedited . Leftover scrap disposal to be completed | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-30 | AUD-2026-03-2000010823ACN-2026-03-4000124823 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124823 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124823 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124823 | AUD-2026-03-2000010823ACN-2026-03-4000124823 | 21 | 21 | 26 | 80 | 11 | 11 | 57 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | FLM was approved and budget was allotted in March 2026. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124824 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | MEB budget in some CEs as per SSA jobs & addl. Jobs undertaken by location | 1.5 | HQO / Zonal support required identified | 1630 | PARADEEP TERMINAL | FLM send by location for additional budget with justification | SOD | Marketing | ECZ | 2026-03-15 | POOR PLANNING OR RISK ASSESSMENT | 3 | PROCESS SAFETY | S3 | F1 | 2026-03-15 | AUD-2026-03-2000010823ACN-2026-03-4000124824 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124824 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124824 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124824 | AUD-2026-03-2000010823ACN-2026-03-4000124824 | 21 | 21 | 26 | 80 | 11 | 11 | 28 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | SOD-252050 approved and appropriated for Lux Level Improvement | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124825 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Lux level checked and found low level at TT gantry (84) , Control room (290), security cabin (80) , secondary road (8) . | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1630 | PARADEEP TERMINAL | Location has already taken budget for lux level improvement | SOD | Marketing | ECZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010823ACN-2026-03-4000124825 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124825 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124825 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124825 | AUD-2026-03-2000010823ACN-2026-03-4000124825 | 21 | 21 | 26 | 80 | 11 | 11 | 44 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Training session arranged for security for alertness and energetic responses. Training photo attached. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124826 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1630 | PARADEEP TERMINAL | security person need to be more energetic to be ready allthe time for facing any situation . More training and their working to be checked during mock drill | SOD | Marketing | ECZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010823ACN-2026-03-4000124826 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124826 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124826 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124826 | AUD-2026-03-2000010823ACN-2026-03-4000124826 | 21 | 21 | 26 | 80 | 11 | 11 | 44 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-05-11 | Location has procured Eyesight Colour Blindness testing kit and same has been kept in health centre. It will be used by CDP and others during routine health checkups and camps. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124827 | Closed | PATIL AMOD MOHANRAO | 2026-05-11 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1630 | PARADEEP TERMINAL | advised to procure the same urgently | SOD | Marketing | ECZ | 2026-04-30 | INADEQUATE SAFETY CULTURE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010823ACN-2026-03-4000124827 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124827 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124827 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124827 | AUD-2026-03-2000010823ACN-2026-03-4000124827 | 21 | 21 | 26 | 80 | 11 | 11 | 35 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Routine Meetings are being planned with transporters on awareness. Daily safety talk is also being done with TT crew to address safety in transit and during unloading. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124834 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Transporter and dealer meet done | 3.2 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1630 | PARADEEP TERMINAL | Transporter - safety during transit advised . Transporters required to provide safe route in rayagada route to avoid unsafe Ghat section. Toll tax payments Dealer meet- improvement in communication with transporter , location . Saftey in transit & during unloading . | SOD | Marketing | ECZ | 2026-03-31 | POOR COMMUNICATION | 2 | CONTRACTOR SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124834 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124834 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124834 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124834 | AUD-2026-03-2000010823ACN-2026-03-4000124834 | 21 | 21 | 26 | 80 | 11 | 11 | 31 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Complied. Route correction for all identified incorrect routes completed and secondary routes also added and approved. Routine monitoring is being done for all routes and NRO routes also to ensure accurate routes are available in SAP. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124828 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Checked . Route deviation voilation found | 3.3 | VTS deviations reviewed | 1630 | PARADEEP TERMINAL | route correction in some cases | SOD | Marketing | ECZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124828 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124828 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124828 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124828 | AUD-2026-03-2000010823ACN-2026-03-4000124828 | 21 | 21 | 26 | 80 | 11 | 11 | 31 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | All Ethanol TTs are being monitored with physical dip + UG Tank dip.TTs where abnormal loss observed in UG tank are re-checked in calibration shed for any calibration errors. Loss has been controlled to -7 KL (-0.09%) loss in June 2026. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124829 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Before unloading TT dips and TT fittings checked | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1630 | PARADEEP TERMINAL | Advised location to carry out analysis of all ethanol TTs stock loss variation during unloading by tank dips and check suspected TTs in calibration | SOD | Marketing | ECZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 2 | ASSET INTEGRITY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000010823ACN-2026-03-4000124829 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124829 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124829 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124829 | AUD-2026-03-2000010823ACN-2026-03-4000124829 | 21 | 21 | 26 | 80 | 11 | 11 | 35 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Complied : Mail sent to Manager Automation SOD-SBU for surplus skid availability on 15-05-2026. Copy attached in SAP audit compliance. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124830 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | SKO dye mixing equipement surplus after location made SKO free | 3.9 | Abnormal variations / unused assets reviewed | 1630 | PARADEEP TERMINAL | this facility to be offered to HQO for utilization at other locations | SOD | Marketing | ECZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124830 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124830 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124830 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124830 | AUD-2026-03-2000010823ACN-2026-03-4000124830 | 21 | 21 | 26 | 80 | 11 | 11 | 31 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Lawn developed infront of Admin office and other areas housekeeping done. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124831 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Checked . Gardening improvement advised infront of office | 3.15 | Housekeeping & PPE usage checked | 1630 | PARADEEP TERMINAL | yes | SOD | Marketing | ECZ | 2026-05-30 | INSUFFICIENT SUPERVISION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-05-30 | AUD-2026-03-2000010823ACN-2026-03-4000124831 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124831 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124831 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124831 | AUD-2026-03-2000010823ACN-2026-03-4000124831 | 21 | 21 | 26 | 80 | 11 | 11 | 39 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Grass cutting in railway siding area , ETP area completed. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124832 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1630 | PARADEEP TERMINAL | yes | SOD | Marketing | ECZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124832 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124832 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124832 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124832 | AUD-2026-03-2000010823ACN-2026-03-4000124832 | 21 | 21 | 26 | 80 | 11 | 11 | 31 | 46
|  | RAHA ROY SUBRAJYOTI | 2026-07-14 |  | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124833 | Completed |  |  | Compliance status reviewed . OISD compliances of 5 pointsAND 12 NOS. FOR SSA pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1630 | PARADEEP TERMINAL | advised to comply by 31.3.2026 | SOD | Marketing | ECZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124833 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124833 | 2026-08-20 17:50 | 60.0108 | 211 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124833 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010823ACN-2026-03-4000124833 |  | AUD-2026-03-2000010823ACN-2026-03-4000124833 | 21 |  | 26 | 80 | 11 | 11 | 31
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | 1. Currently SKO is available in pipeline, same if planned for PDS loading, blue dye skid will be used. Post complete evacuation ofSKO, existing facility will be dismantled with MOC. Blue dye blending skid has been offered to HQO TAS for possibility of shiftingto other location. 2. Existing SKO UG Pipeline has been converted to Ethanol. Existing SKO pump will be utilized for pumping. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124835 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Yes | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1630 | PARADEEP TERMINAL | Removal of idling facilities like SKO marker skit / air compressor shed near MCC room , ethanol unlaoding pumping arrangement | SOD | Marketing | ECZ | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000010823ACN-2026-03-4000124835 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124835 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124835 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124835 | AUD-2026-03-2000010823ACN-2026-03-4000124835 | 21 | 21 | 26 | 80 | 11 | 11 | 44 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 |  |  | TK1 conversion and commissioning Completed , TK2 TK2 is undergoing repair post inspection. PO palced for TK15,TK16. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124836 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Reviewed . | 4.3 | Project progress reviewed | 1630 | PARADEEP TERMINAL | location advised to speed up all jobs of tank conversion | SOD | Marketing | ECZ | 2026-09-30 | NATURAL DISASTERS OR UNFORESEEN EVENTS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010823ACN-2026-03-4000124836 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124836 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124836 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124836 | AUD-2026-03-2000010823ACN-2026-03-4000124836 | 21 | 21 | 26 | 80 | 11 | 11 | 57 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Scrap disposal for major items completed. Contracts placed for uplifting and scrap uplifting is ongoing. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124837 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | scrap disposal of pending sprinkler material & other misc. fixed assets items valuation done. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1630 | PARADEEP TERMINAL | RFD to be made within 2 days | SOD | Marketing | ECZ | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010823ACN-2026-03-4000124837 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124837 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124837 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124837 | AUD-2026-03-2000010823ACN-2026-03-4000124837 | 21 | 21 | 26 | 80 | 11 | 11 | 31 | 46
RAHA ROY SUBRAJYOTI | 2026-07-14 | PATIL AMOD MOHANRAO | 2026-07-14 | Hydrant line is now withstanding pressure up to 9.5. Upon issuing the command for Jockey Pump stop, the signal is successfully reflected in SCADA, thereby preventing any further pressure build-up. | SENIOR MANAGEMENT INSPECTION 050326 | 2026-03-06 | AUD-2026-03-2000010823 | 2026-03-06 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124838 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | At far end of hydrant line header , pressure found to be 11 kg compare to 9-9.5 kg at fire engine shed . | 6.1 | FIRE HYDRANT LINE PRESSURE | 1630 | PARADEEP TERMINAL | Advised to check PTs and check the setting of jockey pumps to reduce far end pressure to 8.5-9 kg | SOD | Marketing | ECZ | 2026-04-15 | INSTRUMENTATION OR ALARM FAILURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010823ACN-2026-03-4000124838 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010823ACN-2026-03-4000124838 | 2026-08-20 17:50 | 60.0108 | 316 | >20 | AUD-2026-03-2000010823 - ACN-2026-03-4000124838 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010823ACN-2026-03-4000124838 | AUD-2026-03-2000010823ACN-2026-03-4000124838 | 21 | 21 | 26 | 80 | 11 | 11 | 33 | 46
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Location has procured Eyesight Colour Blindness testing kit and same has been kept in health centre. It will be used by CDP and others during routine health checkups and camps. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000134148 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1630 | PARADEEP TERMINAL | advised to procure the same urgently | SOD | Marketing | ECZ | 2026-06-30 | FATIGUE AND STRESS | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134148 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134148 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134148 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000134148 |  | AUD-2026-06-2000012424ACN-2026-06-4000134148 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Housekeeping of planning room , TWG siding area , ETP and tankfarm completed. Housekeeping is being maintained daily. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135304 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 |  | 3.15 | Housekeeping & PPE usage checked | 1630 | PARADEEP TERMINAL | Housekeeping to be done | SOD | Marketing | ECZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135304 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135304 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135304 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135304 |  | AUD-2026-06-2000012424ACN-2026-06-4000135304 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Route are being monitored and route corrections & secondary route addition completed. Toll tax old payments cleared for submitted payment slips , activity is being done in timebound manner. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135307 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Transporters meeting done on 20.5.26 | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1630 | PARADEEP TERMINAL | Transporter - safety during transit advised . Transporters required to provide safe route in rayagada route to avoid unsafe Ghat section. Toll tax payments | SOD | Marketing | ECZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135307 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135307 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135307 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135307 |  | AUD-2026-06-2000012424ACN-2026-06-4000135307 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Route are being monitored and route corrections & secondary route addition completed in identified routes. Awareness creation is being done for route violations , stoppages regularly and letters are also being issued along with action as per ITDG for stoppages. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000134149 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Checked . Route deviation voilation & unauthorized stoppages found . ATF TTs to Ranchi , stoppage voilation found diversion from route | 3.3 | VTS deviations reviewed | 1630 | PARADEEP TERMINAL | route correction in some cases & stoppages voilation (other than authorized) to be stopped | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134149 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134149 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134149 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000134149 |  | AUD-2026-06-2000012424ACN-2026-06-4000134149 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Location is daily analyzing Dip shortages and UG Tank dip shortages. TT Dip shortages are being booked on TT during GRNs and for abnormal UG Tank losses , TT is being re-checked in calibration shed in presence of supplier representative. Vehicle blocked in IEMS for legal metrology violation in case of error in calibration. Vehicle blocked in IEMS AP39WJ1519 , AP39WJ4567 , WB11Q8867. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135300 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Some TTs of few suppliers like Cuttuck distillaries & Ankur Biochem found to be having abnormal variation during unloading and later found to be having short calibration by 3000-4000 ltrs. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1630 | PARADEEP TERMINAL | Advised location to carry out analysis of all ethanol TTs stock loss variation during unloading by tank dips and check suspected TTs in calibration and make one record of all suppliers. Also action against deflauter TTs to be taken by suppliers and same TTs shallnot be operated in Industry .Action on TT needs to be updated on IEMS portal in coordination with HQO | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135300 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135300 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135300 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135300 |  | AUD-2026-06-2000012424ACN-2026-06-4000135300 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Stock Loss is under control with latest data as +0.069 for MS and -0.09 for Ethanol for June 2026. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135302 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | daily reco sheet checked | 3.8 | Auto vs Manual reconciliation checked | 1630 | PARADEEP TERMINAL | Stock loss of Ethanol and MS is beyond the target , location required to pay full attention on Ethanol TT unloading and PLT receiptfrom IOC to cover up losses by month end | SOD | Marketing | ECZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135302 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135302 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135302 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135302 |  | AUD-2026-06-2000012424ACN-2026-06-4000135302 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | PM Job file is being maintained with monthly all PM activities updated facility wise in file. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000135309 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . Records of stariner / pressure gauge checked and found incomplete | 4.2 | Maintenance activities reviewed | 1630 | PARADEEP TERMINAL | Suggested that in addition to comnpletion of inspoection report in audit module , print out of the same shall also be available in location records | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135309 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135309 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135309 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135309 |  | AUD-2026-06-2000012424ACN-2026-06-4000135309 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | All Pos placed and jobs are being carried out as per set timelines. TK2 commissioning delayed due to major repair in annular plates. TK15 has been taken in outage and undergoing IFR conversion. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000135310 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Reviewed . | 4.3 | Project progress reviewed | 1630 | PARADEEP TERMINAL | location advised to speed up all jobs of tank conversion | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 6 | ASSET INTEGRITY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000012424ACN-2026-06-4000135310 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135310 | 2026-08-20 17:50 | 60.0108 | 394 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135310 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135310 |  | AUD-2026-06-2000012424ACN-2026-06-4000135310 | 21 |  | 27 | 80 | 11 | 11 | 57
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Hydrant line is now withstanding pressure up to 9.5. Upon issuing the command for Jockey Pump stop, the signal is successfully reflected in SCADA, thereby preventing any further pressure build-up. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135312 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | At far end of hydrant line header , pressure found to be 11 kg compare to 9-9.5 kg at fire engine shed . | 6.1 | FIRE HYDRANT LINE PRESSURE | 1630 | PARADEEP TERMINAL | Advised to check PTs and check the setting of jockey pumps to reduce far end pressure to 8.5-9 kg | SOD | Marketing | ECZ | 2026-06-30 | INSTRUMENTATION OR ALARM FAILURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135312 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135312 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135312 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135312 |  | AUD-2026-06-2000012424ACN-2026-06-4000135312 | 21 |  | 27 | 80 | 11 | 11 | 44
|  | PATIL AMOD MOHANRAO | 2026-07-14 | Panel has been decommissioned and removed from Battery room on 14-06-2026 | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000135313 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | one non-FLP panel of 50 KVA DGSET found in battery room. | 6.2 | Battery room of control room | 1630 | PARADEEP TERMINAL | Location either remove the panel or make it FLP | SOD | Marketing | ECZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135313 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135313 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135313 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135313 |  | AUD-2026-06-2000012424ACN-2026-06-4000135313 | 21 |  | 27 | 80 | 11 | 11 | 44
RAHA ROY SUBRAJYOTI | 2026-07-15 | PATIL AMOD MOHANRAO | 2026-07-14 | "1. Stock Loss is under control with latest data as +0.069 for MS and -0.09 for Ethanol for June 2026. 2. Contract generated for misc lot and disposal in ongoing. Remaining scrap will also be completed in timebound manner. 3. Visit done to R&B office jagathsingpur and letter submitted to get latest cost utilization certificate. Certificate will be shared by R&B in July 26 with expense done upto June 26. 4. Housekeeping completed in ETP , UG TF , TWG area and other areas are also being maintained clean. " | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000134143 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1630 | PARADEEP TERMINAL | 1.Stock loss - Stock loss in ethanol & MS is beyond AOP target . Location need to check the areas of losses & take action 2. Scrapdisposal - Balance scrap & old unusable equipment RFD to be made & disposed 3. receiipt of PWD payment made outside terminal of Rs.1 Cr to be taken 4. Housekeeping to be improved in operating area | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000012424ACN-2026-06-4000134143 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134143 | 2026-08-20 17:50 | 60.0108 | 317 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134143 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012424ACN-2026-06-4000134143 | AUD-2026-06-2000012424ACN-2026-06-4000134143 | 21 | 21 | 27 | 80 | 11 | 11 | 57 | 46
RAHA ROY SUBRAJYOTI | 2026-07-15 | PATIL AMOD MOHANRAO | 2026-07-14 | "Toll tax claims physically received with toll receipts cleared. Remaining claims will be cleared in timebound manner. Route corrections completed and status is being shared in E-MIS. Secondary route updates also done for multiple Ros. " | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000134144 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Reviewed . Old Toll tax payments of transporters , route corrections , etc | 1.3 | Pending issues reviewed | 1630 | PARADEEP TERMINAL | Old cases of toll tax and route correction to be completed by 30.6.26 | SOD | Marketing | ECZ | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134144 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134144 | 2026-08-20 17:50 | 60.0108 | 317 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134144 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012424ACN-2026-06-4000134144 | AUD-2026-06-2000012424ACN-2026-06-4000134144 | 21 | 21 | 27 | 80 | 11 | 11 | 44 | 46
RAHA ROY SUBRAJYOTI | 2026-07-15 | PATIL AMOD MOHANRAO | 2026-07-14 | Lux level taken from design vendor in last week of June and modifications are being done in existing pole lights also to optimize use of lights and availability of sufficient Lux. Routine Lux monitoring is also being done by location. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000134146 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Lux level checked and found low level at TT gantry (84) , Control room (290), security cabin (80) , secondary road (8) . | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1630 | PARADEEP TERMINAL | Installation of LED lights on existing HMT and additional light poles is in progress. Location advised to get the Lux level checkedfrom same party who has provided design | SOD | Marketing | ECZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134146 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134146 | 2026-08-20 17:50 | 60.0108 | 317 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134146 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012424ACN-2026-06-4000134146 | AUD-2026-06-2000012424ACN-2026-06-4000134146 | 21 | 21 | 27 | 80 | 11 | 11 | 44 | 46
|  | PATIL AMOD MOHANRAO | 2026-07-17 | Grass cutting in railway siding area , ETP area completed. | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135305 | Completed | PATIL AMOD MOHANRAO | 2026-07-14 | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1630 | PARADEEP TERMINAL | yes | SOD | Marketing | ECZ | 2026-05-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-05-30 | AUD-2026-06-2000012424ACN-2026-06-4000135305 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135305 | 2026-08-20 17:50 | 60.0108 | 271 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135305 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135305 |  | AUD-2026-06-2000012424ACN-2026-06-4000135305 | 21 |  | 27 | 80 | 11 | 11 | 39
|  | PATIL AMOD MOHANRAO | 2026-07-17 | No recommendation | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000135308 | Completed | PATIL AMOD MOHANRAO | 2026-07-17 | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1630 | PARADEEP TERMINAL | XX | SOD | Marketing | ECZ | 2026-06-30 |  | 6 |  | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000135308 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000135308 | 2026-08-20 17:50 | 60.0108 | 302 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000135308 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012424ACN-2026-06-4000135308 |  | AUD-2026-06-2000012424ACN-2026-06-4000135308 | 21 |  | 27 | 80 | 11 | 11 | 44
RAHA ROY SUBRAJYOTI | 2026-07-17 | PATIL AMOD MOHANRAO | 2026-07-17 | Action has been taken and intimated to HR head EZ. (attached) | SR.MGMT AUDIT FOR PARADEEP TER | 2026-05-20 17:22 | AUD-2026-06-2000012424 | 2026-05-19 12:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000134142 | Closed | PATIL AMOD MOHANRAO | 2026-07-14 | Interaction done . However Anup Tirkey not doing any productive work and not able to understand any instructions given by LIC or zonal officers | 1.1 | Interaction with all officers (1–1.5 hrs) | 1630 | PARADEEP TERMINAL | Case to be build up against Anup KR Tirkey and take up with HR | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000012424ACN-2026-06-4000134142 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012424ACN-2026-06-4000134142 | 2026-08-20 17:50 | 60.0108 | 319 | >20 | AUD-2026-06-2000012424 - ACN-2026-06-4000134142 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012424ACN-2026-06-4000134142 | AUD-2026-06-2000012424ACN-2026-06-4000134142 | 21 | 21 | 27 | 80 | 11 | 11 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-17 | Water cooler is provided in TT Crew rest room | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130287 | Closed | KAMLESH SAHU | 2026-07-17 | No water cooler provided for TT crew | 6.3 | Driver amenity room | 1528 | RAIPUR IRD-II | to be provided . Budget request to be given | SOD | Marketing | ECZ | 2026-06-30 | FATIGUE AND STRESS | 3 | OCCUPATIONAL HEALTH | S3 | F1 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130287 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130287 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130287 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130287 | AUD-2026-05-2000012405ACN-2026-05-4000130287 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Repeated observation and recommendation Covered in point number 1.3 so we are closing it | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130280 | Closed | KAMLESH SAHU | 2026-07-16 | Compliance status reviewed . OISD compliances of 28 points reviewed and found that 7 complied & budget is required for other points | 3.18 | OISD/MDSA/SSA compliance reviewed | 1528 | RAIPUR IRD-II | Location advised to submit budget request for complinace of all pending points by 30.05.2026 | SOD | Marketing | ECZ | 2026-05-30 | THIRD PARTY ERRORS | 6 | PROCESS SAFETY | S3 | F2 | 2026-05-30 | AUD-2026-05-2000012405ACN-2026-05-4000130280 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130280 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130280 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130280 | AUD-2026-05-2000012405ACN-2026-05-4000130280 | 21 | 21 | 27 | 80 | 3 | 3 | 39 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Location has clean the unwanted vegitation on other side of siding and ETP. Location will continue to clean vegatation through outthe location | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130279 | Closed | KAMLESH SAHU | 2026-07-16 | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1528 | RAIPUR IRD-II | yes | SOD | Marketing | ECZ | 2026-06-15 | FAILURE TO FOLLOW PROCEDURES | 6 | ENVIRONMENTAL | S2 | F3 | 2026-06-15 | AUD-2026-05-2000012405ACN-2026-05-4000130279 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130279 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130279 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130279 | AUD-2026-05-2000012405ACN-2026-05-4000130279 | 21 | 21 | 27 | 80 | 3 | 3 | 41 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Location continued to maintained the greenery through out the location | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130278 | Closed | KAMLESH SAHU | 2026-07-16 | Found okay . | 3.15 | Housekeeping & PPE usage checked | 1528 | RAIPUR IRD-II | Greenery started by location to be maintained | SOD | Marketing | ECZ | 2026-07-01 | THIRD PARTY ERRORS | 1 | ENVIRONMENTAL | S1 | F1 | 2026-07-01 | AUD-2026-05-2000012405ACN-2026-05-4000130278 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130278 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130278 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130278 | AUD-2026-05-2000012405ACN-2026-05-4000130278 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-17 | Route correction is continuos process, Location ir regularly conducting training to create awareness among TT Crew. Record maintained and Also doing route correction as and when require. | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130276 | Closed | KAMLESH SAHU | 2026-07-17 | Checked . Route deviation voilation found | 3.3 | VTS deviations reviewed | 1528 | RAIPUR IRD-II | route correction in some cases | SOD | Marketing | ECZ | 2026-05-31 | FAILURE TO FOLLOW PROCEDURES | 6 | CONTRACTOR SAFETY | S2 | F3 | 2026-05-31 | AUD-2026-05-2000012405ACN-2026-05-4000130276 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130276 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130276 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130276 | AUD-2026-05-2000012405ACN-2026-05-4000130276 | 21 | 21 | 27 | 80 | 3 | 3 | 39 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Location has procured the same and using it | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130275 | Closed | KAMLESH SAHU | 2026-07-16 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1528 | RAIPUR IRD-II | advised to procure the same urgently | SOD | Marketing | ECZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | CONTRACTOR SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130275 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130275 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130275 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130275 | AUD-2026-05-2000012405ACN-2026-05-4000130275 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | VMS Impliment and followed | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130272 | Closed | KAMLESH SAHU | 2026-07-16 | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1528 | RAIPUR IRD-II | Visitor managmenet system recently rolled out by Godrej, need to be bring into operations for all visitors | SOD | Marketing | ECZ | 2026-06-30 | THIRD PARTY ERRORS | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130272 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130272 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130272 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130272 | AUD-2026-05-2000012405ACN-2026-05-4000130272 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Budget request has submitted to SOD HQO | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130271 | Closed | KAMLESH SAHU | 2026-07-16 | As per OISD AUDIT lux level was found inadquate in parking area , DG area , ETP Panel room, transf room , VCB area , primary roads | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1528 | RAIPUR IRD-II | Location advised to submit budget request for complinace of lux level | SOD | Marketing | ECZ | 2026-12-31 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-05-2000012405ACN-2026-05-4000130271 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130271 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130271 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130271 | AUD-2026-05-2000012405ACN-2026-05-4000130271 | 21 | 21 | 27 | 80 | 3 | 3 | 70 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Short coming of the drill has discussed in Q1 FY26-27 Safety committee meeting. Table talk of FOC and drill was conducted on 18June 26 and Practise in upcoming emergency drill dtd 18June & 27 May 26 | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130270 | Closed | KAMLESH SAHU | 2026-07-16 | Sudden mock drill of product leakage from tank valves of MS tank was done at old depot . some of deficiency in mock drill found are : 1. Affected tank sprinkler was operated very late , even after nearby tank 2. Rescue team reaches very late 3. Though emergency trolley was pulled in time but soak mats usage was delayed 4. overall coordination issue found 5. PA system not used | 2.2 | Double contingency scenario simulated; observations recorded | 1528 | RAIPUR IRD-II | All such deficiency in mock drill to be corrected in all further drills | SOD | Marketing | ECZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 9 | PROCESS SAFETY | S3 | F3 | 2026-08-31 | AUD-2026-05-2000012405ACN-2026-05-4000130270 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130270 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130270 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130270 | AUD-2026-05-2000012405ACN-2026-05-4000130270 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Location is continuosly working to improve the efficiency of gantry operation and reduce the cycle time | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130269 | Closed | KAMLESH SAHU | 2026-07-16 | Improvement plan with smooth transition of important portfolio of officers was discussed with LIC in view of transfer of officers | 1.8 | Improvement plans discussed | 1528 | RAIPUR IRD-II | TT gantry perfromance improvement was discussed as per SBU targets given | SOD | Marketing | ECZ | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130269 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130269 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130269 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130269 | AUD-2026-05-2000012405ACN-2026-05-4000130269 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | All officers works are inline to acheive expection of top management and improve in opeation efficiency. This is an continue procces and all officers are determine for it | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130268 | Closed | KAMLESH SAHU | 2026-07-16 | Top management expectations and improvement in operational efficiency was discussed | 1.6 | Expectations clearly communicated to officers | 1528 | RAIPUR IRD-II | Advise all officers to be aligned with top mgmt expectations & adherance to SOPs with safe working culture | SOD | Marketing | ECZ | 2026-05-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | PROCESS SAFETY | S2 | F3 | 2026-05-30 | AUD-2026-05-2000012405ACN-2026-05-4000130268 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130268 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130268 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130268 | AUD-2026-05-2000012405ACN-2026-05-4000130268 | 21 | 21 | 27 | 80 | 3 | 3 | 39 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | Reply of IA Audit has submitted to IA Depatment after discussion | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130266 | Closed | KAMLESH SAHU | 2026-07-16 | Pending IA audit report reply | 1.4 | Earlier action points status checked | 1528 | RAIPUR IRD-II | IA report reply discussed & to be sent | SOD | Marketing | ECZ | 2026-05-25 | THIRD PARTY ERRORS | 3 | ASSET INTEGRITY | S1 | F3 | 2026-05-25 | AUD-2026-05-2000012405ACN-2026-05-4000130266 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130266 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130266 | 532 | 8294 | 21 | 8294 | 147 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130266 | AUD-2026-05-2000012405ACN-2026-05-4000130266 | 21 | 21 | 27 | 80 | 3 | 3 | 38 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-16 | details of Pending parking area and cost estimate for NPCB budget required for OISD has submitted to HQO | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130265 | Closed | KAMLESH SAHU | 2026-07-16 | All pending OISD points , pending parking area jobs discussed . Location advised to provide cost estimate of pending parking area jobs | 1.3 | Pending issues reviewed | 1528 | RAIPUR IRD-II | details of panding parking area and cost estimate for NPCB budget required for OISD to be provided | SOD | Marketing | ECZ | 2026-05-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-05-30 | AUD-2026-05-2000012405ACN-2026-05-4000130265 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130265 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130265 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130265 | AUD-2026-05-2000012405ACN-2026-05-4000130265 | 21 | 21 | 27 | 80 | 3 | 3 | 39 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-07-15 | Details has already provided to HQO for further allotment of budget | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130264 | Closed | KAMLESH SAHU | 2026-07-15 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed for last year . MEB budget requirement for new depotalso discussed & asked to provide details | 1.2 | Performance review conducted | 1528 | RAIPUR IRD-II | addl. Budget for new depot , details to be provided | SOD | Marketing | ECZ | 2026-06-15 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-15 | AUD-2026-05-2000012405ACN-2026-05-4000130264 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130264 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130264 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130264 | AUD-2026-05-2000012405ACN-2026-05-4000130264 | 21 | 21 | 27 | 80 | 3 | 3 | 41 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | Location is continue to resolve the issues of transporter and delear by one to one meeting and continue to schedule delear/transpoerter meet. | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127194 | Closed | KAMLESH SAHU | 2026-05-07 | 1) Lack of Co-ordination : Dealers raised concern that at times they are not able to contact to depot officials to address their queries. It was advised to send their queries thru whatsapp as seperate whatsapp group is created for TT information. 2) VTS blockingof TT : DCT transporters enquired about issue of VTS blocking. It was informed to them that, if loaded TT does not follow approved route, it will get blocked. If transporters feel there is issue with approved route, they may get it changed from field officer withthe help of terminal officials. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1528 | RAIPUR IRD-II | Advised location to have frequent meeting with dealears / transporters to sort out their issues if any | SOD | Marketing | ECZ | 2026-03-25 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011236ACN-2026-03-4000127194 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127194 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127194 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127194 | AUD-2026-03-2000011236ACN-2026-03-4000127194 | 21 | 21 | 26 | 80 | 3 | 3 | 30 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | Shortcoming was address to Transporter and compliance has been updated and implimented | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127192 | Closed | KAMLESH SAHU | 2026-05-07 | Thorough checking of one TT was carried out with Safety Officer and Operation Officer. The shortcomings were advised to the TT crewfor compliance. | 3.1 | TT fittings & discipline checked | 1528 | RAIPUR IRD-II | Advised officer to ensure compliance before loading the TT in its next trip | SOD | Marketing | ECZ | 2026-03-25 | THIRD PARTY ERRORS | 6 | CONTRACTOR SAFETY | S2 | F3 | 2026-03-25 | AUD-2026-03-2000011236ACN-2026-03-4000127192 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127192 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127192 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011236ACN-2026-03-4000127192 | AUD-2026-03-2000011236ACN-2026-03-4000127192 | 21 | 21 | 26 | 80 | 3 | 3 | 30 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | CBAC IS COMMISSIONED AND FUNTIONAL NOW | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127191 | Closed | KAMLESH SAHU | 2026-07-17 | CBAC Systen was functional along with Biomatric operational at Maingate, Entry to Licence area and Control room. The system is not yet handed over by E&P to Operation Team. | 2.8 | Access control systems checked | 1528 | RAIPUR IRD-II | Following up with E&P for making CBAC functional | SOD | Marketing | ECZ | 2026-04-30 | THIRD PARTY ERRORS | 3 | PROCESS SAFETY | S3 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127191 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127191 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127191 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127191 | AUD-2026-03-2000011236ACN-2026-03-4000127191 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | 1) Positioning of Emergency trolly at Railway Siding-Completed 2) Visibility of ESD in all direction - Completed 3) Removal of obstructions for free movement of people - Removed 4) Frequent carrying out Fire Drills - After 13 Jan 26, drills are conducted on following dates 29 Jan 26, 7 feb 26, 25 feb 26, 30 March 26, 06 April 26 & 28 April 26 | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127188 | Closed | KAMLESH SAHU | 2026-05-07 | Surprised mock fire drill was carried out at extreme end of Railway siding. The responses and shortcomings were discussed with all the participants team. The shortcomings such as positioning of Emergency trolly at far away from Railway siding area, visibility of ESD from only one direction instead of all directions, Due to some ongoing civil work sand was lying at few patches obstructing the road movement, delay in communication of emergency over VHF. Advised location for carrying out more mock fire drill on weekly/fortnightly basis covering remaining various scenario. | 2.5 | Emergency response preparedness reviewed | 1528 | RAIPUR IRD-II | 1) Positioning of Emergency trolly at Railway Siding 2) Visibility of ESD in all direction 3) Removal of obstructions for free movement of people 4) Frequent carrying out Fire Drills | SOD | Marketing | ECZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 2 | EMERGENCY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127188 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127188 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127188 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127188 | AUD-2026-03-2000011236ACN-2026-03-4000127188 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | Achieved Lux level inside gantry is 112 against 100 requirement | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127187 | Closed | KAMLESH SAHU | 2026-05-07 | Lux levels was checked at TT Gantry, peripheral road and admin building area. The inadequate lux level at TT gantry was brought to the attention of location for necessary corrective action. The reason for inadequate lux at TT gantry was due to damages in ELDB power cable, which is now rectified and restored back. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1528 | RAIPUR IRD-II | The reason for inadequate lux at TT gantry was due to damages in ELDB power cable, which is now rectified and restored back. | SOD | Marketing | ECZ | 2026-03-25 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-25 | AUD-2026-03-2000011236ACN-2026-03-4000127187 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127187 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127187 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127187 | AUD-2026-03-2000011236ACN-2026-03-4000127187 | 21 | 21 | 26 | 80 | 3 | 3 | 30 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | After 13 Jan 26, drills are conducted on following dates 29 Jan 26, 7 feb 26, 25 feb 26, 30 March 26, 06 April 26 & 28 April 26 | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127186 | Closed | KAMLESH SAHU | 2026-05-07 | Only single fire contingency scenario was simulated at Railway siding. | 2.2 | Double contingency scenario simulated; observations recorded | 1528 | RAIPUR IRD-II | Frequency of carrying out Fire Drills to be increased | SOD | Marketing | ECZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 2 | EMERGENCY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127186 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127186 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127186 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127186 | AUD-2026-03-2000011236ACN-2026-03-4000127186 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | 1) Positioning of Emergency trolly at Railway Siding-Completed 2) Visibility of ESD in all direction - Completed 3) Removal of obstructions for free movement of people - Removed 4) Frequent carrying out Fire Drills - After 13 Jan 26, drills are conducted on following dates 29 Jan 26, 7 feb 26, 25 feb 26, 30 March 26, 06 April 26 & 28 April 26 | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127185 | Closed | KAMLESH SAHU | 2026-05-07 | Surprised mock fire drill was carried out at extreme end of Railway siding. The responses and shortcomings were discussed with all the participants team. The shortcomings such as positioning of Emergency trolly at far away from Railway siding area, visibility of ESD from only one direction instead of all directions, Due to some ongoing civil work sand was lying at few patches obstructing the road movement, delay in communication of emergency over VHF. Advised location for carrying out more mock fire drill on weekly/fortnightly basis covering remaining various scenario. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1528 | RAIPUR IRD-II | 1) Positioning of Emergency trolly at Railway Siding 2) Visibility of ESD in all direction 3) Removal of obstructions for free movement of people 4) Frequent carrying out Fire Drills | SOD | Marketing | ECZ | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127185 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127185 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127185 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127185 | AUD-2026-03-2000011236ACN-2026-03-4000127185 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 46
YADAV GIRISH KUMAR | 2026-07-17 | KAMLESH SAHU | 2026-05-07 | Urgent po has been placed and some work has been completed before OISD Audit in feb-2026 | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127183 | Closed | KAMLESH SAHU | 2026-05-07 | Zonal support sought as mentioned above, was extended and ensured placement of pending Pos. | 1.5 | HQO / Zonal support required identified | 1528 | RAIPUR IRD-II | Matter taken up with CPO by Zonal O&D Head for expediting placement of PO | SOD | Marketing | ECZ | 2026-04-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127183 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127183 | 2026-08-28 18:00 | 52.0038 | 319 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127183 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127183 | AUD-2026-03-2000011236ACN-2026-03-4000127183 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-16 | VA alerts have been significantly minimized through regular TT crew training, daily gate meetings, enhanced supervision, and continuous monitoring of alert trends. TT crews are being regularly trained during daily gate meetings on proper placement of wheel chocks and fire extinguishers at the designated locations before loading/unloading operations. Awareness on compliance with PPE and safety harness requirements has been reinforced. Security personnel have been instructed to monitor and prevent perimeter intrusion and intrusion during non-working hours. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127330 | Closed | KUMAR GOPESH | 2026-07-16 | VA alerts checked for the period 01.12.2025 to 26.01.2026. The observations are: 1. Non compliance towards wheel choke: No. of total alerts vs false alert: 81/30 2. Non compliance towards Fire ext: No. of total alerts vs false alert: 39/11 3. Non compliance towards safety harness: No. of total alerts vs false alert: 18/0 4. Non compliance towards PPE: No. of total alerts vs false alert: 33/1 5. Emergency gate opening: 4/0 6. TT crew not there: 3/3 7. Permiter intrusion: 71/25 8. Intrucsion in non workinh hour: 82/12 | 2.7 | VA alerts checked / analysed | 1281 | AJMER TERMINAL | No. of alerts are in higher side. Location to take corrective action | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127330 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127330 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127330 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127330 | AUD-2026-03-2000011239ACN-2026-03-4000127330 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-16 | During Tank Truck (TT) checking, it was observed that all Tank Trucks being loaded at the terminal are carrying the required branding as per the Transport Tender Terms & Conditions. It has been clearly communicated to all transporters that only properly branded Tank Trucks will be permitted for loading. Any TT found without the prescribed branding will not be allowed to load until the branding is completed in accordance with the tender requirements. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127334 | Closed | KUMAR GOPESH | 2026-07-16 | Checked for three Tts and found okay. Branding of TTs to be improved | 3.1 | TT fittings & discipline checked | 1281 | AJMER TERMINAL | Pls ensure that TT crew branding is completed inline with transport tender terms and conditions. | SOD | Marketing | NWF | 2026-04-30 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127334 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127334 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127334 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127334 | AUD-2026-03-2000011239ACN-2026-03-4000127334 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-16 | **Compliance / Corrective Action Taken (Point-wise):** 1. **Overall Housekeeping:** Complied. Overall housekeeping is being maintained in good condition. 2. **Drain Surrounding the Gantry:** Complied. The drain surrounding the gantry is being cleaned regularly. 3. **Cleaning of Pipelines, TAS Equipment & Structures:** Complied. One dedicated contract workman has been deployed for daily cleaning of pipelines, TAS equipment, structures, and all tank farm facilities using detergent and a wet cloth. 4. **Gantry Area & UG Tank Farm Area:** Complied. Regular housekeeping is being carried out, and these areas are being cleaned on a daily basis. 5. **Tank Farm Area:** Complied. The tank farm area is being cleaned daily by the dedicated housekeeping workman to maintain good housekeeping standards. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127338 | Closed | KUMAR GOPESH | 2026-07-16 | Overal Housekeeping was good. Drain surrounding the gantry not clean. One contract workman should regularly clean pipeline, TAS equipment, structures through detergent and wet cloth. Gantry area, UG tank farm area are not clean. Tank farm areas are clean. Disposal of old documents as per circular to be done. | 3.15 | Housekeeping & PPE usage checked | 1281 | AJMER TERMINAL | Location to ensure. One bay to be identified for renovation of green gantry | SOD | Marketing | NWF | 2026-05-31 | INSUFFICIENT SUPERVISION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-05-31 | AUD-2026-03-2000011239ACN-2026-03-4000127338 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127338 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127338 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127338 | AUD-2026-03-2000011239ACN-2026-03-4000127338 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-16 | The history cards of CCTV, HVLR, RSFPS, Pumps, Tanks, and VRU have been updated with all maintenance/visit details. Details of all replaced parts, including those replaced at no cost to HPCL, have also been recorded. The updated history cards have been shared with NWFZ via email as requested | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127342 | Closed | KUMAR GOPESH | 2026-07-16 | History card of CCTV, HVLR, RSFPS, Pumps, Tanks, VRU should be updated properly. Location should update all visit details in History card. If any parts are replaced (even if cost is not borne by HPCL), pls mention that in history card. | 6.4 | History card | 1281 | AJMER TERMINAL | Pls update all details including visit of OEM, any servicing done, any filter changed. Even if material changed is under the scope of CAMC vendor, pls write name of material changed and associated cost | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | ASSET INTEGRITY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127342 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127342 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127342 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127342 | AUD-2026-03-2000011239ACN-2026-03-4000127342 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-16 | 1. Transporters' Meeting Conducted: A Transporters' Meeting was conducted on 19.06.2026, attended by 8–9 transporters. The requirements of ITDG 5.0, VTS Violation SOP, route compliance, unauthorized stoppages, TT blocking, and the actions to be taken for violations were discussed in detail. 2. Unauthorized Stoppage Review: A follow-up meeting with transporters was conducted on 14.07.2026 to specifically address the issue of multiple loaded TTs making unauthorized stoppages at the same location. Transporters were instructed to ensure strict route compliance and avoid unauthorized halts. 3. Physical Verification of Suspected Locations: Ajmer Terminal officials carried out physical verification of the suspected stoppage locations on 10.07.2026 to validate VTS observations and identify the reasons for repeated TT stoppages. 4. Dealer Awareness through VC: An online Dealer VC was conducted on 16.07.2026, attended by more than 91 dealers. The meeting covered VTS violations, TT blocking, EM lock-related issues, and the responsibilities of dealers in ensuring timely unloading and preventing unnecessary TT detention. 5. Explanation from Transporters: Explanations have been sought from the concerned transporters for VTS deviations. Cases of repeated unauthorized stoppages are being monitored, and furtheraction will be taken as per the applicable SOP, including administrative action and stoppage of TT loading in case of non-compliance. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127336 | Closed | KUMAR GOPESH | 2026-07-16 | List of VTS deviations for the period 05.01.2026 to 22.02.2026 shared with locations by Zone. There are cases where route corrections may be required. Multiple loaded Tts are stopping at one place. Location is required to take explanation from transporter. If explanation is not satisfactory, location needs to take up with Administration, including SP. If concerned DCT or transporter is not giving reply of our letter and their TT is still stopping at that place, then TT loading has to be stopped. | 3.3 | VTS deviations reviewed | 1281 | AJMER TERMINAL | Location to take corrective action and revert. | SOD | Marketing | NWF | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127336 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127336 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127336 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127336 | AUD-2026-03-2000011239ACN-2026-03-4000127336 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-04 | 1. complied 2. Tf 4 ROSOV cable issue rectified. For MOV, PO placed and issue recified for operational MOVs. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127324 | Closed | KUMAR GOPESH | 2026-07-04 | Two points of SSA, Sept 2025 are still pending to be complied: 1. CP system is not functional for all 14 tanks foundations. 2. MOV's of all above ground tanks are not opening from control room (not opening in remote). Feedback issue in ROSOV of tank No 4,5,6,11&12 recirculation line | 1.3 | Pending issues reviewed | 1281 | AJMER TERMINAL | Pls ensure compliance of both the points. | SOD | Marketing | NWF | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 9 | ASSET INTEGRITY | S3 | F3 | 2026-04-15 | AUD-2026-03-2000011239ACN-2026-03-4000127324 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127324 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127324 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127324 | AUD-2026-03-2000011239ACN-2026-03-4000127324 | 21 | 21 | 26 | 80 | 0 | 0 | 33 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-04 | Regular monitoring of audit observations is being carried out, with periodic reviews to ensure timely compliance and closure of allaudit points. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127325 | Closed | KUMAR GOPESH | 2026-07-04 | Comprehensive audit conducted. Out of 11 audit points, 8 points are pending. TAS audit compliance: 2 points of TAS audit date 12.12.2024 and 5 points of TAS audit date 26.12.2025, are still pending to be complied | 1.4 | Earlier acThe comprehensive audit observations have been addressed. All pending audit points, including 2 points from the TAS Auditdated 12.12.2024 and 5 points from the TAS Audit dated 26.12.2025, have been complied with and closed.tion points status checked | 1281 | AJMER TERMINAL | Time bound action plan is to be maintained | SOD | Marketing | NWF | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011239ACN-2026-03-4000127325 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127325 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127325 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127325 | AUD-2026-03-2000011239ACN-2026-03-4000127325 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 46
DINKAR SUMIT | 2026-07-18 | KUMAR GOPESH | 2026-07-04 | The location has focused on improving operational parameters, resulting in a significant improvement in CAT-A performance. Similarly, continued emphasis has been placed on enhancing the first two-hour loading performance and TT cycle time to achieve further operational efficiency. improvments | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127326 | Closed | DINKAR SUMIT | 2026-07-18 | Yes. Location to focus on improvement of operational parameters. There is good improvemebt in CAT-A performance. Similarly, location needs to focus on 1st two hr loading performance and cycle time | 1.8 | Improvement plans discussed-The location has focused on improving operational parameters, resulting in a significant improvement inCAT-A performance. Similarly, continued emphasis has been placed on enhancing the first two-hour loading performance and TT cycle time to achieve further operational efficiency. | 1281 | AJMER TERMINAL | Location is requested to bifurcate cycle time into three components, Bay queue time, Loading time and exit time. Location needs to watch these three time component on daily basis and analyse the problem. A weekly data should be shared by location with undersign. Location should aim for 4 TTs per bay per two hr in 1st two hr. | SOD | Marketing | NWF | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-31 | AUD-2026-03-2000011239ACN-2026-03-4000127326 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127326 | 2026-09-09 17:45 | 40.0143 | 320 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127326 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127326 | AUD-2026-03-2000011239ACN-2026-03-4000127326 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Daily efforts by STL team is given on improving Solar Performance, Dormant Keys, SSA /MDSA compliance, CCTV, Dip Elimination File note, M&I Projects | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129554 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1919 | SECUNDERABAD TERMINAL | Solar Performance, Dormant Keys, SSA /MDSA compliance, CCTV, Dip Elimination File note, M&I Projects | SOD | Marketing | SCR | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-05-2000012102ACN-2026-05-4000129554 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129554 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129554 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129554 | AUD-2026-05-2000012102ACN-2026-05-4000129554 | 21 | 21 | 27 | 80 | 1 | -12 | 48 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Transporter of TS08UK2052 advised to complete the required branding and submit the 3M branding certificate for verification at the earliest. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129557 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Branding is not available for TT No. TS08UK2052. Checked for TT Number TS08UK5099, TS07UK4425 and found ok. | 3.1 | TT fittings & discipline checked | 1919 | SECUNDERABAD TERMINAL | Branding for TT No TS08UK 2052 to be completed . | SOD | Marketing | SCR | 2026-05-20 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129557 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129557 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129557 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129557 | AUD-2026-05-2000012102ACN-2026-05-4000129557 | 21 | 21 | 27 | 80 | 1 | -12 | 38 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Issue taken up with VVSPL for completion of calibration and commencing of MFM based accounting on 15.06.2026. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-05-4000129561 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | MFM based accounting not being done . VVSPL MFM to be calibrated , Hence, PLT booking presenlty done thru manual tank dips. | 5.1 | MFM based accounting at Pipeline and OMC location | 1919 | SECUNDERABAD TERMINAL | To take up with VVSPL for completion of calibration and commencing of MFM based accounting | SOD | Marketing | SCR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-05-2000012102ACN-2026-05-4000129561 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129561 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129561 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129561 | AUD-2026-05-2000012102ACN-2026-05-4000129561 | 21 | 21 | 27 | 80 | 1 | -12 | 44 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | SSA is being done by location and continuous discussion is being held for gap observed in line with OISD audit preparation action plan | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129563 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | OISD audit is due for Terminal and preparations for audit to be made. | 6.2 |  | 1919 | SECUNDERABAD TERMINAL | OISD audit preparation action plan to be given and additional documents to be verified. | SOD | Marketing | SCR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-05-2000012102ACN-2026-05-4000129563 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129563 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129563 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129563 | AUD-2026-05-2000012102ACN-2026-05-4000129563 | 21 | 21 | 27 | 80 | 1 | -12 | 44 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Open sales order, DC and OBD are being monitored periodically. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129564 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Open sales order, DC and OBD. | 6.3 |  | 1919 | SECUNDERABAD TERMINAL | Open sales order, DC and OBD. | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129564 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129564 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129564 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129564 | AUD-2026-05-2000012102ACN-2026-05-4000129564 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Intelligent Key usage being done by LIC regularly | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129566 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Intelligent Key usage by LIC regularly | 6.5 |  | 1919 | SECUNDERABAD TERMINAL | Intelligent Key usage by LIC regularly | SOD | Marketing | SCR | 2026-05-15 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-15 | AUD-2026-05-2000012102ACN-2026-05-4000129566 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129566 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129566 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129566 | AUD-2026-05-2000012102ACN-2026-05-4000129566 | 21 | 21 | 27 | 80 | 1 | -12 | 37 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | Shortage Bookings being analyzed along with VTS route deviation, Stoppages being monitored on daily basis | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129569 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Shortage Bookings to be analyzed – VTS route deviation, Stoppage | 6.8 |  | 1919 | SECUNDERABAD TERMINAL | Shortage Bookings to be analyzed – VTS route deviation, Stoppages to be monitored on daily basis | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129569 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129569 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129569 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129569 | AUD-2026-05-2000012102ACN-2026-05-4000129569 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 46
NIDAMARTHI NAGA KIRAN | 2026-07-18 | SATYENDRA CHOURASIA | 2026-07-15 | VRU Pipe installed at Bay 10. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129570 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Bay Number 10 VRU hose installation works pending | 6.9 |  | 1919 | SECUNDERABAD TERMINAL | Bay Number 10 VRU hose to be completed. | SOD | Marketing | SCR | 2026-06-15 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-15 | AUD-2026-05-2000012102ACN-2026-05-4000129570 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129570 | 2026-08-06 19:00 | 73.9622 | 320 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129570 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129570 | AUD-2026-05-2000012102ACN-2026-05-4000129570 | 21 | 21 | 27 | 80 | 1 | -12 | 41 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Job has been completed | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128576 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | TW PH to be made as sunken reservoir for removal of storm water from Terminal specially during rainy season. This is also one of audit points. All scraps to be disposed for which RFD approved. RFD to be prepared for e-waste items. | 1.8 | Improvement plans discussed | 1233 | BHARATPUR TERMINAL | Job to be completed. | SOD | Marketing | NWF | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128576 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128576 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128576 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010749ACN-2026-04-4000128576 | AUD-2026-04-2000010749ACN-2026-04-4000128576 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Live fire fighting training with local fire dept was conducted | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128584 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes. Rahul and Neetesh to be involved in understanding all fire fighting system. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1233 | BHARATPUR TERMINAL | Training to be enhanced for operation of all fire fighting facilities | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128584 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128584 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128584 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128584 | AUD-2026-04-2000010749ACN-2026-04-4000128584 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | SOP displayed and marking on road has been done | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128585 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Checked. Further training is required for TT crew. A board in Hindi is displayed at TT gantry area which stipulates actions to be taken by TT crew in case of an emergency both inside and outside terminal premise. However, location officer needs to further enhancethe same. Few TT crew were not aware of TREM card | 2.15 | TT crew roadside emergency procedures checked | 1233 | BHARATPUR TERMINAL | Training program to be arranged as refresher course. | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128585 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128585 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128585 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128585 | AUD-2026-04-2000010749ACN-2026-04-4000128585 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  |  | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128577 | Closed |  |  | Equipment worked well. All personnel reached timely at site. Siren was timely actuated. LIC was coordinating by using mike. Foam blanket was made properly. LEL was checked after extinguishing fire. ESD operated. Emergency kit trolley was brought to the site. Area of improvements: 1. There was poor coordination between team leaders and Fire Chief. Team leader should ask and communicate the development during fire drill. That was absent. 2. One WCFM was operated by team member. however, consent of fire chief not taken. 3. As TT valve box was not accessible easily, throw of WCFM was not reaching to actual site of fire. Fire hose was not used initially. Afterwards, fire hose was laid, however, not used. 4. Ambulance not arranged. No Mutual aid members reported. Even pipeline officers also didn't report to site. 5. TT movement/evacuation was in disordered manner. No clear action plan. No coordination. 6. TT crew were moving around. Evacuation of persons were not good. 7. Fire was simulated in valve box, however. communication was given that fire took place in battery of TT. | 2.2 | Single contingency scenario simulated as fire in valve box of one of the tank truck standing in TT parking | 1233 | BHARATPUR TERMINAL | Pls ensure that shortcomings are not repeated. Increase awareness among team members by continuous training. | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 15 | PROCESS SAFETY | S3 | F5 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128577 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128577 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128577 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128577 | AUD-2026-04-2000010749ACN-2026-04-4000128577 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Lux level improved | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128578 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Checked. Lux level was not meeting in tank farm area, PH, TLF gantry, ETP and on road. There is similar audit point in comprehensive audit conducted in Sept 2025. Location is advised to comply. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1233 | BHARATPUR TERMINAL | Pls ensure closure of audit point related to insuff. Lux level. | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128578 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128578 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128578 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128578 | AUD-2026-04-2000010749ACN-2026-04-4000128578 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | drills increased in q1 only two L2 drills conducted | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128579 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes reviewed. Location was advised to ensure that drill is conducted at all locations and all types of risk scenarios are covered as mentioned in ERDMP. | 2.5 | Emergency response preparedness reviewed | 1233 | BHARATPUR TERMINAL | Location to confirm for the same with list of locations and risk scenarios mentioned in ERDMP | SOD | Marketing | NWF | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128579 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128579 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128579 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128579 | AUD-2026-04-2000010749ACN-2026-04-4000128579 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | cbacs visitor pass is being used | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128580 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes CCTV camera checked. All CCTVs were working. Security alertness was checked. Cross checked with security about safety briefing,frisking, visitor management. New Security supervisor needs to be trained. Security was also asked to explain TAS display positioned at security gate. They explained properly. Location should issue visitor pass (red for entry to licence area and green for entry to Admin bldg ony0 | 2.6 | CCTV functioning checked | 1233 | BHARATPUR TERMINAL | Pls implement visitor pass | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128580 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128580 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128580 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128580 | AUD-2026-04-2000010749ACN-2026-04-4000128580 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | VA alerts are being monitired thru NOVEX | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128581 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | VA alerts were checked for 1st March to 31st March 2026. Pls find the report: 1. Wheel choke not positioned: 52, False alert; 38, Actual non conformity: 14 2. Unauthorised opening of Emergency gate: 17, False alert: 2, Actual NC: 15 3. Fire ext not placed infront of TT: 34, False alert: 32, Atual non conformity: 2 4. TT crew not available in TT at gantry: 1, False alert: 1, Actual NC: 0 | 2.7 | VA alerts checked / analysed | 1233 | BHARATPUR TERMINAL | Needful action to be taken by location | SOD | Marketing | NWF | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128581 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128581 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128581 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128581 | AUD-2026-04-2000010749ACN-2026-04-4000128581 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Housekeeping imporved | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128586 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Housekeeping needs to be improved. Grass growth was unusually high. | 3.15 | Housekeeping & PPE usage checked | 1233 | BHARATPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128586 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128586 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128586 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128586 | AUD-2026-04-2000010749ACN-2026-04-4000128586 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | all the earthpits crosschecked | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128587 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Total 5 nos.of earth pits were checked. Observations are: 1. Soil level was high in one earth pit. 2. Funnel net was damaged in one case. 3. Nut was loose. As OISD audit is scheduled. Location has been advised to take 10 earth pits in a day. Check all 223 earth pits one by one. Clean the pits, paint the rusted portion with GI paint, apply grease on nut bolt to avoid corrosion, There should be complete lap joint between two strip without any air gaps. | 3.16 | Earth pits / boundary / vegetation control checked | 1233 | BHARATPUR TERMINAL | Location is requested to share monthly progress on Earth pits checked | SOD | Marketing | NWF | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128587 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128587 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128587 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128587 | AUD-2026-04-2000010749ACN-2026-04-4000128587 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Culture for MOCs has been improved | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128588 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | MOC not taken for ATF tank conversion. MOC not taken for ATF bay conversion. MOC to be taken for repair of one DG. | 3.17 | MOC status reviewed | 1233 | BHARATPUR TERMINAL | MOC to be taken timely | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128588 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128588 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128588 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128588 | AUD-2026-04-2000010749ACN-2026-04-4000128588 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 46
SUDHIR KUMAR | 2026-07-20 | SHETTY ANURANJAN | 2026-07-20 | Implementation in progress, majority have been complete. Specific issues pertaining to individual toll plazas are being taken up individually. The job is a continuous and needs close coordination with Toll Plaza, Transporters including DCT and PIU NHAI. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125409 | Closed | SHETTY ANURANJAN | 2026-07-20 | Discounted toll to be implemented | 6.10 | Discounted toll | 1242 | JAIPUR TERMINAL | There is Gazette notification. Email shared with location on discounted toll concept. Pls implement | SOD | Marketing | NWF | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011022ACN-2026-03-4000125409 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125409 | 2026-09-30 | 19.7538 | 322 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125409 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125409 | AUD-2026-03-2000011022ACN-2026-03-4000125409 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 46
SUDHIR KUMAR | 2026-07-20 | SHETTY ANURANJAN | 2026-07-20 | SOP boards displayed in Hindi. | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125412 | Closed | SHETTY ANURANJAN | 2026-07-20 | It is observed that many SOP boards are displayed in English language only. These SOPs cannot be understood by many contract staffswhoc are having good knowledge and experience. Pls convert these SOP boards in Hindi | 6.13 | SOP Boards | 1242 | JAIPUR TERMINAL | SOP boards written in English only, should be displayed in Hindi. | SOD | Marketing | NWF | 2026-06-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011022ACN-2026-03-4000125412 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125412 | 2026-09-30 | 19.7538 | 322 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125412 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125412 | AUD-2026-03-2000011022ACN-2026-03-4000125412 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Jobs have been completed | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128589 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Taken. Pls find observation points 1. Curb wall behind TTG with drain connected to drain. 2. BAE to be removed (MS & Ethanol) 3.Arrow marking of TT movement at TTG 4. Emergency SOP for TTG for evacuation of TT during emergancy. 5. Pump Emergency stop not working from TT gantry 6. Drain to be extended near ATF filter 7. Area wise earth pit layout diagram after verification. 8. LPS at ATF PH, oversize gland at ATF PH. 9. Unused pipeline to be removed from TWD PH and manifold area near rail gate 10. Tree trimming at various places shown | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1233 | BHARATPUR TERMINAL | Pls take corrective actions | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128589 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128589 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128589 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128589 | AUD-2026-04-2000010749ACN-2026-04-4000128589 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | required jobs have been completed | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128590 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes. Location was thoroughly inspected for continuous three days with respect to preparation towards ESA along with Sr. Manager, HSE, M&I and Proj. Total 274 minor and major points were noted. Location is requested to carry out compliance in war footing basis. List of jobs is mentioned in email from LIC dt 21.04.2026 | 4.2 | Maintenance activities reviewed | 1233 | BHARATPUR TERMINAL | Pls take corrective actions | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128590 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128590 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128590 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128590 | AUD-2026-04-2000010749ACN-2026-04-4000128590 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | E waste RFD has been completed | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128592 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Scrap disposal RFD is approved. Physical disposal is to be done latest by this month end. E-RFD is pending for e-waste items | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1233 | BHARATPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128592 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128592 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128592 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128592 | AUD-2026-04-2000010749ACN-2026-04-4000128592 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | valves are being kept in open position | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128595 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Float system in HVLR foam tanks to be implemented | 6.5 | Handling emergency | 1233 | BHARATPUR TERMINAL | 2 inch valve on foam line leading to daughter tank of HVLR tank, needs to be kept in open condition. Pls ensure float system | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128595 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128595 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128595 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128595 | AUD-2026-04-2000010749ACN-2026-04-4000128595 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | gantry curb wall and ETP outlet has been routed to TWD sunken pump house | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128596 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Job is under progress | 6.6 | Drainage system | 1233 | BHARATPUR TERMINAL | XX | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128596 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128596 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128596 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128596 | AUD-2026-04-2000010749ACN-2026-04-4000128596 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | monthly monitoring has been done | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128597 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Good control. However, as per location there were 18 RTGP pending. As per security, 22 RTGPs were pending. This needs to be verified. | 6.7 | RTGP monitoring | 1233 | BHARATPUR TERMINAL | Monthly monitoring of RTGP by security to be done | SOD | Marketing | NWF | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128597 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128597 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128597 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128597 | AUD-2026-04-2000010749ACN-2026-04-4000128597 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Timly required | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122544 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes. Rahul and Neetesh to be involved in understanding all fire fighting system. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1233 | BHARATPUR TERMINAL | Training to be enhanced for operation of all fire fighting facilities | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122544 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122544 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122544 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122544 | AUD-2026-03-2000011210ACN-2026-03-4000122544 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Continuous drills have been practice | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122541 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | a) HSEofficer acted as SIC, all three teams demonstrated their activities in presence of alternate team leaders. b) Fire fighting equipment operated – DCP FE – 02 numbers, Foam trolley, WCFM – 03 numbers, water curtain, RKPL Fire Tender. Performance of all equipment was found satisfactory. c) Demonstration of spillage barrier use, Emergency trolley and ERV for product suction, use of SCABA and LEL checking with fire proximity suit was made during the drill d) Ambulance, RKPL team with Foam tender and Mutual Aid membersreported promptly. e) Following shortcomings were pointed out – i. Communication between team members was found lacking in the initial phase of drill ii. Use of megaphone by SIC for communication to be ensured. iii. TT’s were instructed not to move from site in view of product spillage, but after the declaration of fire also TT crew remained near TT’s. iv. Auxiliary team didn’t prepare hose line with portable foam nozzle. v. Water spray for cooling of nearby bays continued during foam blanket formation | 2.2 | Double contingency scenario simulated; observations recorded | 1233 | BHARATPUR TERMINAL | Pls ensure that shortcomings are not repeated. Increase awareness among team members by continuous training. | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122541 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122541 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122541 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122541 | AUD-2026-03-2000011210ACN-2026-03-4000122541 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  |  | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122542 | Closed |  |  | Checked. Lux level was not meeting in tank farm area. There is similar audit point in comprehensive audit conducted in Sept 2025. Location is advised to comply. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1233 | BHARATPUR TERMINAL | Pls ensure closure of audit point related to insuff. Lux level. | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122542 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122542 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122542 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122542 | AUD-2026-03-2000011210ACN-2026-03-4000122542 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Local loadings have been checked | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122545 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Checked. Local loading of Dec 25. There are 76 cases of local loading. Out of 76 cases, 12 cases are for prover tank checking, RKPLuse/own use. Balance 64 cases, Tts were loaded locally for small quantities ranging from 5 liter to 63 liter | 3.14 | Local loading checks (if applicable) | 1233 | BHARATPUR TERMINAL | No. of local loading cases are high. It needs to be reduced | SOD | Marketing | NWF | 2026-03-05 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-05 | AUD-2026-03-2000011210ACN-2026-03-4000122545 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122545 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122545 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122545 | AUD-2026-03-2000011210ACN-2026-03-4000122545 | 21 | 21 | 26 | 80 | 2 | 1 | 27 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Housekeeping has been improved | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122546 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Gantry equipments, gantry pipeline, structures are to be cleaned on daily basis, with soap detergent. One dedicated housekeeping manpower to be deployed for gantry | 3.15 | Housekeeping & PPE usage checked | 1233 | BHARATPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122546 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122546 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122546 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122546 | AUD-2026-03-2000011210ACN-2026-03-4000122546 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Earth pits have been checked | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122547 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | As OISD audit is due this year, location is advised to check all earth pits. Before carrying out maintenance job in earth pit, one officer has to go through all design spec for Earth pit as per IS 3043 and OISD 244. | 3.16 | Earth pits / boundary / vegetation control checked | 1233 | BHARATPUR TERMINAL | Location is requested to share monthly progress on Earth pits checked | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000011210ACN-2026-03-4000122547 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122547 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122547 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122547 | AUD-2026-03-2000011210ACN-2026-03-4000122547 | 21 | 21 | 26 | 80 | 2 | 1 | 44 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  |  | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122549 | Closed |  |  |  | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1233 | BHARATPUR TERMINAL | Dealers reported issues of non-receipt of SMS’s, problems in use of MyfleetVigil app. It is advuised to conduct awareness program to use my Vigil App by dealers to the maximum extent. Report of such programs should be shared with us. Location may also share leaflet, short video on My Vigil App so that it becomes user friendly for them. | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011210ACN-2026-03-4000122549 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122549 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122549 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122549 | AUD-2026-03-2000011210ACN-2026-03-4000122549 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | all the activities have been done | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122700 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Taken. Pls find observation points d) Ethanol Header is having HOV, MOV to be installed at the earliest e) Drain near sample point to be covered with grating f) Site SOP in Hindi for foam system to be displayed along with valve numbers g) Simplified ETP process in Hindi to be displayed in ETP area h) Mesh to be provided in outlet pipe near Tertiary valve near boundary wall i) Concertinacoil at the corner towards railway siding to be repaired j) Submersible pump to be checked for use in UG tank k) All items in thestore to be inventoried, classified and marked l) Gantry headers to be cleaned | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1233 | BHARATPUR TERMINAL | Pls take corrective actions | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011210ACN-2026-03-4000122700 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122700 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122700 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122700 | AUD-2026-03-2000011210ACN-2026-03-4000122700 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | Scrap has been uplifted till OISD | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122703 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Location to identify all scrap items and process RFds. Location has to be scrap free by 31st March 2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1233 | BHARATPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | ENVIRONMENTAL | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122703 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122703 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122703 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122703 | AUD-2026-03-2000011210ACN-2026-03-4000122703 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | RTGP monthly monitoring is being done | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122708 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Pending RTGP record (month wise) to be parepared on RTGP register itself. List of open RTGP as per security vs list of open RTGP asper online gate pass portal | 6.7 | RTGP monitoring | 1233 | BHARATPUR TERMINAL | Monthly monitoring of RTGP by security to be done | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122708 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122708 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122708 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122708 | AUD-2026-03-2000011210ACN-2026-03-4000122708 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000144048 | Open |  |  | Timelines for the closure of Technical and MDSA observations. The scrap disposal activity has also been completed during FY 25-26 resulting in Rs.13 lakhs of amount generated through disposal. | 1.4 | Earlier action points status checked | 1991 | CHENNAI TERMINAL | An old TT is lying near VRU. Valuation report has been obtained. Location to process RFD and dispose off the asset. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144048 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144048 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144048 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144048 |  | AUD-2026-07-2000015443ACN-2026-07-4000144048 | 21 |  | 27 | 80 | 42 | 42 | 57
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000144049 | Open |  |  | Chennai Terminal Revamp has been approved by Board in Apr'26. As per the E&P mail, revamp activities may commence from Oct'26. | 1.5 | HQO / Zonal support required identified | 1991 | CHENNAI TERMINAL | Location to revert with the plan of degassing of pipelines and handing over of Tank wagon gantry to E&P. | SOD | Marketing | SZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015443ACN-2026-07-4000144049 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144049 | 2026-06-27 | 114.7538 | 333 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144049 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144049 |  | AUD-2026-07-2000015443ACN-2026-07-4000144049 | 21 |  | 27 | 80 | 42 | 42 | 48
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000144550 | Open |  |  | Prover Tank calibration Tower needs replacement as the structure and Prover tanks are heavily corroded. | 1.5 | HQO / Zonal support required identified | 1991 | CHENNAI TERMINAL | Location to seek estimates from vendors and send proposal to Zone for review and onward submission to HQO | SOD | Marketing | SZ | 2026-08-15 |  | 4 |  | S2 | F2 | 2026-08-15 | AUD-2026-07-2000015443ACN-2026-07-4000144550 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144550 | 2026-06-27 | 114.7538 | 348 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144550 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144550 |  | AUD-2026-07-2000015443ACN-2026-07-4000144550 | 21 |  | 27 | 80 | 42 | 42 | 50
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000144551 | Open |  |  | LIC and Officers to ensure safety should be of paramount importance. Officers to take physical rounds of location and inform the shortcomings observed to Safety Officer/Maintenance and get it rectfied. | 1.8 | Improvement plans discussed | 1991 | CHENNAI TERMINAL | e-dairy implementation by location incharge and submit the same on daily basis on e-dairy portal. No. of observations recorded in e-diary. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144551 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144551 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144551 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144551 |  | AUD-2026-07-2000015443ACN-2026-07-4000144551 | 21 |  | 27 | 80 | 42 | 42 | 57
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144552 | Open |  |  | Reviewed the FY fire drill report. Location has conducted fire drills as per ERDMP scenarios. Fire drill of July month was conducted at 0800 hrs before Terminal Operations commenced. This has helped in ascertaining the preparedness of the location in absence of Officers and when only Security Guards are available. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1991 | CHENNAI TERMINAL | Location advised to ensure all ERDMP scenarios are implemented during Fire Drills. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144552 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144552 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144552 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144552 |  | AUD-2026-07-2000015443ACN-2026-07-4000144552 | 21 |  | 27 | 80 | 42 | 42 | 57
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144553 | Open |  |  | Before any TT is released in Novex, Officers review the entire route through the VTS system. Any deviations identified are examinedon a case-by-case basis with the transporter and TT crew. Further loading is permitted only after valid reasons for the deviations have been established. Wherever route corrections are required, the matter is promptly taken up with SOs. Additionally, Novex alertsgenerated through the system are regularly reviewed, and appropriate corrective actions are taken as required. | 3.3 | VTS deviations reviewed | 1991 | CHENNAI TERMINAL | Close monitoring by LIC on Speed violations and ensure that OCC Tickets are closed in time bound manner. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144553 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144553 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144553 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144553 |  | AUD-2026-07-2000015443ACN-2026-07-4000144553 | 21 |  | 27 | 80 | 42 | 42 | 57
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144554 | Open |  |  | All OISD points are complied. Pending MDSA/SSA points are complied as target dates except for the points which require to be carried out under Terminal revamp project | 3.18 | OISD/MDSA/SSA compliance reviewed | 1991 | CHENNAI TERMINAL | XX | SOD | Marketing | SZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144554 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144554 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144554 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144554 |  | AUD-2026-07-2000015443ACN-2026-07-4000144554 | 21 |  | 27 | 80 | 42 | 42 | 57
[5 empty] | Q1 2026-27 SR. MGMT INSPECTION OF CNT | 2026-06-26 17:00 | AUD-2026-07-2000015443 | 2026-06-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000144555 | Open |  |  | Location Already disposed Scrap Worth of RS.13.89 Lakhs during the year 2025-26. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1991 | CHENNAI TERMINAL | Old TT parked near VRU to be discposed off. Valuation report taken. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015443ACN-2026-07-4000144555 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015443ACN-2026-07-4000144555 | 2026-06-27 | 114.7538 | 394 | >20 | AUD-2026-07-2000015443 - ACN-2026-07-4000144555 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015443ACN-2026-07-4000144555 |  | AUD-2026-07-2000015443ACN-2026-07-4000144555 | 21 |  | 27 | 80 | 42 | 42 | 57
MEENA HEMANT KUMAR | 2026-07-20 |  |  | TTG curb wall and ETP outlet line has been laid | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122707 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Drainage system was discussed in detail. Location to make land level study to understand the slope. It was informed that ETP area and smal water reservoir area becomes full of water during rainy season. Water from ETP outlet, cannot be thrown outside as outside land is agricultural land, Farmer opposes the same. It is advised to use TW pump house (sunken PH) as water reservoir. Location needsto make RFD of all pipelines and branches of TWPH. After disposal of these unused pipelines, one pump can be used to remove water from this TWPH reservoir to outside boundary wall towards IOCL during rainy season. This area is not being used for agriculture. | 6.6 | Drainage system | 1233 | BHARATPUR TERMINAL | Location is requested to study the same and make proposal. | SOD | Marketing | NWF | 2026-04-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S2 | F3 | 2026-04-10 | AUD-2026-03-2000011210ACN-2026-03-4000122707 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122707 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122707 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122707 | AUD-2026-03-2000011210ACN-2026-03-4000122707 | 21 | 21 | 26 | 80 | 2 | 1 | 32 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | 200 DG has been repaired | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122701 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | Yes. 200 KVA DG to be repaired immediately and maintenance schedule to be displayed in field | 4.2 | Maintenance activities reviewed | 1233 | BHARATPUR TERMINAL | Pls bring DG in operating condition | SOD | Marketing | NWF | 2026-03-05 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-05 | AUD-2026-03-2000011210ACN-2026-03-4000122701 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122701 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122701 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122701 | AUD-2026-03-2000011210ACN-2026-03-4000122701 | 21 | 21 | 26 | 80 | 2 | 1 | 27 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  | repeat point 1.4 | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122548 | Closed | MEENA HEMANT KUMAR | 2026-07-20 | 1 . Self safety Audit, Set 2025: 5 points pending 2. Comprehensive audit, 23rd Sept to 27th Sept 2025: 23 points pending 3. T4S audit: 15 points pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1233 | BHARATPUR TERMINAL | Pls ensure compliance of all points except two points of CA by 31st March 2026. | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122548 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122548 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122548 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122548 | AUD-2026-03-2000011210ACN-2026-03-4000122548 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 46
MEENA HEMANT KUMAR | 2026-07-20 |  |  |  | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138491 | Closed |  |  | Yes CCTV camera checked. All CCTVs were working. CCTV are having Video Analytics System. In case, there is any detection of emergency situation in night by VA system (say permiter intrusion, any leakage of product/fire scenario), there is no alert to location in phone. Location informed that they get alert through email. However, this is not sufficent to take care of any such emergencies. | 2.6 | CCTV functioning checked | 1233 | BHARATPUR TERMINAL | Location is requested to ensure the followings: 1) A whatsapp message should come to LIC for VA alert of critical nature. 2) There is display at security room which gives visual indication of any VA alert. This needs to be rectified. SOP to be finalysed for thesame. | SOD | Marketing | NWF | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-06-2000013164ACN-2026-06-4000138491 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138491 | 2026-09-16 17:45 | 33.0143 | 322 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138491 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138491 | AUD-2026-06-2000013164ACN-2026-06-4000138491 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 46
[5 empty] | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144668 | Open |  |  | checked dip of all 4 MS tanks after closure of operation on 25.06.2026. Pls find the observation (Gross/water/temp): TK1 (MS): As per TFMS: 558.8/0/38.9/748.7 Manual dip: 558.9/0/37/745.2 Diff in L15: -3342.539 L15 TK2 (MS): As per TFMS: 1062.7/0/39.23/746.9 Manual dip: 1062.9/0/37.5/741.9 Diff in L15: -5610.825 L15 TK29 (MS) As per TFMS: 188.9/0/32.5/734.1 Manual dip: 188.8/0/39.3/743.1 Diff in L15: -4338.134 L15 UG tank TK9 (MS) As per TFMS: 43.1/0/39.57/748.3 Manual dip: 43.9/0/35/746.6 Diff in L15: -2761.250 L15 Total difference: - 16052.749 L15 | 3.7 | Inventory physical dip of minimum two tanks taken | 1278 | JODHPUR TERMINAL | There is difference in density, temp and product dip (TFMS dip vs manual dip). This was also noticed in manual control records (monthly records) maintained by location. Location needs to correct the same in coordination with vendor. Pls get approval of e-file note for TFMS SAP integration inline with circular. It needs to be renewed every 3 years. This is due for renewal | SOD | Marketing | NWF | 2026-08-31 |  | 8 |  | S2 | F4 | 2026-08-31 | AUD-2026-07-2000015346ACN-2026-07-4000144668 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144668 | 2026-09-25 20:45 | 23.8893 | 364 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144668 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015346ACN-2026-07-4000144668 |  | AUD-2026-07-2000015346ACN-2026-07-4000144668 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144682 | Open |  |  | Branding of all TTs to be ensured. On random observation branding not found good for TT no. RJ27GD5930 and RJ30GA2810 | 6.13 | Operations and Maintenance | 1278 | JODHPUR TERMINAL | Pls ensure branding of all Tts as per Corporation Visual identity policy. | SOD | Marketing | NWF | 2026-08-31 |  | 8 |  | S2 | F4 | 2026-08-31 | AUD-2026-07-2000015346ACN-2026-07-4000144682 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144682 | 2026-09-25 20:45 | 23.8893 | 364 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144682 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015346ACN-2026-07-4000144682 |  | AUD-2026-07-2000015346ACN-2026-07-4000144682 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144685 | Open |  |  | It is observed that there is no maintenance schedule for Electrical manpower. Location M&I officer to develop a maintenance schedule in coordination with Zonal M&I officer for so that electricians remain occupied for at least 4 hours in a day. | 6.16 | Maintenance schedule for electricans | 1278 | JODHPUR TERMINAL | Pls develop and implement | SOD | Marketing | NWF | 2026-07-31 |  | 8 |  | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144685 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144685 | 2026-09-25 20:45 | 23.8893 | 333 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144685 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015346ACN-2026-07-4000144685 |  | AUD-2026-07-2000015346ACN-2026-07-4000144685 | 21 |  | 27 | 80 | 0 | 0 | 48
MADHAVI LATHA KARMUNGI | 2026-07-22 | JERRY JOSEPH | 2026-05-18 | Camera Frames have been corrected. | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123415 | Closed | JERRY JOSEPH | 2026-05-18 | Yes. Suggested change in frames of camera number 72, 71 and 68 to prevent false alerts of absence of TT crew at gantry | 2.7 | VA alerts checked / analysed. Frames are getting dsturbed due to winds. Being correced regularly | 1584 | LONI TERMINAL | XX | SOD | Marketing | WZ | 2026-03-15 | HARSH WORKING CONDITIONS | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-15 | AUD-2026-03-2000011168ACN-2026-03-4000123415 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123415 | 2026-10-15 | 4.7538 | 324 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123415 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011168ACN-2026-03-4000123415 | AUD-2026-03-2000011168ACN-2026-03-4000123415 | 21 | 21 | 26 | 80 | 18 | 18 | 28 | 47
|  | JERRY JOSEPH | 2026-05-18 | 62 Lakhs worth of Scrap disposed off as per AOP target of 60 lakhs. | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123417 | Open | JERRY JOSEPH | 2026-05-18 | Yes. Advised location to dispose off scrap by 31-03-2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1584 | LONI TERMINAL | XX | SOD | Marketing | WZ | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011168ACN-2026-03-4000123417 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123417 | 2026-10-15 | 4.7538 | 211 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123417 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011168ACN-2026-03-4000123417 |  | AUD-2026-03-2000011168ACN-2026-03-4000123417 | 21 |  | 26 | 80 | 18 | 18 | 31
MADHAVI LATHA KARMUNGI | 2026-07-22 | JERRY JOSEPH | 2026-05-18 | All Leaks have been arrested. | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123418 | Closed | JERRY JOSEPH | 2026-05-18 | Drop leak observed in TWS from the valves which are not in use. Location advised to address the issue immediately | 6.1 | At Railwagon loading gantry | 1584 | LONI TERMINAL | XX | SOD | Marketing | WZ | 2026-03-06 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-06 | AUD-2026-03-2000011168ACN-2026-03-4000123418 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123418 | 2026-10-15 | 4.7538 | 324 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123418 | 532 | 8294 | 21 | 8294 | 227 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011168ACN-2026-03-4000123418 | AUD-2026-03-2000011168ACN-2026-03-4000123418 | 21 | 21 | 26 | 80 | 18 | 18 | 27 | 47
DINKAR SUMIT | 2026-07-23 | KUMAR GOPESH | 2026-07-23 | 1.Complied. Foam Pourer Schematic Diagrams have been updated and permanently mounted on the respective storage tanks for easy reference and operation during emergencies. 2.Complied. Foam Pourer testing arrangement has been provided in the foam pourers and associated foam lines of the AG tanks, enabling periodic testing without affecting tank safety. 3. Complied. Emergency Shutdown (ESD)system has been provided at the Effluent Treatment Plant (ETP) as per safety requirements. 4.Complied. Comprehensive training programmes have been conducted for contract workmen and security personnel covering VFD, Rim Seal Fire Protection System, Hydrocarbon Detector (HCD), DCP & CO₂ Fire Extinguishers, High Volume Long Range (HVLR) Monitor, Remote Operated Shut-Off Valve (ROSOV), Motor Operated Valve (MOV), QC Laboratory Process, and other critical terminal equipment. Pre-training and post-training evaluations were conducted to assess the effectiveness of the training. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127331 | Closed | KUMAR GOPESH | 2026-07-23 | System checked for efficacy. Fire fighting equipment found in working condition. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1281 | AJMER TERMINAL | 1) Foam pourer schematic diagram to be displayed so that everybody can operate foam pourer. 2) Testing system of Foam pourer to beinstalled in AG tanks. 3) ESD to be provided at ETP 4) Training on VFD, Rim seal, HCD, DCP, HVLR, ROSOV, MOV, QC lab process and other equipment to be strenthened. | SOD | Marketing | NWF | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011239ACN-2026-03-4000127331 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127331 | 2026-09-09 17:45 | 40.0143 | 325 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127331 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127331 | AUD-2026-03-2000011239ACN-2026-03-4000127331 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 47
DINKAR SUMIT | 2026-07-23 | KUMAR GOPESH | 2026-07-23 | RTGP Monitoring: Monthly monitoring of RTGP shall be carried out by Security, and dispatch shall be permitted only after RTGP approval/confirmation. Handling Register: A Handling Register shall be maintained at the Security Main Gate and reviewed with weekly signatures by the concerned department officer and LIC. Pending Returnable Items: Vendors shall be followed up regularly through email for the return of pending items, and the status shall be monitored until closure. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127343 | Closed | KUMAR GOPESH | 2026-07-23 | Pending RTGP record (month wise) to be parepared on RTGP register itself. List of open RTGP as per security vs list of open RTGP asper online gate pass portal to be mentioned. It is observed that confirm despatch not done. Pls ensure to carry out Confirm Despatch after approving RTGPs. | 6.5 | RTGP monitoring | 1281 | AJMER TERMINAL | Monthly monitoring of RTGP by security to be done. Confirm despatch to be done after approving RTGP. | SOD | Marketing | NWF | 2026-04-30 | POOR COMMUNICATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127343 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127343 | 2026-09-09 17:45 | 40.0143 | 325 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127343 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127343 | AUD-2026-03-2000011239ACN-2026-03-4000127343 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 47
DINKAR SUMIT | 2026-07-23 | KUMAR GOPESH | 2026-07-16 | The EM locks of Tank Trucks are being checked using the Intelligent Key by the LIC. The verification is carried out as per the prescribed procedure, and the results are recorded in the EM Lock Check Register with the LIC's signature. Weekly checks are conducted on a minimum of five (05) Tank Trucks, and any discrepancy observed is immediately attended to before allowing vehicle dispatch. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127347 | Closed | KUMAR GOPESH | 2026-07-16 | Intelligent Key was used to check EM lock conditions of Tts. Two transport Tt and three DCT Tts were checked and found okay. LIC also checked from his own key. | 6.9 | Checking of lock by Intelligent key | 1281 | AJMER TERMINAL | Pls check locks by using Intelligent key on weekly basis. 5 Tts per week. Revert with result. 100% locks to be checked. | SOD | Marketing | NWF | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011239ACN-2026-03-4000127347 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127347 | 2026-09-09 17:45 | 40.0143 | 325 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127347 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127347 | AUD-2026-03-2000011239ACN-2026-03-4000127347 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 47
DINKAR SUMIT | 2026-07-23 | KUMAR GOPESH | 2026-07-23 | **Compliance Status: Complied** The **Hindi SOP for actions to be taken by TT Crew during emergency situations (both inside and outside the terminal)**, as shared by the Zone, has been displayed at prominent locations, including the **TT Crew Room** and the **Locking Shed inside the Terminal**, for easy visibility and reference by all TT crews. A detailed training session was conducted for all TT crews covering the Standard Operating Procedure (SOP) for **Tank Truck (TT) evacuation during emergency situations**. Thetraining included emergency response actions in the event of **gantry fire, hydrocarbon leakage, tank farm fire/leakage, and emergencies occurring both inside and outside the terminal**. All TT crews were briefed on evacuation routes, emergency assembly points, communication procedures, emergency siren/hooter system, and the immediate actions to be taken upon activation of an emergency alarm. The importance of remaining calm, following instructions issued by the **Chief Fire Officer, Security Personnel, and Terminal Officials**, and ensuring safe evacuation without panic was emphasized. The training was completed successfully, and all participating TT crews were made aware of the emergency response procedures in line with HPCL requirements and applicable OISD guidelines. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127333 | Closed | KUMAR GOPESH | 2026-07-23 | Emergency preparedness checked. It require further training. | 2.15 | TT crew roadside emergency procedures checked | 1281 | AJMER TERMINAL | Zone has shared SOP in Hindi for actions to be taken by TT crew in case of emergency (both inside terminal as well as outside termnal. It needs to be displayed at prominent place and training to be given to all TT crew | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011239ACN-2026-03-4000127333 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127333 | 2026-09-09 17:45 | 40.0143 | 325 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127333 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127333 | AUD-2026-03-2000011239ACN-2026-03-4000127333 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 47
SUJEET KUMAR | 2026-07-24 | SAXENA UMESH CHANDRA | 2026-06-22 | All observations of MDSA Audit 2024-25 have been complied with. CAPA as on date is enclosed herewith. All observations of the SSA have also been complied with(CAPA enclosed). Hence this point can be closed now. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127179 | Closed | SAXENA UMESH CHANDRA | 2026-07-24 | Yes, reviewed OISD/MDSA/SSA complaince. OISD Nil pending. MDSA-24-25 (Out of 60, 57 are complied. 3 balance are pending which are in progress and targeted to complete by 31st March 2026. SSA (out of 30 points, 27 are complied). The pending 3 points are common that of MDSA. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1457 | INDORE DEPOT | Location to expedite closure of open Audit obsevation points in a time bound manner | SOD | Marketing | CEN | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011235ACN-2026-03-4000127179 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127179 | 2026-09-09 19:00 | 39.9622 | 326 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127179 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127179 | AUD-2026-03-2000011235ACN-2026-03-4000127179 | 21 | 21 | 26 | 80 | 0 | -3 | 35 | 47
DINKAR SUMIT | 2026-07-24 | KUMAR GOPESH | 2026-07-24 | Comprehensive training on all firefighting facilities was conducted for the newly joined personnel, including Shri Ankur Khandelwal(Officer) and Mr. Kirtik (GET), along with all Security Guards. The training covered the location, operation, and emergency response procedures for all firefighting systems. During the practical session, the officers themselves operated the firefighting equipment, including the Fire Engine (FE), HVLR Monitor/Monitor, Medium Expansion Foam Generator (MEFG), DCP Fire Extinguishers, CO₂ Fire Extinguishers, and other firefighting equipment, to gain hands-on operational experience and confidence in emergency response. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127332 | Closed | KUMAR GOPESH | 2026-07-24 | New joinee need to be trained for operations of fire fighting equipment | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1281 | AJMER TERMINAL | Pls train all new officers, GAT for all fire fighting facilities. | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011239ACN-2026-03-4000127332 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127332 | 2026-09-09 17:45 | 40.0143 | 326 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127332 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127332 | AUD-2026-03-2000011239ACN-2026-03-4000127332 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 47
DINKAR SUMIT | 2026-07-24 | KUMAR GOPESH | 2026-07-24 | The terminal is already equipped with a Pipeline Split Repair Kit for emergency handling of pipeline leakages. In addition, clamps of various sizes 4 ,5 ,8 ,11,12 inches and wooden plugs/blocks have been procured and kept readily available as part of the emergency leakage response kit to control product spillage until permanent repairs are carried out. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127341 | Closed | KUMAR GOPESH | 2026-07-24 | To handle sudden leakage from product pipeline, location should have safety kit. | 6.3 | Handling emergency | 1281 | AJMER TERMINAL | Pls make clamp and nipple arrangement for taking care of any leak in product pipeline. Make different sizes of clamps. | SOD | Marketing | NWF | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127341 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127341 | 2026-09-09 17:45 | 40.0143 | 326 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127341 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011239ACN-2026-03-4000127341 | AUD-2026-03-2000011239ACN-2026-03-4000127341 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 47
DINKAR SUMIT | 2026-07-24 | KUMAR GOPESH | 2026-07-24 | All CCTV cameras and display screens, including those in the Control Room, TT OLA Display, and LIC Room, have been repaired and arenow functioning properly. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127329 | Closed | KUMAR GOPESH | 2026-07-24 | CCTV functioning checked. One camera is not working. Most of the display screen (Control room, TT OLA display, LIC room) are not working. To be repaired | 2.6 | CCTV functioning checked | 1281 | AJMER TERMINAL | The camera is to be repaired. TV screen to be replaced/repaired | SOD | Marketing | NWF | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 20 | PROCESS SAFETY | S4 | F5 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127329 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127329 | 2026-09-09 17:45 | 40.0143 | 326 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127329 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | HIGH |  | AUD-2026-03-2000011239ACN-2026-03-4000127329 | AUD-2026-03-2000011239ACN-2026-03-4000127329 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 47
DINKAR SUMIT | 2026-07-24 | KUMAR GOPESH | 2026-07-24 | Total 72 transporters Tank trucks and many of the dealers Tank trucks has been surprises check at calibration Tower and record has been maintained as per( Annexure III ) No abnormal variation has been observed as per Rule 14 of the Legal Metrology act (General) Rules 2011. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127335 | Closed | KUMAR GOPESH | 2026-07-24 | Checked for 5 Tts. Dip was found okay in DCt Tts except two transport Tts | 3.2 | Post-loading dip checks verified | 1281 | AJMER TERMINAL | Variation observed in two trasnport Tts. DCT Tts performed well. It is advised to check dip of all transport Tts and share the result. If any transport TT is consistently showing variation equal to or greater than +3 mm, pls go for recalibration of that TT. | SOD | Marketing | NWF | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127335 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127335 | 2026-09-09 17:45 | 40.0143 | 326 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127335 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127335 | AUD-2026-03-2000011239ACN-2026-03-4000127335 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 47
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Sprinkler nozzles cleaned, (Work Permit No. 100000840284 attached). Dyke 2 drain valve issue also attened, valve not opening now inclosed position. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140182 | Closed | SINGH PREETI | 2026-07-16 | • WCFM-19 in front of Air compressor shed checked by Contract workman Kanubhai and found working. • WCFM-40 near dyke -2 TF-09 operated by Contract workman Prahlad and found working. • Sprinkler system of Tank TF-10 was operated, in Upper part Nozzle no. 14, 18, 24, 43, 45, 49 Middle-nozzle no. 12, 54, 18 Lower- Nozzle no. 54 were found to be not working. • HVLR-03 near Dyke-2 between tanks TF-09 and TF-10 operated by contract worker Kanubhai and found working. • HVLR-01 near Dyke-2 TF-11 operated by round guard Shailesh and found working ok. • Dyke-02 drain valve opening and alarm coming even while locked. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140182 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140182 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140182 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140182 | AUD-2026-06-2000013929ACN-2026-06-4000140182 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Verified with all existing contract personnel deployed at the location. No individual is currently available with a valid HVD/HZA endorsement. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140183 | Closed | SINGH PREETI | 2026-07-16 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140183 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140183 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140183 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140183 | AUD-2026-06-2000013929ACN-2026-06-4000140183 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Facility for Color blindness test available now at location. Also, regular eye tests of all TT Crew and Contract personnel are ensured annually and eye test records are also maintained. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140184 | Closed | SINGH PREETI | 2026-07-16 | Facility not available. | 2.16 | Eyesight / colour-blindness awareness checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE SAFETY CULTURE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140184 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140184 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140184 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140184 | AUD-2026-06-2000013929ACN-2026-06-4000140184 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Concertina coil at boundary has been fixed now. Photo attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140190 | Closed | SINGH PREETI | 2026-07-16 | 1. Concertina coil found damaged at main gate boundry wall. 2. Earth Pit checking observation: EP/PPH/17: Grid: 0.3, Individual: 0.9 EP/PPH/11: Grid:0.29, Individual: 0.4 | 3.16 | Earth pits / boundary / vegetation control checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140190 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140190 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140190 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140190 | AUD-2026-06-2000013929ACN-2026-06-4000140190 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-18 | Issuer sign being ensured on permits and in closing column. Checklist filled up as applicable. Tool box talks being conducted everyday now. Earth Pit boards changed. Fire Extinguishers were serviced and checked, All FEs operating and performing satisfactory. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140195 | Closed | SINGH PREETI | 2026-07-18 | 1. Check list of cold work permit reviewed. Issuer sign missing in the work permit and in closing column. Location to fill up checklist as per applicable site conditions. Tool box talk not conducted each day. 2. Earth Pit boards to be changed 3. 5 numbers of fire extinguishers were checked at TT gantry, out of 5 only 1 performed satisfactory. Remaining failed to operate. | 4.2 | Maintenance activities reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140195 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140195 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140195 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140195 | AUD-2026-06-2000013929ACN-2026-06-4000140195 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Extra plates in emergeny gates painted. Photo attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140811 | Closed | SINGH PREETI | 2026-07-16 | Extra plates in Emergency gate to be painted. | 6.14 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140811 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140811 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140811 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140811 | AUD-2026-06-2000013929ACN-2026-06-4000140811 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | Near Miss/Unsafe acts/unsafe conditions are being reported by all now. Total 22 reportings done in Q1 2026. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140812 | Closed | SINGH PREETI | 2026-07-16 | Near Miss/Unsafe acts/unsafe conditions to be reported by all. | 6.15 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE SAFETY CULTURE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140812 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140812 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140812 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140812 | AUD-2026-06-2000013929ACN-2026-06-4000140812 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-16 | As per OISD-STD-244, fire hydrant monitors shall be spaced at intervals not exceeding 30 m. This requirement is being complied withat the location. Further, OISD-STD-244 does not prescribe any minimum separation distance between a fire hydrant and an HVLR monitor panel. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140803 | Closed | SINGH PREETI | 2026-07-16 | Distance between Fire hydrant and monitor to be checked | 6.6 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140803 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140803 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140803 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140803 | AUD-2026-06-2000013929ACN-2026-06-4000140803 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-28 | SINGH PREETI | 2026-07-18 | Pond water cleaned/replenished. Inhouse fountain arrangement made for pond near main gate for water recirculation. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140806 | Closed | SINGH PREETI | 2026-07-18 | Pond water to be cleaned/replenished | 6.9 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | POOR EQUIPMENT MAINTENANCE | 1 | ENVIRONMENTAL | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140806 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140806 | 2026-08-22 22:00 | 57.8372 | 330 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140806 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140806 | AUD-2026-06-2000013929ACN-2026-06-4000140806 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
M MAHESH BABU | 2026-07-28 | SELVAN J | 2026-07-27 | Daily physical safety rounds have been resumed, and all observations are now being recorded in the e-Diary and tracked until closure. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143790 | Closed | SELVAN J | 2026-07-27 | Officers were advised to take physical rounds of the location and contribute to the betterment of location. Officers to leave legacy behind of doing something good for location before moving to another location. | 1.8 | Improvement plans discussed | 1973 | CASSIMODE BLACK OIL TERMINAL | e-dairy implementation by location incharge and submit the same on daily basis on e-dairy portal. No. of observations recorded in e-diary. | SOD | Marketing | SZ | 2026-09-30 | INADEQUATE SAFETY CULTURE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143790 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143790 | 2026-09-22 17:00 | 27.0455 | 330 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143790 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143790 | AUD-2026-07-2000015706ACN-2026-07-4000143790 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-07-28 | SELVAN J | 2026-07-27 | Mock drills have been conducted in accordance with the Emergency Response and Disaster Management Plan (ERDMP) scenarios. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143791 | Closed | SELVAN J | 2026-07-27 | Reviewed this FY fire drill report. Location has completed monthly L1 drills(L1 Fire drils conducted on 21.04.2026 and 29.05.2026. June Fire drill yet to be conducted. Undersigned did not conduct drill during this visit. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1973 | CASSIMODE BLACK OIL TERMINAL | Location advised to ensure all ERDMP scenarios are implemented during Fire Drills. | SOD | Marketing | SZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143791 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143791 | 2026-09-22 17:00 | 27.0455 | 330 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143791 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143791 | AUD-2026-07-2000015706ACN-2026-07-4000143791 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-07-28 | SELVAN J | 2026-07-27 | The competency of the TT crew, contract workman, and officers was assessed through a practical demonstration. The personnel were found competent to operate the WCF Monitor, and the assessment has been documented. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143792 | Closed | SELVAN J | 2026-07-27 | Checked knowledge of TT crew(Velu Murugan), contract workmen(Nagaraju) and officers and found satisfactory. JEO Mr. Srikanth was asked to operate WCF Monitor. Officer's Knoweldege was checked and found competent to handle the same. | 2.5 | Emergency response preparedness reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | Officers were asked to practice regularly the operation of critical equipments and gain knowledge in other aspects of fire fightingfacilities. | SOD | Marketing | SZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143792 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143792 | 2026-09-22 17:00 | 27.0455 | 330 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143792 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143792 | AUD-2026-07-2000015706ACN-2026-07-4000143792 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-07-28 | SELVAN J | 2026-07-27 | A surprise check of the TREM Card was conducted on Truck No. TN05BH0853. No deviations were observed during the inspection. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143793 | Closed | SELVAN J | 2026-07-27 | TT crew having adequate knowledge. All TT's are having TREM card. | 2.15 | TT crew roadside emergency procedures checked | 1973 | CASSIMODE BLACK OIL TERMINAL | Officers to do surprise checks of the TREM card and check its validity. | SOD | Marketing | SZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143793 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143793 | 2026-09-22 17:00 | 27.0455 | 330 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143793 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143793 | AUD-2026-07-2000015706ACN-2026-07-4000143793 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-07-28 | SELVAN J | 2026-07-27 | EM Lock SOP compliance was verified for the selected Tank Trucks (TTs). For TTs originating from ETTPL Ennore, manual locking was ensured, followed by re-locking with EM locks at Cassimode before dispatch to customers. The approved MOC was verified and found to be in place. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143795 | Closed | SELVAN J | 2026-07-27 | 100 % TTs are being sent with EM locks and compliance to the circular SOD/EM Lock dtd 22.12.2022 is being ensured. EM lock verifiedfor the following TTs with lock no - VM logistics-TN02BP5676(HE5662,HE1584) VM logistics-TN02CH0414(HE12836,HE3895) Sri Dhanapathy Transport-TN03Y9068(HE33071,33170) I&C Region have taken tanks at ETTPL Ennore. It is ensured that TTs from Ennore are manuallylocked and brought to Cassimode. Then are re-locked with EM locks and sent to cusotmers. MOC checked and in place. | 3.5 | EM Lock SOP compliance verified | 1973 | CASSIMODE BLACK OIL TERMINAL | Location to ensure that Sterna Locking works at ETTPL Ennore is completed so that Abloy locking can be stopped. | SOD | Marketing | SZ | 2026-09-30 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143795 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143795 | 2026-09-22 17:00 | 27.0455 | 330 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143795 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143795 | AUD-2026-07-2000015706ACN-2026-07-4000143795 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
DINKAR SUMIT | 2026-07-29 | KUMAR GOPESH | 2026-07-29 | Night lux level measurements were carried out in July 2026. The TT Gantry recorded 128 lux against the required 100 lux, and the TTParking recorded 53 lux against the required 20 lux, meeting the prescribed illumination requirements. All defective high mast lights have been repaired/replaced with LED luminaires, and adequate lighting has been ensured in the TT Gantry and TT Parking areas. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127327 | Closed | KUMAR GOPESH | 2026-07-29 | Yes checked. Lux level to be improved in TT gantry, TT parking. Some of the lights of high mast towers are not working. To be repaired | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1281 | AJMER TERMINAL | Pls take corrective action | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011239ACN-2026-03-4000127327 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127327 | 2026-09-09 17:45 | 40.0143 | 331 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127327 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127327 | AUD-2026-03-2000011239ACN-2026-03-4000127327 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 48
DINKAR SUMIT | 2026-07-29 | KUMAR GOPESH | 2026-07-29 | 1.Security personnel have been trained on frisking procedures, visitor screening, and mandatory safety briefing as per the SecurityGate SOP. Periodic refresher training is being conducted to ensure compliance.Training given as on 24.07.2026 as SURAKSHIT2021 withPPT & Training in filed at Main Gate . 2.A dedicated SOP display board has been installed at the Security Gate covering the complete procedure for visitor entry and exit, including document verification, frisking, PPE requirements, prohibited items, and exit formalities. 3. A Do's and Don'ts display board has been installed at the Security Gate for security personnel, highlighting key responsibilities, safety precautions, emergency response, and prohibited practices. 4.A TV display has been installed at the Security Gate to continuously play animated videos on frisking procedures, visitor safety instructions, emergency response, PPE requirements, and other terminal SOPs. Audio announcements are also being played periodically to enhance awareness. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127328 | Closed | KUMAR GOPESH | 2026-07-29 | Checked. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1281 | AJMER TERMINAL | Security needs to be trained further for frisking as well as safety briefing. One display board to be installed at security gate describing complete SOP for entry and exit of visitors. Display board on Dos and Don’t's for Security guards One TV screen to be installed at gate showing animated video of frisking and for playing audio about various SOPs. | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 15 | PROCESS SAFETY | S3 | F5 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127328 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127328 | 2026-09-09 17:45 | 40.0143 | 331 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127328 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127328 | AUD-2026-03-2000011239ACN-2026-03-4000127328 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 48
DINKAR SUMIT | 2026-07-29 | KUMAR GOPESH | 2026-07-29 | The MOVs and ROSOVs were attended by M/s Gastek Engineering (Delhi). All identified issues have been rectified, and all MOVs and ROSOVs are functioning satisfactorily. The system is now operating in Remote/Auto mode, and all valves can be operated automatically from the Control Room through the SCADA/PLC system. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127340 | Closed | KUMAR GOPESH | 2026-07-29 | Few ROSOVs are not communicating. MOVs are also not communicating. Tender floated for MOV spares. To be rectified | 6.1 | mov repair and communication | 1281 | AJMER TERMINAL | MOV to be repaired. Pumps should be kept in remote mode. | SOD | Marketing | NWF | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011239ACN-2026-03-4000127340 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127340 | 2026-09-09 17:45 | 40.0143 | 331 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127340 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127340 | AUD-2026-03-2000011239ACN-2026-03-4000127340 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 48
DINKAR SUMIT | 2026-07-29 | KUMAR GOPESH | 2026-07-29 | 1. Corrosion Inhibitor (CI) inventory stock and the "Own Use" dropdown in SAP have been updated through July 2026. 2.Physical stock and book stock of additives are monitored on a monthly basis. The quantities of Petrol Plus and Diesel Plus additives are automatically depleted in SAP based on product loading/dispatch, and inventory is reconciled with the system records. Monthly monitoring records are maintained accordingly. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127344 | Closed | KUMAR GOPESH | 2026-07-29 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.6 | Additive stock monitoring | 1281 | AJMER TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127344 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127344 | 2026-09-09 17:45 | 40.0143 | 331 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127344 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127344 | AUD-2026-03-2000011239ACN-2026-03-4000127344 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | MS scrap has been disposed off via invoice no HR0150133528 dated 27.03.2026 | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143874 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Scrap available-20 MT. RFD processed with successful action and only upliftment is pending. Target completion-28th March’26 | 4.08 | Scrap disposal progress reviewed / scrap-free environment checked | 1341 | HISAR TERMINAL | Complete Scrap disposal in time bound manner. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143874 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143874 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143874 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143874 | AUD-2026-07-2000015093ACN-2026-07-4000143874 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Crocodile clip has been changed. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143873 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | The crocodile clip installed at Bay No. 03 & used for earthing of TTs placed for loading was found to be lacking strength to firmlygrip the TT body for the intended purpos due to reduced spring tension leading to inadequate clamping force. This may result in improper bonding/ earthing contact with the TT during gantry operations. | 4.03 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Replace the defective crocodile clip at Bay No. 03 immediately to ensure proper bonding/earthing during TT gantry operations. Also,check for similar kind of issues at other bays and take corrective actions as required. | SOD | Marketing | NZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143873 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143873 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143873 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143873 | AUD-2026-07-2000015093ACN-2026-07-4000143873 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Leakage has been arrrested from product pump of Ethanols. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143872 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | In Product pump house leakage observed from Oil Cup | 4.0199999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Leakage to be arrested immediately | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143872 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143872 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143872 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143872 | AUD-2026-07-2000015093ACN-2026-07-4000143872 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Pressure gauge has been changed. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143871 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Pressure Gauge of Jockey pump-02 found to be faulty | 4.01 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Pressure Gauge to be replaced | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143871 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143871 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143871 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143871 | AUD-2026-07-2000015093ACN-2026-07-4000143871 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | All points of T4S audit will be complied by 30.09.2026 | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143870 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | T4S Audit of the location was carried out during the period 19-21 May'26. Total of 38 recommendations were made during the audit and 21 out of them have been complied by the location. | 3.24 | OISD/MDSA/SSA compliance reviewed | 1341 | HISAR TERMINAL | Pending recommendations to be complied in time bound manner. | SOD | Marketing | NZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015093ACN-2026-07-4000143870 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143870 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143870 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143870 | AUD-2026-07-2000015093ACN-2026-07-4000143870 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | ALL MOC has been closed. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143869 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | A total of 4 MOCs are appearing as open as on 02.07.2026. | 3.2 | MOC status reviewed | 1341 | HISAR TERMINAL | All open MOCs to be closed. | SOD | Marketing | NZ | 2026-07-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143869 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143869 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143869 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143869 | AUD-2026-07-2000015093ACN-2026-07-4000143869 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Flexible wire originating directly from EPs has been removed with proper earthing from the nearest point from the earthing grid/ strip. Same has been rectified | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143868 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | EP#127 of tank no. TK04 (MS Tank) was verified in field: Individual EP Resistance was observed as 1.40 Ohm Vs. 1.37 Ohm displayed. Grid EP Resistance was observed as 0.29 Ohm Vs. 0.41 Ohm. It was observed that flexible wires were found originated from EP#152which is not the correct engineering practice. | 3.19 | Earth pits / boundary / vegetation control checked | 1341 | HISAR TERMINAL | Flexible wire originating directly from EPs to be removed with proper earthing from the nearest point from the earthing grid/ strip. | SOD | Marketing | NZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143868 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143868 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143868 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143868 | AUD-2026-07-2000015093ACN-2026-07-4000143868 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Tree branches near TK3 and along with boundry wall has been trimmed. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143867 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Housekeeping - Housekeeping of the location is found to be satisfactory with some areas requiring minor upkeep which were discussedduring field round with location team. | 3.15 | Housekeeping & PPE usage checked | 1341 | HISAR TERMINAL | Few tree branches along the boundary wall behind HSD tank TK03 to be trimmed. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143867 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143867 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143867 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143867 | AUD-2026-07-2000015093ACN-2026-07-4000143867 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | 3. Proper comments during local loading is being manitained 4. MFM communication with TAS server is rectified by Honeywell. MFM readings is updating in daily day end report. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143866 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | 1. Location is maintaining day-wise local loading report duly signed by TAS Officer & LIC. 2. Bay Re-Assignment was also verifiedfor the period 1st Apr'26 to 30th Jun'26. During this period, locations carried out 27 cases of Bay Re-Assignments. Last bay reassigment during the period was carried out on 22.06.2026- Print-out of the same duly signed by the TAS officer is available in the day end bunch provided to the LIC on daily basis. 3. A total of 272 instances of local loading were observed during the period 1st Apr'26 to 30th Jun'26. All these instances were found to be recorded with remarks as Prover under the truck number except for three instances on 03.06.2026 for Bay no. 9 where 0 is recorded under truck number. 4. MFM of Bay no.13 is not communicating with LRC server since date 21.06.2026. This is resulting in MFM Vs. BCU reading at the day end. Records for this differnce are available duly signedby TAS officer, Planning Officer and LIC. However, reason for the difference is not recorded on the day end report. | 3.14 | Local loading checks (if applicable) | 1341 | HISAR TERMINAL | 3. Location to record proper comments in all cases of local loading. 4. Location should record the reason for MFM Vs. BCU difference at the day end on daily basis. Date since any issue with the equipment is encountered should be also recorded on daily basis tillits resolution. Also, location should carry-out 100% dip checking of TTs loaded from Bay No. 13 till the issue get resolved and maintain records. Alternatively, the bay should be declared as unavailable in IMS to avoid loading from it. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143866 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143866 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143866 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143866 | AUD-2026-07-2000015093ACN-2026-07-4000143866 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Scaling issue observed in water sensor and calibration issue observed in PT. Issues has been rectified by Honeywell. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143865 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Physical dips of tank no. TK04 was verified along with density and temparature on 30.06.2026. Water dip of the tank had variation beyond norms (observed dip 129mm Vs. TAS dip 121mm). Density variation was also found beyond norms (observed density 741.8 Vs. TAS density 748.87). Physical gauging of all the product tanks was carried out at the location along with an officer from Pipelines SBU on 30.06.2026. | 3.07 | Inventory physical dip of minimum two tanks taken | 1341 | HISAR TERMINAL | Location to identify the root cause for variation in the water dip and density for taking necessary corrective action. | SOD | Marketing | NZ | 2026-07-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143865 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143865 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143865 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143865 | AUD-2026-07-2000015093ACN-2026-07-4000143865 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | 5% EM locks of daily reported TTs are being checked and records maintained. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143864 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Check for 5% EM locks is being done by the location and has been reviewed during visit | 3.05 | EM Lock SOP compliance verified | 1341 | HISAR TERMINAL | Proper record for 5 % daily check and 100% monthly check to be made | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143864 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143864 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143864 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143864 | AUD-2026-07-2000015093ACN-2026-07-4000143864 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | 5% Monitoring of daily trips is being done. Records maintained | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143863 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-29 | Check for 5% VTS deviation is being done by the location and has been reviewed during visit | 3.03 | VTS deviations reviewed | 1341 | HISAR TERMINAL | Proper record for 5 % daily check and 100% monthly check to be made | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143863 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143863 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143863 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143863 | AUD-2026-07-2000015093ACN-2026-07-4000143863 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145976 | Open |  |  | C bacs installed near planning room is non operational. | 2.8 | Access control systems checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145976 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145976 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145976 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145976 |  | AUD-2026-07-2000016256ACN-2026-07-4000145976 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145977 | Open |  |  | HCD: TLF PH, HCD 54 & HCD 100 : checked and found working. HVLR: HVLR 1 operated by officer Manish and performed satisfactory. Hose box-146 was checked and found equipped with 2 hose pipes and 2 nozzles. Testing date was not mentioned, test date was faded. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 |  | 1 |  | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145977 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145977 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145977 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145977 |  | AUD-2026-07-2000016256ACN-2026-07-4000145977 | 21 |  | 27 | 80 | 0 | -26 | 50
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145982 | Open |  |  | 1. TK101B: Dip TAS: 1808 CM, Field: 1805 cm, Temp TAS: 33.09 Field: 33.1 2. 1. TK102C: Dip TAS: 1817.3 CM, Field: 1820 cm, Temp TAS: 33.5 Field: 34.5 | 3.7 | Inventory physical dip of minimum two tanks taken | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145982 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145982 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145982 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145982 |  | AUD-2026-07-2000016256ACN-2026-07-4000145982 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000145987 | Open |  |  | Strainer at TT gantry are overdue for cleaning. Quaterly check list of Fire engine and DG is not duly filled. Earthing arrangement found improper for ROSOV 1702. | 4.2 | Maintenance activities reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 |  | 1 |  | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145987 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145987 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145987 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145987 |  | AUD-2026-07-2000016256ACN-2026-07-4000145987 | 21 |  | 27 | 80 | 0 | -26 | 50
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000145988 | Open |  |  | Disposal of un-used or damaged assets, misc scrap is to be expedited. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145988 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145988 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145988 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145988 |  | AUD-2026-07-2000016256ACN-2026-07-4000145988 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145989 | Open |  |  | TT crew of GJ04W949 and GJ20J8833 was not able to read SOP boards available in Hindi/English at TT gantry as they can read only local language Gujrati. | 6.1 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145989 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145989 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145989 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145989 |  | AUD-2026-07-2000016256ACN-2026-07-4000145989 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145993 | Open |  |  | Lube leak observed in ethanol pump P-108A | 6.5 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145993 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145993 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145993 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145993 |  | AUD-2026-07-2000016256ACN-2026-07-4000145993 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145994 | Open |  |  | Location to check inclusion of mechanical seal cooling arrangement for MS pump in location SOP. | 6.6 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145994 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145994 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145994 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145994 |  | AUD-2026-07-2000016256ACN-2026-07-4000145994 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145995 | Open |  |  | SLD of Foam pump shed is not updated. | 6.7 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145995 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145995 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145995 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145995 |  | AUD-2026-07-2000016256ACN-2026-07-4000145995 | 21 |  | 27 | 80 | 0 | -26 | 52
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145996 | Open |  |  | Location to install test bench and put to use. | 6.8 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145996 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145996 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145996 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145996 |  | AUD-2026-07-2000016256ACN-2026-07-4000145996 | 21 |  | 27 | 80 | 0 | -26 | 52
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Location is mentioning weight of Co2 FE on fire extinguishers. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143859 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Fire Extinguisher - Total nos. DCP's available at the location - 142 (9 Kg), 16 nos. (25 Kg), 03 nos. (75 Kg) Total no CO2 - 62 nos. (4.5 Kg), 16 nos. (2 kg) & 03 nos. of Clean agent (2 Kg). Knowledge level of location officers about operation of these equipment is found satisfactory. While CO2 fire extinguishers are periodically inspected and date of testing and due date for testing duly mentioned on each of the equipment, the weight observed during inspection is not mentioned on it. | 2.17 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1341 | HISAR TERMINAL | Location is advised to mention the weight of the CO2 FE on each date of its testing. | SOD | Marketing | NZ | 2026-07-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143859 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143859 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143859 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143859 | AUD-2026-07-2000015093ACN-2026-07-4000143859 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Choked foam pourers has been rectified of all tanks. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143857 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | While checkiing the foam pourer of tank no. TK04, one of the five foam pourer was found choked. Location is maintaining the practice of quarterly testing of cleaning of foam pourer with last testing done on 04.04.2026. | 2.0699999999999998 | Emergency response preparedness reviewed | 1341 | HISAR TERMINAL | Location to ensure proper functioning of all foam pourers. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143857 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143857 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143857 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143857 | AUD-2026-07-2000015093ACN-2026-07-4000143857 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | LUX Level at TT parking is low due to power cable faulty. As advised,The remark of faulty power cable has been mentioned in LUX Level report of July-26. However, for the replacement of faulty cable, Required quantity of power cable mentioned in M&R LPR. Once PO get finalized same shall be replaced on priority. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143854 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Location is carrying out lux level monitoring on monthly basis. From the records available, lux levels were checked on 10.04.2026, 12.05.2026 & 15.06.2026 during Q1: 2026-27. In all these reports, lux levels are recorded lower than the required level in the TT parking area with remarks LED light not working + Cable fault. Corrective action taken is not recorded in the report. | 2.0299999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1341 | HISAR TERMINAL | a) Lux levels as per the norms to be maintained in all the operating areas. b) Records maintained should be entered with the follow-up action taken with date for closure of findings below the minimum lux level norms. | SOD | Marketing | NZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015093ACN-2026-07-4000143854 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143854 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143854 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143854 | AUD-2026-07-2000015093ACN-2026-07-4000143854 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | ESD operation is being reported in Mock drill report | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143852 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | Location is carrying out monthly mock fire drills- all on double contingencies basis. During Q1: 2026-27, fire drill were conductedon 18.04.2026, 19.05.2026 and 06.06.2026. Location is not incorporating operation of ESD and observations due to it in each of the fire drill report. | 2.0099999999999998 | Fire drill conducted in last 6 months (surprise) | 1341 | HISAR TERMINAL | As per the requirement of OISD 244, ESD operation has to be verified during mock fire drills. Accordingly, location to record ESD operation in each of the mock fire drill reports. | SOD | Marketing | NZ | 2026-07-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143852 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143852 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143852 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143852 | AUD-2026-07-2000015093ACN-2026-07-4000143852 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
DURGA NARAIN MEENA | 2026-07-30 | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | ) TT exit time and LPM are reviewed on daily basis. ( Complied) b)Checklist for VTS and EM locking is being filled and checked on daily basis. C) Safety officer is checking equiments on daily basis and filling the daily safet checklist d) Tank painting details has been submitted to HQO | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.10 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143851 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-07-30 | a) The TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlierVC's with all Location TAS officer b) The Transportation officer to maintain Annex-1 of VTS circular and ensuring that all TT's are covered for VTS and EM locking check on monthly baisis with record c) The Safety Officer shall ensure that all field equipmentare maintained in intact and operational condition at all times through regular inspection and monitoring. d) The Maintenance Officer shall initiate and pursue budget proposals for tank painting and any required repair works to ensure asset integrity and compliance with maintenance standards. | 1.08 | Improvement plans discussed | 1341 | HISAR TERMINAL | a) A structured monitoring system to be ensured to track TT exit time and LPM on a daily basis, with periodic review by location. b) A monthly compliance checklist shall be institutionalized for VTS coverage and EM locking verification of all TTs. c) A preventive maintenance and inspection schedule shall to be followed for all critical field equipment, with records maintained and periodically audited to ensure operational readiness. d) Budget requisitions shall be initiated in a timely manner, with systematic follow-up to ensure prompt approval and disbursement of funds. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143851 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143851 | 2026-09-30 17:00 | 19.0455 | 332 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143851 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143851 | AUD-2026-07-2000015093ACN-2026-07-4000143851 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
|  | SELVAN J | 2026-07-30 | The NPCB funding proposal has been forwarded to the Zone along with the repair estimate for approval and necessary action. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000144100 | Completed | SELVAN J | 2026-07-30 | Yes. Full field round completed (gantry/tank farm/jetty/pump house/TT crew rest room/security/admin). Climbed Tank no. 2 which has been taken out of service due to metal thickness loss and corrosion at wind girder. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1973 | CASSIMODE BLACK OIL TERMINAL | NPCB funds proposal to be forwarded to zone after taking estimates as mentioned in above pt. no. 3.18 | SOD | Marketing | SZ | 2026-07-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-15 | AUD-2026-07-2000015706ACN-2026-07-4000144100 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000144100 | 2026-09-22 17:00 | 27.0455 | 317 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000144100 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015706ACN-2026-07-4000144100 |  | AUD-2026-07-2000015706ACN-2026-07-4000144100 | 21 |  | 27 | 80 | 0 | 0 | 46
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146324 | Open |  |  | Disposal of un-used or damaged assets, misc scrap is to be expedited. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146324 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146324 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146324 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016503ACN-2026-07-4000146324 |  | AUD-2026-07-2000016503ACN-2026-07-4000146324 | 21 |  | 27 | 80 | 0 | -26 | 52
|  |  |  | 1 CCTV repaired and repair for balance 1 camera held up due to non-availability of spare at OEM end. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145695 | Open | KUMAR NITISH | 2026-07-31 | 53 out of 55 cameras are currently operational. Backup is available for 92 days. | 2.6 | CCTV functioning checked | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-07-15 |  | 1 |  | S1 | F1 | 2026-08-31 | AUD-2026-06-2000012346ACN-2026-07-4000145695 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145695 | 2026-09-18 | 31.7538 | 317 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145695 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012346ACN-2026-07-4000145695 |  | AUD-2026-06-2000012346ACN-2026-07-4000145695 | 21 |  | 27 | 80 | 5 | 5 | 46
|  |  |  | Fire Engine Display panels procurement proposal being prepared. Display of critical parameters of fire engine available in manual controller installed for FE6 to FE10. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146503 | Open | KUMAR NITISH | 2026-07-31 | Fire engine display panels are not available for FE-06, FE-07, FE-08, FE-09, and FE-10. | 6.2 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000012346ACN-2026-07-4000146503 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146503 | 2026-09-18 | 31.7538 | 287 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146503 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012346ACN-2026-07-4000146503 |  | AUD-2026-06-2000012346ACN-2026-07-4000146503 | 21 |  | 27 | 80 | 5 | 5 | 41
TILKAN RAVINDRA KUMAR | 2026-07-30 | Sreelal P P | 2026-07-30 | Matter taken up with HR with detailed manpower requirement with respect officers, non-management employees and trainees by mail dt 23.06.2026 | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141175 | Closed | Sreelal P P | 2026-07-30 | Interacted with Officers. Concerns regarding reduction in Employees due to superannuation was discussed. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1845 | IRUMPANAM TERMINAL | Location needs E0 Officers in place of retiring NM employees urgently. Matter to be taken up with Zone/HQO For further taking up with HR. | SOD | Marketing | CZR | 2026-06-30 | COST-CUTTING COMPROMISING SAFETY | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013833ACN-2026-06-4000141175 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141175 | 2026-09-02 16:30 | 47.0663 | 332 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141175 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013833ACN-2026-06-4000141175 | AUD-2026-06-2000013833ACN-2026-06-4000141175 | 21 | 21 | 27 | 80 | 1 | -4 | 44 | 48
TILKAN RAVINDRA KUMAR | 2026-07-30 | Sreelal P P | 2026-07-30 | All PM jobs are closed within schedule | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141192 | Closed | Sreelal P P | 2026-07-30 | All PM jobs completed on time by location in the previous months. | 4.4 |  | 1845 | IRUMPANAM TERMINAL | All PM jobs closure to be ensured progressively during the scheduled month | SOD | Marketing | CZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-06-30 | AUD-2026-06-2000013833ACN-2026-06-4000141192 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141192 | 2026-09-02 16:30 | 47.0663 | 332 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141192 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141192 | AUD-2026-06-2000013833ACN-2026-06-4000141192 | 21 | 21 | 27 | 80 | 1 | -4 | 44 | 48
TILKAN RAVINDRA KUMAR | 2026-07-30 | Sreelal P P | 2026-07-30 | Project AR Submitted | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141191 | Closed | Sreelal P P | 2026-07-30 | Reviewed project status of Valve procurement | 4.3 | 2 projects to be completed for which tendering is under progress | 1845 | IRUMPANAM TERMINAL | Advised to submit AR urgently | SOD | Marketing | CZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013833ACN-2026-06-4000141191 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141191 | 2026-09-02 16:30 | 47.0663 | 332 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141191 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013833ACN-2026-06-4000141191 | AUD-2026-06-2000013833ACN-2026-06-4000141191 | 21 | 21 | 27 | 80 | 1 | -4 | 44 | 48
|  | CHANGMAI RAHUL | 2026-07-30 | Many of the TAS related job which were to be completed by location as mentioned in are not completed yet. 1) Fire Alarm ControlPanel -Installed and commissioned 2) OIC & TFMS Monitors - 2 Nos. - Arranged from Kolkata Terminal spare. 3) TSI for Radar Gauges- 2 Nos. - Two to the TSI installed for TK-3 & TK-4 is functional now. TSI for TK-1 and TK-2 are obsolete, no spare avilable in market. need to revamp entire Radar gauge facility 4) DPGs for 3" strainers - 4 Nos.- After TAS installation check by TAS vendor and is working 5) Filter elements (for strainers)- 2 Nos. is arranged from RIT spare. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127088 | Completed | CHANGMAI RAHUL | 2026-07-30 | Many of the TAS related job which were to be completed by location as mentioned in are not completed yet. 1) Fire Alarm ControlPanel - It was given to understand that the card procured but not commissioned. 2) OIC & TFMS Monitors - 2 Nos. - It was given to understand that the tendering still not completed 3) TSI for Radar Gauges - 2 Nos. - Two to the TSI installed for TK-3 & TK-4 but variations observed. TSI not available for TK-1 & TK-2 4) DPGs for 3 strainers - 4 Nos.- It was given to understand that the corrective action taken but testing not done yet 5) Filter elements (for strainers)- 2 Nos. - Not yet procured | 4.3 | Project progress reviewed | 1708 | DIMAPUR DEPOT | LIC to ensure closure of all the open points are closed after taking necessary corrective action. | SOD | Marketing | GZR | 2026-04-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010729ACN-2026-03-4000127088 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127088 | 2026-09-12 | 37.7538 | 241 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127088 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127088 |  | AUD-2026-03-2000010729ACN-2026-03-4000127088 | 21 |  | 26 | 80 | 7 | 7 | 35
|  | CHANGMAI RAHUL | 2026-07-30 | All open PM order are closed now . PM order are generated only after work permit is taken. Printout was not available in the location to save paper. Now printout taken and filed | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127089 | Completed | CHANGMAI RAHUL | 2026-07-30 | PM orders are clsoed without any work permit. | 4.4 | Quality of PM compliance reviewed | 1708 | DIMAPUR DEPOT | Needs Improvement | SOD | Marketing | GZR | 2026-03-30 | OUTDATED OR COMPLEX SOPS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127089 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127089 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127089 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127089 |  | AUD-2026-03-2000010729ACN-2026-03-4000127089 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-07-30 | All BCU bolting completed | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127090 | Completed | CHANGMAI RAHUL | 2026-07-30 | All the 4 BCU was having ony 1 bolt each and all other bolts were missing. | 6.1 | Additional Observations | 1708 | DIMAPUR DEPOT | To be installed immediately | SOD | Marketing | GZR | 2026-03-30 |  | 10 |  | S2 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127090 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127090 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127090 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127090 |  | AUD-2026-03-2000010729ACN-2026-03-4000127090 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-07-30 | 2 KL prover was loaded with HSD from TK-3 [using local batch processing in BCU] and flollowing are the observations : 1. 2KL prover tank graduated glass tube is rectified 2. Recalibration of the prover tank is done in Jun26 3. Acknowledge button in RIT of MS for Bay no. 1 is replaced from Bay-2 spare 4. Bay-2 : HSD Strainer bolts were missing were replaced 5. Reconciallation completed | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127091 | Completed | CHANGMAI RAHUL | 2026-07-30 | 2 KL prover was loaded with HSD from TK-3 [using local batch processing in BCU] and flollowing are the observations : 1. Gauze of2KL prover tank is showing incorrect reading 2. The prover certificate dated 02.02.26 mentioned that there will ba gap 25.3 CM from top of the prover tank. However, there is variations observed after physical locading. 3. Acknowledge button found missing in RIT of MS for Bay no. 1 4. Bay-2 : HSD Strainer bolts were missing 5. FA Reconcillation for cyce 24-27 to be completed by 31.03.26 | 6.2 | Additional Observations | 1708 | DIMAPUR DEPOT | Corrective action to be taken immediately | SOD | Marketing | GZR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010729ACN-2026-03-4000127091 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127091 | 2026-09-12 | 37.7538 | 241 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127091 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127091 |  | AUD-2026-03-2000010729ACN-2026-03-4000127091 | 21 |  | 26 | 80 | 7 | 7 | 35
|  | CHANGMAI RAHUL | 2026-07-30 | TAS installed and Critical alarms like ESDs , FAP are checked and is ok | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127082 | Completed | CHANGMAI RAHUL | 2026-07-30 | Not Avaialable as TAS is not functional as of now | 3.12 | Critical alarms checked & corrective actions reviewed | 1708 | DIMAPUR DEPOT | Location to immediately get the MOC approval followed by close coordination with HQO for early procurement and installation of radar gauge | SOD | Marketing | GZR | 2026-03-30 |  | 5 |  | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127082 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127082 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127082 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127082 |  | AUD-2026-03-2000010729ACN-2026-03-4000127082 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-07-30 | Procured the immeditate faulty items likes Gate barrier,sensors, loading arms swivel joints. Other faulty items replacement are sourced from other HPCL terminal and installed. Few are still faulty like Density Probe found in recent maintenance. Shall be arranged from other locations where TAS revamption is to be done. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000136997 | Completed | CHANGMAI RAHUL | 2026-07-30 | TAS automation pending due to faulty equipments | 3.8 | Auto vs Manual reconciliation checked | 1708 | DIMAPUR DEPOT | To replace faulty items | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136997 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136997 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136997 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136997 |  | AUD-2026-06-2000012955ACN-2026-06-4000136997 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-30 | No abnormal variations and unused assets. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000136998 | Completed | CHANGMAI RAHUL | 2026-07-30 | Nil | 3.9 | Abnormal variations / unused assets reviewed | 1708 | DIMAPUR DEPOT | XX | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136998 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136998 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136998 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136998 |  | AUD-2026-06-2000012955ACN-2026-06-4000136998 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-30 | Product reconciallation is being done on regular basis and is ok | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000136999 | Completed | CHANGMAI RAHUL | 2026-07-30 | Monthly reconcialltion checked and is ok | 3.10 | TFMS/SAP reconciliation checked | 1708 | DIMAPUR DEPOT | Officer advised to do daily reconciallation | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136999 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136999 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136999 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136999 |  | AUD-2026-06-2000012955ACN-2026-06-4000136999 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-30 | Housekeeping is improved and Training given to all security and workmen | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137150 | Completed | CHANGMAI RAHUL | 2026-07-30 | Checked.Housekeeping to be monitored on daily basis. Green belt area development in open area | 3.15 | Housekeeping & PPE usage checked | 1708 | DIMAPUR DEPOT | Training to Security/Workman | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000137150 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137150 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137150 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137150 |  | AUD-2026-06-2000012955ACN-2026-06-4000137150 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-07-30 | Started maintaining the checklist for the equipment | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137153 | Completed | CHANGMAI RAHUL | 2026-07-30 | No record for equipments check are available. | 4.2 | Maintenance activities reviewed. | 1708 | DIMAPUR DEPOT | Regular checking of equipments are advised as per checklist and record to be maintained. | SOD | Marketing | GZR | 2026-05-20 |  | 1 |  | S1 | F1 | 2026-05-20 | AUD-2026-06-2000012955ACN-2026-06-4000137153 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137153 | 2026-09-12 | 37.7538 | 261 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137153 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137153 |  | AUD-2026-06-2000012955ACN-2026-06-4000137153 | 21 |  | 27 | 80 | 7 | 7 | 38
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146462 | Open |  |  | HFHSD thruput to be increased | 1.2 | Performance review conducted | 3693 | KAKINADA TML | To take up with DS for increase in thruput of HFHSD | SOD | Marketing | SCR | 2026-07-30 |  | 5 |  | S1 | F5 | 2026-07-30 | AUD-2026-07-2000016564ACN-2026-07-4000146462 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146462 | 2026-09-16 16:00 | 33.0872 | 332 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146462 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146462 |  | AUD-2026-07-2000016564ACN-2026-07-4000146462 | 21 |  | 27 | 80 | 0 | 0 | 48
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146463 | Open |  |  | Pending Issues reviewed . PESO initial approval received for removal of Class A four tanks. However in view of proposal for usage of the tanks for FO, applied for conversion of the 4 tanks to Class C. PESO Hyderabad have advised to submit application to PESO Nagpur. | 1.3 | Pending issues reviewed | 3693 | KAKINADA TML | Application to be submitted to PESO Nagpur by 15.06.2026 | SOD | Marketing | SCR | 2026-06-15 |  | 5 |  | S1 | F5 | 2026-06-15 | AUD-2026-07-2000016564ACN-2026-07-4000146463 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146463 | 2026-09-16 16:00 | 33.0872 | 287 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146463 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146463 |  | AUD-2026-07-2000016564ACN-2026-07-4000146463 | 21 |  | 27 | 80 | 0 | 0 | 41
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146464 | Open |  |  | Status of action points from the last BCM reviewed | 1.4 | Earlier action points status checked | 3693 | KAKINADA TML | Pending audit points of SSA & MDSA to be completed by 30.09.2026 | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000016564ACN-2026-07-4000146464 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146464 | 2026-09-16 16:00 | 33.0872 | 394 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146464 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146464 |  | AUD-2026-07-2000016564ACN-2026-07-4000146464 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146465 | Open |  |  | DHMD not working , Frisking not being done by Security guard,No lady guard available and No separate cabin available for checking female visitors | 1.7 | Compliance to HQO/Zonal circulars reviewed | 3693 | KAKINADA TML | DHMD to be rectified, Training to be imparted to Security guards , Lady guard to be provided in new security contract, Provision tobe made for separate cabin for checking of female visitors by Lady Security guard | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-07-2000016564ACN-2026-07-4000146465 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146465 | 2026-09-16 16:00 | 33.0872 | 394 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146465 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146465 |  | AUD-2026-07-2000016564ACN-2026-07-4000146465 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146467 | Open |  |  | Chain Link Fencing AR in technically completed status to be closed. Lux level improvement project materials received to be installed and project to be completed by 31.07.2026 | 4.3 | Project progress reviewed | 3693 | KAKINADA TML | Chain link fencing project AR to be closed immdeiately and Lux level improvement project to be completed and closed by 31.07.2026 | SOD | Marketing | SCR | 2026-07-30 |  | 5 |  | S1 | F5 | 2026-07-30 | AUD-2026-07-2000016564ACN-2026-07-4000146467 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146467 | 2026-09-16 16:00 | 33.0872 | 332 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146467 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146467 |  | AUD-2026-07-2000016564ACN-2026-07-4000146467 | 21 |  | 27 | 80 | 0 | 0 | 48
[5 empty] | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146518 | Open |  |  | Cooling water line of fire engine is in close loop, thus difficult to ensure its flowability | 6.1 | Fire Engine Shed | 1485 | AKOLA DEPOT | To provide in consultation with OEM | SOD | Marketing | WZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146518 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146518 | 2026-08-24 | 56.7538 | 394 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146518 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013155ACN-2026-07-4000146518 |  | AUD-2026-06-2000013155ACN-2026-07-4000146518 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146523 | Open |  |  | The displayed Single Line Diagram (SLD) contains outdated and incomplete details. | 6.6 | SLD | 1485 | AKOLA DEPOT | Update the SLD with the latest information and ensure all required details are incorporated. | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146523 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146523 | 2026-08-24 | 56.7538 | 394 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146523 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013155ACN-2026-07-4000146523 |  | AUD-2026-06-2000013155ACN-2026-07-4000146523 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | LONI LOCATION VISIT 18.05.2026 | 2026-05-18 | AUD-2026-07-2000016452 | 2026-05-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146533 | Open |  |  | Bitumen is found to be on annullar plates of tanks wherein bitumen coating is repaired. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1584 | LONI TERMINAL | Fresh Bitumen on annullar plates to be removed | SOD | Marketing | WZ | 2026-06-30 |  | 2 |  | S2 | F1 | 2026-06-30 | AUD-2026-07-2000016452ACN-2026-07-4000146533 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016452ACN-2026-07-4000146533 | 2026-10-15 | 4.7538 | 302 | >20 | AUD-2026-07-2000016452 - ACN-2026-07-4000146533 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016452ACN-2026-07-4000146533 |  | AUD-2026-07-2000016452ACN-2026-07-4000146533 | 21 |  | 27 | 80 | 18 | 18 | 44
[5 empty] | LONI LOCATION VISIT 18.05.2026 | 2026-05-18 | AUD-2026-07-2000016452 | 2026-05-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146535 | Open |  |  | Painting of tank railings, ladder and roofs is observed to be worn off. | 6.1 |  | 1584 | LONI TERMINAL | Painting of tank railings, ladder and roofs to be done where paint is worn off. | SOD | Marketing | WZ | 2026-06-30 |  | 4 |  | S2 | F2 | 2026-06-30 | AUD-2026-07-2000016452ACN-2026-07-4000146535 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016452ACN-2026-07-4000146535 | 2026-10-15 | 4.7538 | 302 | >20 | AUD-2026-07-2000016452 - ACN-2026-07-4000146535 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016452ACN-2026-07-4000146535 |  | AUD-2026-07-2000016452ACN-2026-07-4000146535 | 21 |  | 27 | 80 | 18 | 18 | 44
|  |  |  | Discussion with Zone | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146543 | Open | SUKHWANT SINGH KAHLON | 2026-07-31 | YES | 1.3 | Pending issues reviewed | 1551 | VASCO BLACK OIL TERMINAL | Pending payments to IOC on way leave charge/ Common Jetty line maintenance Charges PRF prepared & Send it for payment | SOD | Marketing | WZ | 2026-07-31 |  | 9 |  | S3 | F3 | 2026-07-31 | AUD-2026-07-2000016454ACN-2026-07-4000146543 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146543 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146543 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000016454ACN-2026-07-4000146543 |  | AUD-2026-07-2000016454ACN-2026-07-4000146543 | 21 |  | 27 | 80 | 31 | 31 | 48
|  |  |  | TK8 undertaken for cleaning | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146544 | Open | SUKHWANT SINGH KAHLON | 2026-07-31 | YES | 1.5 | HQO / Zonal support required identified | 1551 | VASCO BLACK OIL TERMINAL | TK5 & TK8 internal Inspection & TK Painting after Tank cleaning TK8 undertaken for cleaning | SOD | Marketing | WZ | 2026-12-30 |  | 9 |  | S3 | F3 | 2026-12-30 | AUD-2026-07-2000016454ACN-2026-07-4000146544 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146544 | 2026-09-04 | 45.7538 | 485 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146544 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000016454ACN-2026-07-4000146544 |  | AUD-2026-07-2000016454ACN-2026-07-4000146544 | 21 |  | 27 | 80 | 31 | 31 | 70
[5 empty] | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146545 | Open |  |  | NO | 2.2 | Double contingency scenario simulated; observations recorded | 1551 | VASCO BLACK OIL TERMINAL | To be conducted level-2 drill | SOD | Marketing | WZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-07-2000016454ACN-2026-07-4000146545 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146545 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146545 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016454ACN-2026-07-4000146545 |  | AUD-2026-07-2000016454ACN-2026-07-4000146545 | 21 |  | 27 | 80 | 31 | 31 | 48
|  |  |  | 3 Street Lights were changed | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146546 | Open | SUKHWANT SINGH KAHLON | 2026-07-31 | YES | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1551 | VASCO BLACK OIL TERMINAL | Few Lights required to be replaced | SOD | Marketing | WZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-07-2000016454ACN-2026-07-4000146546 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146546 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146546 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016454ACN-2026-07-4000146546 |  | AUD-2026-07-2000016454ACN-2026-07-4000146546 | 21 |  | 27 | 80 | 31 | 31 | 48
[5 empty] | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146547 | Open |  |  | YES | 2.4 | Security alertness checked (night-halt / surprise checks) | 1551 | VASCO BLACK OIL TERMINAL | More Frequency of night surprise check recommended | SOD | Marketing | WZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-07-2000016454ACN-2026-07-4000146547 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146547 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146547 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016454ACN-2026-07-4000146547 |  | AUD-2026-07-2000016454ACN-2026-07-4000146547 | 21 |  | 27 | 80 | 31 | 31 | 48
|  |  |  | Location planning to install system locally without waiting for NPCB | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146548 | Open | SUKHWANT SINGH KAHLON | 2026-07-31 | Old analogue system non functional | 2.6 | CCTV functioning checked | 1551 | VASCO BLACK OIL TERMINAL | Proposed for new System in NPCB25-26. Required Budget allocation Rs 10 Lakhs | SOD | Marketing | WZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-07-2000016454ACN-2026-07-4000146548 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146548 | 2026-09-04 | 45.7538 | 576 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146548 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016454ACN-2026-07-4000146548 |  | AUD-2026-07-2000016454ACN-2026-07-4000146548 | 21 |  | 27 | 80 | 31 | 31 | 83
[5 empty] | VASCO BOT VISIT 30.05.2026 | 2026-05-30 | AUD-2026-07-2000016454 | 2026-05-30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146549 | Open |  |  | YES | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1551 | VASCO BLACK OIL TERMINAL | Advised Location to expedite the scrap disposal . Advised to make scrap free by 30.04.2027 | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-07-2000016454ACN-2026-07-4000146549 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016454ACN-2026-07-4000146549 | 2026-09-04 | 45.7538 | 576 | >20 | AUD-2026-07-2000016454 - ACN-2026-07-4000146549 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016454ACN-2026-07-4000146549 |  | AUD-2026-07-2000016454ACN-2026-07-4000146549 | 21 |  | 27 | 80 | 31 | 31 | 83
[5 empty] | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146562 | Open |  |  | expansion valve to be provided in p/l section coming from Siding | 6.3 | Safety | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-08-31 |  | 4 |  | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146562 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146562 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146562 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146562 |  | AUD-2026-07-2000016455ACN-2026-07-4000146562 | 21 |  | 27 | 80 | 0 | 0 | 52
|  |  |  | folllowup done but no corrective action | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146567 | Open | GAKHAR NAVEEN | 2026-08-19 | yes | 2.7 | VA alerts checked / analysed | 1588 | VASHI WHITE OIL TERMINAL | followup to be done with vendor | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146567 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146567 | 2026-10-14 | 5.7538 | 272 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146567 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016456ACN-2026-07-4000146567 |  | AUD-2026-07-2000016456ACN-2026-07-4000146567 | 21 |  | 27 | 80 | 15 | 11 | 39
[5 empty] | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146568 | Open |  |  | yes | 2.8 | Access control systems checked | 1588 | VASHI WHITE OIL TERMINAL | ACESS control being correted from visitor to via vendor arequest | SOD | Marketing | WZ | 2026-05-31 |  | 1 |  | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146568 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146568 | 2026-10-14 | 5.7538 | 272 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146568 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016456ACN-2026-07-4000146568 |  | AUD-2026-07-2000016456ACN-2026-07-4000146568 | 21 |  | 27 | 80 | 15 | 11 | 39
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-31 | Location submitted comprehensive insepction report for the compound wall. The rectification works are initiated and under progress.Budget required for civil repair jobs were submitted. location has cleared the vegetations near the compound wall for access provisions.All PCC and brickwork done at different sections of the compound wall where immediate intervention is needed. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130102 | Closed | SRIJIN S | 2026-07-31 | Location has already initiated clearing the vegetation along the compound wall. Its being observed that vegetation was grown along the compound wall at majority of sections. Small holes and cracks observed at some portions of the compound wall. Location has initiated the rectification of the damaged portions of the compound wall. | 1.5 | HQO / Zonal support required identified | 1833 | COCHIN BLACK TERMINAL | Location to submit civil consultant inspection report and assess condition of compound wall urgently. Location to complete all the rectification works at the earliest. Budget required for civil repair jobs across the compound wall to be submitted | SOD | Marketing | CZR | 2026-12-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S2 | F3 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130102 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130102 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130102 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130102 | AUD-2026-05-2000012202ACN-2026-05-4000130102 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-31 | Tenders floated for the jockey pump and monoblock pump pipeline jobs. 2 numbers of surplus Jockey pumps transferred from delhi terminal.civil jobs and foundation jobs completed.pipeline jobs is under progress. project extension approval taken till 30.09.2026. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130104 | Closed | SRIJIN S | 2026-07-31 | Discussed about target completion in view of FY end. Time extension approval taken for 2 nos open NPCB projects till June 2026. Theprojects were reviewed and advised to close the ARs before 30th June. | 1.8 | Improvement plans discussed | 1833 | COCHIN BLACK TERMINAL | Open NPCB projects (2 no.) reviewed, it is noted that zero expenditure is booked till date. Tenders are to be floated urgently for both the projects. Location to explore the possibility of getting jocky pumps from any other location else tender is to be floated. All other civil, piping works are to be initiated without any further delay. Based on the above, project time extension proposal needs to be worked out based on the estimated delivery period of pumps, fittigns etc. | SOD | Marketing | CZR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 6 | ASSET INTEGRITY | S2 | F3 | 2026-09-30 | AUD-2026-05-2000012202ACN-2026-05-4000130104 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130104 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130104 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130104 | AUD-2026-05-2000012202ACN-2026-05-4000130104 | 21 | 21 | 27 | 80 | 2 | 0 | 57 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-31 | security gap assessment carried out and points are being closed in time bound manner. instructed security guard to give the security briefing to all the visitors. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130106 | Closed | SRIJIN S | 2026-07-31 | Surprise night inspection is being carriend out on monthly basis.Interacted with security and their awareness on emergency preparedness found to be satisfactory. Total Four security available. Documentation in gate found satisfactory. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1833 | COCHIN BLACK TERMINAL | Advise to carry out security gap assessement w.r.t dedicated HLSA team as per HQO email for all applicable points and draw action plan for timely compliances. SG at main gate to give safety briefing for all the visitors | SOD | Marketing | CZR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | EMERGENCY | S2 | F3 | 2026-06-30 | AUD-2026-05-2000012202ACN-2026-05-4000130106 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130106 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130106 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130106 | AUD-2026-05-2000012202ACN-2026-05-4000130106 | 21 | 21 | 27 | 80 | 2 | 0 | 44 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-08 | PPE Matrix is displayed prominently and all workmen is using the PPE's acccordingly | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130114 | Closed | SRIJIN S | 2026-07-08 | House keeping is well maintained at terminal. Observed workman using PPE`s. | 3.15 | Housekeeping & PPE usage checked | 1833 | COCHIN BLACK TERMINAL | Location to display PPE Matrix prominently | SOD | Marketing | CZR | 2026-05-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-30 | AUD-2026-05-2000012202ACN-2026-05-4000130114 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130114 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130114 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130114 | AUD-2026-05-2000012202ACN-2026-05-4000130114 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-08 | Timely closure of permits are done | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130116 | Closed | SRIJIN S | 2026-07-08 | Permits checked and available. Timely closure of permits are being done. | 4.2 | All activies are being performed with Permits and with all PPE in place. | 1833 | COCHIN BLACK TERMINAL | Ensure timely closure of work permits in SAP also. | SOD | Marketing | CZR | 2026-05-31 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-31 | AUD-2026-05-2000012202ACN-2026-05-4000130116 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130116 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130116 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130116 | AUD-2026-05-2000012202ACN-2026-05-4000130116 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-08 | PM jobs are closing timely on SAP | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130118 | Closed | SRIJIN S | 2026-07-08 | PM jobs to be monitored closely and closed progressively as and when the jobs are completed. | 4.4 | PM jobs are being done with the time line, where as the jobs are being done in the last week of month. | 1833 | COCHIN BLACK TERMINAL | PM jobs are to be attended progressively and ensured closure in SAP also | SOD | Marketing | CZR | 2026-05-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 3 | PROCESS SAFETY | S1 | F3 | 2026-05-31 | AUD-2026-05-2000012202ACN-2026-05-4000130118 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130118 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130118 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130118 | AUD-2026-05-2000012202ACN-2026-05-4000130118 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 48
[5 empty] | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146605 | Open |  |  | yes | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 3562 | VASHI BO TML | training programmand refresher course to be organized | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146605 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146605 | 2026-09-15 | 34.7538 | 302 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146605 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016505ACN-2026-07-4000146605 |  | AUD-2026-07-2000016505ACN-2026-07-4000146605 | 21 |  | 27 | 80 | 9 | 9 | 44
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-07-08 | Company owned jeeps to be disposed off | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125863 | Closed | SRIJIN S | 2026-07-08 | RFD for two company owned jeeps completed | 4.5 | scrap disposal progress reviwed/scrap free environment checked. | 1833 | COCHIN BLACK TERMINAL | Company owned jeeps to be disposed off. Upiliftment to be completed | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ENVIRONMENTAL | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125863 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125863 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125863 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125863 | AUD-2026-03-2000011134ACN-2026-03-4000125863 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 48
ALBY ABRAHAM ARACKAL | 2026-07-31 | SRIJIN S | 2026-04-21 | Gantry cleanliness is being maintained on regular basis | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | POST-VISIT REPORTING | ACN-2026-03-4000125864 | Closed | SRIJIN S | 2026-04-21 | Gantry cleanliness to be maintained | 5 | Gantry cleanliness to be maintained | 1833 | COCHIN BLACK TERMINAL | Gantry cleanliness to be maintained | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ENVIRONMENTAL | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125864 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125864 | 2026-09-08 16:00 | 41.0872 | 333 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125864 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125864 | AUD-2026-03-2000011134ACN-2026-03-4000125864 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | Work is under progress | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124920 | Closed | SINGH KUNAL | 2026-04-03 | HCD testing done. 1. at TWD PH, open Path HCD no. 2401 checked & found ok for 40% alarms. Control room & field hooters found functioning 2. open path HCD for TK101D was checked. Field hooter audio not working. 3. Point type HCD for MS dyke checked & found ok .filed hooter & control room hooter functioning properly | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1410 | VADODARA TERMINAL | Hooter to be repaired/rectified | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124920 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124920 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124920 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124920 | AUD-2026-03-2000010974ACN-2026-03-4000124920 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | VTS records are being maintained | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124921 | Closed | SINGH KUNAL | 2026-07-31 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124921 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124921 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124921 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010974ACN-2026-03-4000124921 | AUD-2026-03-2000010974ACN-2026-03-4000124921 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | Faulty lock has been sent to vendor M/s. Sterna for verification as per the circular.. Lock is replaced. | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124922 | Closed | SINGH KUNAL | 2026-07-31 | Yes, records maintained following trucks checked for EM lock with unauthorised key 1. TT no. GJ23Y8788- 12 KL - DCT- M/s Dayabhai& Sons, Aklav Top:- HE11271 Bottom:- HE11272 found ok 2. TT no. GJ06BT6185- 20 KL- TPT- M/s Balaji Transport Top:- HE7219 (ok) Bottom:- HE7220 (not ok) 3. TT No. GJ17UU6521- 12 KL- DCT- Shri Ranchodrai Petroleum Top:- HE27584 Bottom:- HE27583 found ok 4. TT No. GJ17UU2133- 12 KL- DCT- Shri Nath Petroleum, Halol Top:- HE11211 Bottom:- HE11212 found ok | 3.5 | EM Lock SOP compliance verified | 1410 | VADODARA TERMINAL | Faulty lock of TT no. GJ06BT6185 to be replaced Location to ensure correction action in line with circular for verification within15 days | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124922 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124922 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124922 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010974ACN-2026-03-4000124922 | AUD-2026-03-2000010974ACN-2026-03-4000124922 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Corrective action has been discussed and recorded in Quarterly Safety Committee Meeting (Q1) | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131770 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Location has been conducting the mock fire drills on monthly basis covering various scenarios recommended in ERDMP. Report under preparation for Apr'26 mock drill. Report reviewed for mock drill month Mar'26. Location of Emergency1: MS TANK NO 15, Location ofEmergency2: TWD PUMP HOUSE . Observation recorded in mock drill While carrying an injured person, the head should always face forward, and one person should accompany alongside. Compliance pending. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131770 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131770 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131770 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131770 | AUD-2026-05-2000012564ACN-2026-05-4000131770 | 21 | 21 | 27 | 80 | 2 | 2 | 42 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Alocohol test has been carrying out for night shift employee/contract workmen/security entering in depot and record is available. Further, Training has been conducted for security person for TAS parameters available in security screen. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131772 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | During night visit between 0017 to 0117 on date 14.05.2026, Security deployed at gate found taking nap. Record of carrying alocohol test is not availalbe with location. Location to ensure 100% alocohol test for employee/contract workmen/security entering/workinginside depot premise in night shift and record shall be kept. operation Security guard not aware of fire engine sequence. As per night shift security guard, Standby fire engine will start first in case of emergency which is under breakdown. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131772 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131772 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131772 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131772 | AUD-2026-05-2000012564ACN-2026-05-4000131772 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | All 52 CCTVs are working fine. Time is also corrected as per actual | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131773 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | 46 cameras out of 51 are currently working. Time clock of CCTV is not correct. | 2.6 | CCTV functioning checked | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131773 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131773 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131773 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131773 | AUD-2026-05-2000012564ACN-2026-05-4000131773 | 21 | 21 | 27 | 80 | 2 | 2 | 42 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Dyke -02 HCD has been repositioned and Dyke-04 HCD is repaired and installed. Now, All the HCDs are working fine | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131774 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Dyke-2 Open Path HCD was tested using the 20% and 40% LEL testing kit. Found working how ever against 20% LEL, reading 30% and against 40% 60% reading is showing in control room. Dyke no 2 point type HCD is not positioned over pit to capture the presence of vapour. Dyke 4 point HCD is not working. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131774 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131774 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131774 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131774 | AUD-2026-05-2000012564ACN-2026-05-4000131774 | 21 | 21 | 27 | 80 | 2 | 2 | 42 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | All spares/surplus available material in all areas collected. List made and attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140188 | Closed | SINGH PREETI | 2026-07-31 | Comments are updated for abnormal variation. All spares/surplus available material in all areas to be collected and list to be made by 24th June 2026. | 3.9 | Abnormal variations / unused assets reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-06-24 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-24 | AUD-2026-06-2000013929ACN-2026-06-4000140188 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140188 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140188 | 532 | 8294 | 21 | 8294 | 117 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140188 | AUD-2026-06-2000013929ACN-2026-06-4000140188 | 21 | 21 | 27 | 80 | 1 | 1 | 43 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | 15 Nos. Spare hose requirement, Qty included in Consolidated PR 5600071581 for zone. PR sent to CPO for procurement of spare hoses. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140816 | Closed | SINGH PREETI | 2026-07-31 | No. of spare hoses against requirement to be checked. | 6.19 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140816 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140816 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140816 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140816 | AUD-2026-06-2000013929ACN-2026-06-4000140816 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | Scrap and usable material has been segregated. All usable material has been collected in Store and list prepared. Scrap identification done, scrap disposal to be initiated. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140197 | Closed | SINGH PREETI | 2026-07-31 | Location to identify scrap and usable material and initiate scrap disposal process. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140197 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140197 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140197 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140197 | AUD-2026-06-2000013929ACN-2026-06-4000140197 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145548 | Open |  |  | Conduted | 1.2 | Performance review conducted | 1554 | MR-II TERMINAL | Painting needs to be started, rusting has beginning to apper on structure.5 years period is also overdue | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000145548 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000145548 | 2026-10-16 | 3.7538 | 394 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000145548 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000145548 |  | AUD-2026-07-2000016409ACN-2026-07-4000145548 | 21 |  | 27 | 80 | 6 | 5 | 57
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146650 | Open |  |  | Painting of tanks and infrastracture is to be scheduled as facility is 5 years old. Maintenace of pumps to be streamlined. Goose neck for bulk air eliminator sat white gantry | 1.8 | Improvement plans discussed | 1554 | MR-II TERMINAL | XX | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-07-2000016409ACN-2026-07-4000146650 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146650 | 2026-10-16 | 3.7538 | 576 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146650 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146650 |  | AUD-2026-07-2000016409ACN-2026-07-4000146650 | 21 |  | 27 | 80 | 6 | 5 | 83
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146652 | Open |  |  | Last report dt 17.06.2026 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1554 | MR-II TERMINAL | Lux level low at control room. Location to rectify | SOD | Marketing | WZ | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146652 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146652 | 2026-10-16 | 3.7538 | 333 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146652 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146652 |  | AUD-2026-07-2000016409ACN-2026-07-4000146652 | 21 |  | 27 | 80 | 6 | 5 | 48
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146657 | Open |  |  | EM Locks SOP SOP needs to be resubmitted as Zonal HSE cordinator has changed | 3.5 | EM Lock SOP compliance verified | 1554 | MR-II TERMINAL | Location to submit to Zone | SOD | Marketing | WZ | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146657 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146657 | 2026-10-16 | 3.7538 | 333 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146657 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146657 |  | AUD-2026-07-2000016409ACN-2026-07-4000146657 | 21 |  | 27 | 80 | 6 | 5 | 48
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146658 | Open |  |  | Audi Alarm not availble for Dyke drains valves | 3.12 | Critical alarms checked & corrective actions reviewed | 1554 | MR-II TERMINAL | Location to expedite revival of Dyke drain intergation in TAS | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146658 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146658 | 2026-10-16 | 3.7538 | 394 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146658 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146658 |  | AUD-2026-07-2000016409ACN-2026-07-4000146658 | 21 |  | 27 | 80 | 6 | 5 | 57
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146659 | Open |  |  | YES. VRU MOC still pending approval | 3.17 | MOC status reviewed | 1554 | MR-II TERMINAL | Location to submit to Zone along with VRU operations SOP | SOD | Marketing | WZ | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-07-2000016409ACN-2026-07-4000146659 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146659 | 2026-10-16 | 3.7538 | 363 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146659 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146659 |  | AUD-2026-07-2000016409ACN-2026-07-4000146659 | 21 |  | 27 | 80 | 6 | 5 | 52
[5 empty] | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146662 | Open |  |  | Annualr plates of tanks are rusting. | 4.2 | Maintenance activities reviewed | 1554 | MR-II TERMINAL | Location to do immediate spary painiting before rains | SOD | Marketing | WZ | 2026-07-31 |  | 4 |  | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146662 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146662 | 2026-10-16 | 3.7538 | 333 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146662 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016409ACN-2026-07-4000146662 |  | AUD-2026-07-2000016409ACN-2026-07-4000146662 | 21 |  | 27 | 80 | 6 | 5 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Same shall be ensured in future. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131790 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | QC sample register was found unsigned since 31.01.2026 and disposal column was not signed since 11.01.2026. However sample retention and disposal is being done regularly. | 6.1 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131790 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131790 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131790 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131790 | AUD-2026-05-2000012564ACN-2026-05-4000131790 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Same is corrected. Now, Reconciliation has been carried out on Monthly basis | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131792 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Security gate pass register found not updated and not matching with online gate pass record for returnable material. | 6.3 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131792 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131792 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131792 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131792 | AUD-2026-05-2000012564ACN-2026-05-4000131792 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Sprinkler line has been repaired. Now, no leakage is observed | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131784 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | During field round of Tank farm area, pump house, Sample Room, Fire Engine shed etc, housekeeping and clearance of roads around tank farm is satisfactory. Accumulation of water and algae is observed peripheral drain of TK24 due to water leakage from sprinkler. | 3.15 | Housekeeping & PPE usage checked | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131784 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131784 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131784 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131784 | AUD-2026-05-2000012564ACN-2026-05-4000131784 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | All the scrap has been disposed except Flood light Tower. Routing is awaited for the same. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131789 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Disposal of dismantled flood light tower,Fire Extinguishers,45KVA Capacitor, Concertina Coil & Angle Disposal, Misc. Scrap Disposal(15MT), 10KVA UPS and Panel is in progress. Same to be expedited. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012564ACN-2026-05-4000131789 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131789 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131789 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131789 | AUD-2026-05-2000012564ACN-2026-05-4000131789 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Monthly checklist has been filled properly. Same shall be ensured in future also | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131793 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Monthly inspection checklist of battery was found partially filled. | 6.4 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131793 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131793 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131793 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131793 | AUD-2026-05-2000012564ACN-2026-05-4000131793 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | JCB/Tractor hours are maintained and recorded at Security Gate as per practice. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131794 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Upon review of GRN of M/s Rajnath, unsigned measurement sheet was attached with the records. Supporting document for JCB and tractor working hours was not attached with the bill. | 6.5 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131794 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131794 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131794 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131794 | AUD-2026-05-2000012564ACN-2026-05-4000131794 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Observation has been closed as per target date. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131795 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Location has not closed previous sr management inspection audit observation inspite zonal communications. | 6.6 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131795 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131795 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131795 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131795 | AUD-2026-05-2000012564ACN-2026-05-4000131795 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Training has been conducted to all security person and recorded. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131796 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | Security guard Sh. Yogendra was asked to operate HVLR, he expressed his inability to operate the HVLR as he forgot the procedure. | 6.7 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131796 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131796 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131796 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131796 | AUD-2026-05-2000012564ACN-2026-05-4000131796 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | Training given to TT Crew for earthing, to connect earthing separately to tanker and body. Training photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140193 | Closed | SINGH PREETI | 2026-07-31 | • Training to be given to be TT Crew for earthing, earthings to be connected separately to tanker and body. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140193 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140193 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140193 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140193 | AUD-2026-06-2000013929ACN-2026-06-4000140193 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-06-27 | 10 additional eletric poles & 25 additional lights provided in are low lux areas. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125472 | Closed | KUMAR NITISH | 2026-06-27 | Lux levels were checked in night time and observed not meeting at some areas as work is already in progress for provisioning of additional lights and repair of existing lights to meet OISD 244 lux requirements. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125472 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125472 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125472 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125472 | AUD-2026-03-2000010720ACN-2026-03-4000125472 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-06-27 | Regular training & assessment of security isbeing carried out. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125473 | Closed | KUMAR NITISH | 2026-06-27 | Yes checked and observed that improvement/training needed. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125473 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125473 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125473 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125473 | AUD-2026-03-2000010720ACN-2026-03-4000125473 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-06-27 | Vessel & Control Room Log Book is now being maintained properly. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125477 | Closed | KUMAR NITISH | 2026-06-27 | During field round of Tank farm area, pump house, foam shed etc, housekeeping is satisfactory and most of the places are free from vegetation. All contract workmen working in hazardous area were using the PPEs are per applicability. Logbooks in Control Room and Vessel were reviewed and observed that most of the details like, flow rates, qty etc are mentioned but some of the fields are still not been captured in available format. Location has been advised to ensure all relevant details to be captured in both Control Room & Vessel logbooks. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125477 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125477 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125477 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125477 | AUD-2026-03-2000010720ACN-2026-03-4000125477 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-06-27 | Inverter tripping issue resolved. Current daily generation is more than 100%. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125478 | Closed | KUMAR NITISH | 2026-06-27 | Solar generation for a period Apr’25 to Jan’26 was reviewed and observed that frequent inverter tripping was happened due to which generation on those days were affected. Location has been advised to ensure close monitoring of solar generation for generation as per design basis. | 4.2 | Maintenance activities reviewed | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010720ACN-2026-03-4000125478 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125478 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125478 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125478 | AUD-2026-03-2000010720ACN-2026-03-4000125478 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Night inspections are being done regularly and reports being shared with zone. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145692 | Closed | KUMAR NITISH | 2026-07-31 | Surprise night inspections are not being conducted at the location. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000145692 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145692 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145692 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145692 | AUD-2026-06-2000012346ACN-2026-07-4000145692 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | "Coastal performance monitoring being done regularly. Daily Reconciliation being done. Sample records are being maintained properly." | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145693 | Closed | KUMAR NITISH | 2026-07-31 | Location to monitor coastal performance, ensure daily reconcilation and sample room related records/sample keeping shall be improved. | 1.8 | Improvement plans discussed | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000145693 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145693 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145693 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145693 | AUD-2026-06-2000012346ACN-2026-07-4000145693 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | HVLR2 & HVLR3 repair completed. Both HVLRs are working satisfactorily now. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145696 | Closed | KUMAR NITISH | 2026-07-31 | Dyke-3 open-path HCD was checked and found working. Alarms were generated in both the field and control room. Point-type HCD for Dyke-3 was checked and found working. The location should position the HCD above the pit. Dyke-3 dyke valve indicator was working properly. Alarm was generated in both the control room and field. HVLR No. 2 was operated by Shri Anish. Performance was satisfactory; however, the nozzle gets stuck while changing from jet to spray mode. HVLR No. 3 could not be operated due to non-opening of the water MOV. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000145696 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145696 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145696 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145696 | AUD-2026-06-2000012346ACN-2026-07-4000145696 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Water draining of tK13 complete. Physical and TAS Water Dip now within limit. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145697 | Closed | KUMAR NITISH | 2026-07-31 | TK-11 Reference Height: As per record: 1480.3 cm, Actual in field: 1480.3 cm Product Dip: TAS Dip: 699.7 cm, Physical Dip: 699.9 cm Water Dip: TAS: Nil, Physical: Nil TK-13 Reference Height: As per record: 1475.0 cm, Actual in field: 1475.0 cm ProductDip: TAS Dip: 836.7 cm, Physical Dip: 836.5 cm Water Dip: TAS: 5 cm,Physical: 8.5 cm | 3.7 | Inventory physical dip of minimum two tanks taken | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000145697 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145697 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145697 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145697 | AUD-2026-06-2000012346ACN-2026-07-4000145697 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Workers have been counselled regarding usage of PPEs. Vendor has been structly warned for PPE & Safety Complaince. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145698 | Closed | KUMAR NITISH | 2026-07-31 | During the field round of the tank farm area, pump house, sample room, fire engine shed, etc., housekeeping and road clearance around the tank farm were found satisfactory. An MDPL staff member (M/s Jai Bajrang) was found wearing a safety helmet without fastening the chin strap. few workers of M/s Azad Singh at TK-17 was found carrying out tank dismantling activities without wearing a safety helmet. | 3.15 | Housekeeping & PPE usage checked | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | LACK OF TRAINING OR COMPETENCY | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000145698 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145698 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145698 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145698 | AUD-2026-06-2000012346ACN-2026-07-4000145698 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | "1. Jockey pump repair complete. 2. Cooling line repair of FE1 complete. 3. Lube oil lekage issue rectified for FE5. 4. WTH & OTH alarms are now working properly for Transformr 1." | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146500 | Closed | KUMAR NITISH | 2026-07-31 | PM activities are being carried out with proper work permits. The following observations were noted: Leakage observed from the gland of Jockey Pump-2. Water leakage observed from the cooling line of FE-01. Lube oil dripping observed in FE-05. For Transformer-1, WTH and OTH alarms were not working. | 4.2 | Maintenance activities reviewed | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146500 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146500 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146500 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146500 | AUD-2026-06-2000012346ACN-2026-07-4000146500 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | ARs being closed as per schedule. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146501 | Closed | KUMAR NITISH | 2026-07-31 | SOD-242304 – Tank Roof Replacement (TK-09), Mundra: Work in progress. ECM note submitted for time extension. SOD-242305 – Tank Roof Replacement (TK-12), Mundra: Work in progress. ECM note submitted for time extension. SOD-242654 – Tank Roof Replacement (TK-01 &TK-04), Mundra: Work in progress. ECM note submitted for time extension. SOD-251881 – Control Room Upgradation, Mundra Terminal: Work completed. Capitalization pending. SOD-252134 – Audit Compliance, Mundra Terminal: Soft starter installation pending. EDC: June2026. SOD-252146 – Replacement of VHF Sets, Mundra Terminal: Supply completed. Capitalization pending. SOD-252289 – MOV Actuator for Mundra Terminal: Supply completed. Installation in progress. EDC: 30.09.2026. SOD-252290 – Slop Tanks IFR Conversion: TK-17 dismantling completed. Fabrication of the new tank is in progress and is expected to be completed by September 2026. After TK-17, TK-16will be taken up for repair. EDC: January 2027. SOD-252287 – Water Tank Revamping at Mundra Terminal: TK-02 dismantling completed.Plate erection is in progress and expected to be completed by September 2026. Thereafter, TK-01 will be taken up for repair and maintenance. EDC: February 2027. SOD-252285 – ITT Line Revamping at Mundra Terminal: Supply completed. Line flushing for SKO is in progress. EDC: March 2027. SOD-251975 – TAS UPS at Mundra Terminal: Battery supply is delayed. Time extension may be required. | 4.3 | Project progress reviewed | 1546 | Mundra Terminal-MDPL | Location to ensure closure of AR scheduled for closure in Q1. | SOD | Marketing | NWR | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012346ACN-2026-07-4000146501 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146501 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146501 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146501 | AUD-2026-06-2000012346ACN-2026-07-4000146501 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Dyke wall cable entry point sealed. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146502 | Closed | KUMAR NITISH | 2026-07-31 | An opening was found in the cable entry point on the Dyke-5 wall. | 6.1 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146502 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146502 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146502 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146502 | AUD-2026-06-2000012346ACN-2026-07-4000146502 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | FE01 Alarm issue resolved. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146505 | Closed | KUMAR NITISH | 2026-07-31 | Overspeed and LLOP alarms are working for FE-01; however, the high water temperature alarm is not functioning. | 6.4 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146505 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146505 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146505 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146505 | AUD-2026-06-2000012346ACN-2026-07-4000146505 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Counselling carried out for all three alerts . Two alerts are of Maintenane Workmen . Letter obtained from Him . One Alert is for Electrician for Fire Engine Shed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137159 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | 1. PPE non compliance TAS_1583_SOP043_300326_000054 date 30.03.2026 is closed with remarks PPE TO BE USE. No action taken against person is not provided. 2. PPE non compliance TAS_1583_SOP043_300326_000052 is closed with remarks PPE TO BE USE. No action taken against person is not provided. 3. PPE non compliance TAS_1583_SOP043_300326_000056 is closed with remarks We guide him to use properPPE during work. No action taken against person is not provided. | 2.7 | VA alerts checked / analysed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137159 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137159 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137159 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137159 | AUD-2026-06-2000012347ACN-2026-06-4000137159 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Details Updated in Surplus Portal and shared with NWZ | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137167 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Comments are being recorded for abnormal variation. Location to update surplus/idle assets in surplus portal. | 3.9 | Abnormal variations / unused assets reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137167 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137167 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137167 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137167 | AUD-2026-06-2000012347ACN-2026-06-4000137167 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | ESD is working at TT Gantry | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137178 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Emergency stop not working for MS at gantry | 6.4 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137178 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137178 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137178 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137178 | AUD-2026-06-2000012347ACN-2026-06-4000137178 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Gate is in closed condition | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137160 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | C Bacs system is working how ever gate installed near security building was found open which was allowing direct entry to license area bypassing provision of license area Cbacs | 2.8 | Access control systems checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137160 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137160 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137160 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137160 | AUD-2026-06-2000012347ACN-2026-06-4000137160 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Not applicable to Kandla . | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137189 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | 53 out of 55 cameras are currently operational. Backup is available for 92 days. | 2.6 | CCTV functioning checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-06-2000012347ACN-2026-06-4000137189 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137189 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137189 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137189 | AUD-2026-06-2000012347ACN-2026-06-4000137189 | 21 | 21 | 27 | 80 | 2 | 2 | 46 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Not related to kandla | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137191 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | TK-11 Reference Height: As per record: 1480.3 cm, Actual in field: 1480.3 cm Product Dip: TAS Dip: 699.7 cm, Physical Dip: 699.9 cm Water Dip: TAS: Nil, Physical: Nil TK-13 Reference Height: As per record: 1475.0 cm, Actual in field: 1475.0 cm ProductDip: TAS Dip: 836.7 cm, Physical Dip: 836.5 cm Water Dip: TAS: 5 cm,Physical: 8.5 cm | 3.7 | Inventory physical dip of minimum two tanks taken | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012347ACN-2026-06-4000137191 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137191 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137191 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137191 | AUD-2026-06-2000012347ACN-2026-06-4000137191 | 21 | 21 | 27 | 80 | 2 | 2 | 41 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Not related to kandla | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137177 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | DP gauge found broken and not working at Bay no 4. | 6.3 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137177 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137177 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137177 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137177 | AUD-2026-06-2000012347ACN-2026-06-4000137177 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Noted for future compliance | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137174 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | PM orders are being closed on time. Location to ensure checklist are filled post careful inspection of equipment and accordingly records shall be updated on daily basis. | 4.4 | Quality of PM compliance reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137174 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137174 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137174 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137174 | AUD-2026-06-2000012347ACN-2026-06-4000137174 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Noted for future compliance | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137181 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Gate pass is not being prepapared of daily basis for drinking water including transport vehicle. Last gate was prepared on date 18.05.2026. | 6.7 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137181 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137181 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137181 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137181 | AUD-2026-06-2000012347ACN-2026-06-4000137181 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Project work is completed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137173 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Kandla_Facilities Realignment_Land surre: Work completed capitalisation in progress. | 4.3 | Project progress reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137173 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137173 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137173 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137173 | AUD-2026-06-2000012347ACN-2026-06-4000137173 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Revised MOC 3100001934 taken | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137169 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Location has not taken MOC for project related work. | 3.17 | MOC status reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137169 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137169 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137169 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137169 | AUD-2026-06-2000012347ACN-2026-06-4000137169 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Same is maintained and reviewd by officer regularly | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137168 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Yes, checked and observed to be within permissible limit. However location is preparing records on daily basis. Gap observed is more than 7 days. | 3.11 | MFM vs BCU totalizer comparison checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137168 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137168 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137168 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137168 | AUD-2026-06-2000012347ACN-2026-06-4000137168 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Surprise night inspection carried out by DSO/LIC fornighly basis | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137156 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Surprise night inspection is not being done by location. Gasohol samples collected at TT gantry for ethanol blending % checking isnot as per QC manual. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137156 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137156 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137156 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137156 | AUD-2026-06-2000012347ACN-2026-06-4000137156 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Training and infrmation provided to contract workman and non-management employees. | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137166 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Location is preparing manual gasohol sample by taking MS and ethanol seperately and then blending. EBP checked for this sample and kept for retention. Proper training shall be given to contract workmen and management/non management employee. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137166 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137166 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137166 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137166 | AUD-2026-06-2000012347ACN-2026-06-4000137166 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | tree is trimmed . Now clear view is available | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137182 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | CCTV FO 3-4 view is blocked by tree. | 6.8 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137182 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137182 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137182 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137182 | AUD-2026-06-2000012347ACN-2026-06-4000137182 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Valuations of Scrap disposal received from Valuator, reports received. Surplus material segregation and details shared. RFD Initiated from location .2. AR is closed for land surredner.3. Preventive maintenance is being carried out at location | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137157 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Location to ensure disposal of scrap material and shifting of surplus material to required location. Land surrender AR shall be closed as per project time line. Location shall carry out preventive maintenace activity properly in the field. | 1.8 | Improvement plans discussed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012347ACN-2026-06-4000137157 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137157 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137157 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137157 | AUD-2026-06-2000012347ACN-2026-06-4000137157 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Vendor has been counselled and given strict warning to follow the Safety SOP and wear proper PPE inside terminal premises | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137192 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | During the field round of the tank farm area, pump house, sample room, fire engine shed, etc., housekeeping and road clearance around the tank farm were found satisfactory. An MDPL staff member (M/s Jai Bajrang) was found wearing a safety helmet without fastening the chin strap. few workers of M/s Azad Singh at TK-17 was found carrying out tank dismantling activities without wearing a safety helmet. | 3.15 | Housekeeping & PPE usage checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012347ACN-2026-06-4000137192 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137192 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137192 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137192 | AUD-2026-06-2000012347ACN-2026-06-4000137192 | 21 | 21 | 27 | 80 | 2 | 2 | 41 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | VTS deviation records are maintained, and all corrosponding data available in mail and novex portal. | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137165 | Closed | TAK MITHLESH KUMAR | 2026-07-14 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012347ACN-2026-06-4000137165 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137165 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137165 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137165 | AUD-2026-06-2000012347ACN-2026-06-4000137165 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Earthing wire replaced for TK13. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146506 | Closed | KUMAR NITISH | 2026-07-31 | One copper wire used for shell-to-floating roof bonding in TK-13 was found broken. | 6.5 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146506 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146506 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146506 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146506 | AUD-2026-06-2000012346ACN-2026-07-4000146506 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Pump House Construction Work is completed and Structure Work is also completed . Electrical Cable Trench Work is under progress . Hooter and HCD working for Product Pump House | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-03-4000125498 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Not functional at Product pump house HCD. | 5.2 | Functioning of all Hooters in control room | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125498 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125498 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125498 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125498 | AUD-2026-03-2000011072ACN-2026-03-4000125498 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Faulty Foam Pourers replaced for TK13. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146507 | Closed | KUMAR NITISH | 2026-07-31 | In TK-13, three out of six foam pourers were not functioning satisfactorily: Leakage observed from Foam Pourer No. 2. Foam Pourer No. 4 was found choked. Leakage observed at the flange joint of Foam Pourer No. 3. | 6.6 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146507 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146507 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146507 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146507 | AUD-2026-06-2000012346ACN-2026-07-4000146507 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
MANKAR PRAFULLA | 2026-07-31 | KUMAR NITISH | 2026-07-31 | Night Patrolling register now being maintained with observations being recorded daily. | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146508 | Closed | KUMAR NITISH | 2026-07-31 | Observations are not being recorded in the register by security personnel during night patrolling. | 6.7 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-15 | AUD-2026-06-2000012346ACN-2026-07-4000146508 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146508 | 2026-09-18 | 31.7538 | 333 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146508 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146508 | AUD-2026-06-2000012346ACN-2026-07-4000146508 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | Documents are reviewed as per assigned frequency. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131797 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 | DSO and LIC to regularly review the location document for correctness and for ensuring real time updation. | 6.8 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131797 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131797 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131797 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131797 | AUD-2026-05-2000012564ACN-2026-05-4000131797 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 48
GIRI ANJANI KUMAR | 2026-07-31 | AGARWAL RAVI KUMAR | 2026-06-28 | No findings are mentioned. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131777 | Closed | AGARWAL RAVI KUMAR | 2026-06-28 |  | 3.1 | TT fittings & discipline checked | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-19 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131777 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131777 | 2026-08-06 | 74.7538 | 333 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131777 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131777 | AUD-2026-05-2000012564ACN-2026-05-4000131777 | 21 | 21 | 27 | 80 | 2 | 2 | 42 | 48
DEVA DHRUVA | 2026-07-31 | DEVA DHRUVA | 2026-07-31 | Lady guard taken and working since 20.04.2026. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122790 | Closed | DEVA DHRUVA | 2026-07-31 | Interacted with security and their awareness on emergency preparedness found to be satisfactory. Total 12 security available , No lady guard available, Process for recruiting lady guard is going on, documentation in gate found satisfactory. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1800 | HUBLI DEPOT | Lady guard to be available by 01.04.2026 | SOD | Marketing | SWZ | 2026-04-10 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-03-2000011030ACN-2026-03-4000122790 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122790 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122790 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122790 | AUD-2026-03-2000011030ACN-2026-03-4000122790 | 21 | 21 | 26 | 80 | 18 | 18 | 32 | 48
DEVA DHRUVA | 2026-07-31 |  |  | New unloading gantry commissioned and ethanol unloading in new area. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122793 | Closed | DEVA DHRUVA | 2026-07-31 | Ethanol TTs are being taken in to location premise with Gatepass, New dedicated Ethanol unloading Gantry ready manually. The same are being checked for dips with dip rods and certificates, Once unloading is completed the same are being verified for emptyness at out gate with two officers and security checks. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1800 | HUBLI DEPOT | The new unloading gantry to be commissioned by 30.04.2026 | SOD | Marketing | SWZ | 2026-04-20 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-20 | AUD-2026-03-2000011030ACN-2026-03-4000122793 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122793 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122793 | 532 | 8294 | 21 | 8294 | 182 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011030ACN-2026-03-4000122793 | AUD-2026-03-2000011030ACN-2026-03-4000122793 | 21 | 21 | 26 | 80 | 18 | 18 | 33 | 48
DAMARAKONDA VARSHITHA | 2026-07-31 |  |  | Conducted transporters meet and discussed regarding the bottom loading conversion schedule. Taken up with the RO and the sales officers for the toll updation and the routes updation. The issues related to inventory of EM locks, keys, and the VTS has been taken upwith the DGM transportation at the zone. | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128229 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | Transporters meeting conducted. Transporters were advised to expedite conversion of TTs to bottom loading. Some route corrections and Toll updations are pending.Inventory of VTS devices , EM locks and EM keys to be improved at location | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1937 | SURYAPET TERMINAL | Bottom loading conversion schedule to be advised to all Transporters and Dealers, to take up with RO for Toll updation as and when routes are updated by Sales officers, Inventory issues of EM locks, EM keys & VTS to be taken up with DGM Transportation and follow up with vendor | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128229 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128229 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128229 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128229 | AUD-2026-04-2000011400ACN-2026-04-4000128229 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Surplus item of Hubli IRD updated in surplus portal. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122794 | Closed | DEVA DHRUVA | 2026-07-31 | Inventory verification done and found ok.Surplus materials(DG set) already updated in surplus portal, Steelplates and seamless pipes to be in surplus portal | 3.9 | Abnormal variations / unused assets reviewed | 1800 | HUBLI DEPOT | Updation of surplus portal | SOD | Marketing | SWZ | 2026-04-05 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-05 | AUD-2026-03-2000011030ACN-2026-03-4000122794 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122794 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122794 | 532 | 8294 | 21 | 8294 | 197 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122794 | AUD-2026-03-2000011030ACN-2026-03-4000122794 | 21 | 21 | 26 | 80 | 18 | 18 | 31 | 48
DEVA DHRUVA | 2026-07-31 |  |  | k-factor updated for new W&M certificates on calibration chart and pending will be done during calibration in Dec 2026.all future calibrations | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122795 | Closed | DEVA DHRUVA | 2026-07-31 | Daily report of MFM Vs BCU totalizer being maintained, K-Factor changes in Dec 25 report checked and no abnormalities found. Local loading details being maintained. K-factor of MFMs changed on Dec 15th for bay 5 | 3.11 | MFM vs BCU totalizer comparison checked | 1800 | HUBLI DEPOT | Location to take up with W&M officer to incorporate K Factor on calibration chart in all future calibrations | SOD | Marketing | SWZ | 2026-05-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-05-31 | AUD-2026-03-2000011030ACN-2026-03-4000122795 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122795 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122795 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122795 | AUD-2026-03-2000011030ACN-2026-03-4000122795 | 21 | 21 | 26 | 80 | 18 | 18 | 39 | 48
DEVA DHRUVA | 2026-07-31 |  |  | One HVLR which was not operated in remote, has been corrected and now operating in remote. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122797 | Closed | DEVA DHRUVA | 2026-07-31 | All new tank farms checked. Painting of tanks found ok. No corrosion patches found. One HVLR valve not working in remote, checked the same in manual | 4.1 | Full Field round completed. | 1800 | HUBLI DEPOT | Rectification of valve in HVLR | SOD | Marketing | SWZ | 2026-04-05 | INSTRUMENTATION OR ALARM FAILURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-05 | AUD-2026-03-2000011030ACN-2026-03-4000122797 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122797 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122797 | 532 | 8294 | 21 | 8294 | 197 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122797 | AUD-2026-03-2000011030ACN-2026-03-4000122797 | 21 | 21 | 26 | 80 | 18 | 18 | 31 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Training to transporters planned on route violations , speed violations with Novex SOP needs to be conducted on regular basis. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122787 | Closed | DEVA DHRUVA | 2026-07-31 | Route correction are already completed by location however new devaiations are attended immediately. All necessary targets with referecne to KPI and its associated works are clearly communicated to officer. Training to transporters planned on route violations , speed violations with Novex SOP needs to be conducted repeatedly | 1.6 | Expectations clearly communicated to officers | 1800 | HUBLI DEPOT | Training for transporters and dealers with TTs | SOD | Marketing | SWZ | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 2 | CONTRACTOR SAFETY | S2 | F1 | 2026-05-31 | AUD-2026-03-2000011030ACN-2026-03-4000122787 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122787 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122787 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122787 | AUD-2026-03-2000011030ACN-2026-03-4000122787 | 21 | 21 | 26 | 80 | 18 | 18 | 39 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Same is being Ensureed | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122009 | Closed | KUMAR ATUL | 2026-03-14 | Safe 100, samridhhi, cost rationalisation initiative, compliance to circulars and guidelines, expense monitoring & booking, VTS, EMlocking and SOPs were discussed. | 1.6 | Expectations clearly communicated to officers | 1313 | BAITALPUR DEPOT | Regular self monitoring shall be ensured. | SOD | Marketing | NCR | 2026-03-02 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000011111ACN-2026-02-4000122009 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122009 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122009 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122009 | AUD-2026-02-2000011111ACN-2026-02-4000122009 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Recommendations of fire drill observations wiil be strictly implemented henceforth | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122010 | Closed | KUMAR ATUL | 2026-03-14 | 1. Date 07.02.2026 & Time: 16:10 2. Area of drill conducted: Inside depot premises 3. Scenerio covered: Fire in OWS 4. Double/single Contingency: Single contingency 5. Obervations : Communications by team to Fire chief to be improved Location to use equipment kept and designed for a site specific fire to check whether equipment (Portal foam generator with foam) work satisfactory or not. Location to check and verify the sequence of events and shutdown of depot premises. Focus shall be given on correctness of manpower/visitor count during drills. Location to ensure communication to mutual aid member and district authorities. Location to checkand verify the cause and effect in field. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | EMERGENCY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122010 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122010 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122010 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122010 | AUD-2026-02-2000011111ACN-2026-02-4000122010 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | Strret lights, tower lights and manifold area lights have been repaired and now are in working condition. Lux level hance has been increased. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122011 | Closed | KUMAR ATUL | 2026-07-30 | Lux level checked at various facility. Report attached as annexure 1. Street light near TLFPH, Near TK 7 not working. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011111ACN-2026-02-4000122011 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122011 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122011 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122011 | AUD-2026-02-2000011111ACN-2026-02-4000122011 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Training of fire engine operation, TAS interlocks and fire engine critical parameters and alarms has been imparted to the target group of security guards.on 17.02.2026 | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122012 | Closed | KUMAR ATUL | 2026-03-14 | Security guard Mr. J D Ansari, posted in C shift of 06/02/26 found not aware of operation of Fire engine, various displays of panels of FWPH. He was found unaware of operation of manual siren.Refresher training on fire engine operation is required to be iparted to security personnel. Security guards Mr. Jainath Paswan and Mr. Ashok Yadav were asked to pull emergency trolley. They could do that. | 2.5 | Emergency response preparedness reviewed | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122012 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122012 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122012 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122012 | AUD-2026-02-2000011111ACN-2026-02-4000122012 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | we're co ntinuously following up with CAMC vendor SIS limited for functioning of CCTVs. One faulty camera has been repaired and nowis in working condition. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122013 | Closed | KUMAR ATUL | 2026-07-30 | Total camera 52 Nos/ Number of camera active 51 nos. Last recording available for 92 days. | 2.6 | CCTV functioning checked | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011111ACN-2026-02-4000122013 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122013 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122013 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122013 | AUD-2026-02-2000011111ACN-2026-02-4000122013 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | VA alerts are being closed timely. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122014 | Closed | KUMAR ATUL | 2026-03-14 | Number of camera in VA is 44 Nos /Number of camera active in VA is 43. Camera inactive in VA for NEAR_TK_8_PTZ. Follow up is being made. VA alerts are being closed by location in time. 1. Review of alert Intrusion in nonworking hours (Storage Area/Wagon Gantry) TAS_1313_SOP041_121125_000010 dated 12.11.2025. Alert closed with proper comment and alert found false. 2. Review of alert Safety Harness non compliance (TT Unloading) TAS_1313_SOP039_121125_000016 dated 12.11.2025. Alert closed with comment INVALID. How everalert was found to valid, user was not wearing safety harness. | 2.7 | VA alerts checked / analysed | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122014 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122014 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122014 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122014 | AUD-2026-02-2000011111ACN-2026-02-4000122014 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | "3. Lube leakage from fire engine was attended by AMC vendor M/s Sri Guru Enterprises and leakage arrested. 4 & 5. Foam pourers checked and found ok. " | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122015 | Closed | KUMAR ATUL | 2026-03-25 | 1. Tank TK5 Point type HCD checked and found working. 2. Checked ESD 11 during drill. Found working. 3. Lube leak observed from fire engine 1 and 2. 4. TK7 Foam pourer was operated, but the foam generation in one of the foam pourer was not proper and to be checked. 5. TK 8 foam pourer was operated with plane water. One of the two foam pourers of tank no TK8, did not operate properly. Water was coming out thru the air inlet point. 6. TK7 MEFG was operated and found satisfactory. 7. HSD tanks TK3 & TK1 sprinklers were operated by officer Sh. Deepak Kumar and found sprinkler performance satisfactory. 8. Dyke drain valves were tested for Dyke 1 & 2. Alarm activated properly. 9. Fire wall valves of Tanks TK6, TK5, TK8, were checked and found having desired integrity. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122015 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122015 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122015 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122015 | AUD-2026-02-2000011111ACN-2026-02-4000122015 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Water leakes from HVLR-5 was arrested immediately. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122016 | Closed | KUMAR ATUL | 2026-03-14 | HVLR 1 & 2 were operated by security guards and newly joined E0 officer Ms. Vanshika Kumari. water leakage observed from HVLR no 5. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122016 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122016 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122016 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122016 | AUD-2026-02-2000011111ACN-2026-02-4000122016 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Convex mirror has been provided in TT no. UP82BT3799 | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122017 | Closed | KUMAR ATUL | 2026-03-14 | TT fitting check was carried for following TT and observation recorded 1.a. UP58T9374: No observation. 1.b. UP82BT3799: Convex mirror missing. | 3.1 | TT fittings & discipline checked | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122017 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122017 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122017 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122017 | AUD-2026-02-2000011111ACN-2026-02-4000122017 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | Secondary radar dip value was matching however primary radar value was not matching. Same was updated in coordination with AMC vendor | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122018 | Closed | KUMAR ATUL | 2026-03-25 | Refer Anenxure 3. One tank had difference of 1cm between physical gross dip and dip recorded in TAS and field equipment. | 3.7 | Inventory physical dip of minimum two tanks taken | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122018 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122018 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122018 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122018 | AUD-2026-02-2000011111ACN-2026-02-4000122018 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | Asset List completed and updated. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122019 | Closed | KUMAR ATUL | 2026-03-25 | List of unused asset to be updated as per material available in material yard. | 3.9 | Abnormal variations / unused assets reviewed | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122019 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122019 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122019 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122019 | AUD-2026-02-2000011111ACN-2026-02-4000122019 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | MOC 3200000687 & 3200000707 has been raised for pumps breakdown. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122020 | Closed | KUMAR ATUL | 2026-03-14 | MOC not available for pump under repair in TLFPH and TWDPH. | 3.17 | MOC status reviewed | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122020 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122020 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122020 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122020 | AUD-2026-02-2000011111ACN-2026-02-4000122020 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Audit points are being closed as per the target date. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122021 | Closed | KUMAR ATUL | 2026-03-14 | OISD : Nil pending MDSA: Total point 50, Pending point: 8, EDC: 31.03.2026 SSA: Total point 28, Pending point: 1, EDC: 31.03.2026 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1313 | BAITALPUR DEPOT | Location to ensure compliance of open audit observation scheduled for closure in current FY | SOD | Marketing | NCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011111ACN-2026-02-4000122021 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122021 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122021 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122021 | AUD-2026-02-2000011111ACN-2026-02-4000122021 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | TT crew are being trained about emergency button in VTS through Gate meetings and regularly being repeated. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122022 | Closed | KUMAR ATUL | 2026-03-25 | Interaction done with TT crew and contract workmen. Focus on road safety was given. Except Mr. Nilambar, driver of TT OD05AH6113, none of 07 nos of crew interacted with could tell about functioning of emergency button of VTS. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122022 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122022 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122022 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122022 | AUD-2026-02-2000011111ACN-2026-02-4000122022 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | LIC highlightedan power issues .Got one lady officer , joing by 10th Aug | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143113 | Closed | PURANAM PRAKASH | 2026-07-31 | 1 Officer short plus 2 NM employees retiring in June & August. | 1.5 | HQO / Zonal support required identified | 1777 | Hassan Terminal | LIC advised to send email highlighting the manpower shortage so that the same will be taken up with HQO for provising 2 additional Contract Engineers till regular officer is posted. | SOD | Marketing | SWZ | 2026-08-31 | FATIGUE AND STRESS | 6 | PROCESS SAFETY | S3 | F2 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143113 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143113 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143113 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143113 | AUD-2026-07-2000014942ACN-2026-07-4000143113 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | 1. Gantry: leakage observed from HSD loading arm Bay no 3 arrested by replacing O-ring and nose peice Steps of retractable ladderhas been tightened 2. Security & Admin Blocks: Gap observed beneath TT in gate. RCC has been layed just oustide the IN-gate and gap has been covered. 3. Tank Farm: Steps missing for Monitor 15- Provided Sand pit with cover lying nearby- Cover sheets has beencut into small pieces and handles welded to each sheet for ease handling.. 4.PMCC room: SLD not updated- SLD has been updated anddisplayed. CO2 cylinder kept is having damaged pipe.Hose pipe replaced 5. Pump house: Lube leakage observed from pump no 3 HSD and MS 1 in TLFPH. one pump has been overhauled completely but still minor lube leakage is there.As per vendor, available pumps are of old model and complete lekage arresting is not possible. Toe gaurd to be provied for pipe manifold walkways. Toe guards provided Inadeqaute height of hand railing for few walkways.Hand rail height Increased. 6. Siding: Visit could not be done. 7. Control room: No major observation. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122023 | Closed | KUMAR ATUL | 2026-07-30 | 1. Gantry: leakage observed from HSD loading arm Bay no 3. Steps of retractable ladder is loose. 2. Security & Admin Blocks: Gap observed beneath TT in gate. 3. Tank Farm: Steps missing for Monitor 15 Sand pit with cover lying nearby UG water tank manhole cover found touching ground needs to be raised up. 4.PMCC room: SLD not updated. CO2 cylinder kept is having damaged pipe. 5. Pump house: Lube leakage observed from pump no 3 HSD and MS 1 in TLFPH Toe gaurd to be provied for pipe manifold walkways. Inadeqaute height of hand railing for few walkways. 6. Siding: Visit could not be done. 7. Control room: No major observation. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122023 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122023 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122023 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122023 | AUD-2026-02-2000011111ACN-2026-02-4000122023 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Scrap near UG tank Farm 2 needs cleared. Location is ensuring 100% Safety and compliance to SOP. Regular meeting regarding SOP and pending compliance is conducted by LIC with location officers. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138616 | Closed | DEVA DHRUVA | 2026-07-31 | Hubli New IRD Team of officers are fully motivated with enthusiasm and zeal to perform at peak of their potential to not only meet the set Goals & Targets but also excel in the same. | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1800 | HUBLI DEPOT | Officers were appreciated for their efforts and maintaining the depot in good condition. However scrap near UG tank Farm 2 needs tobe cleared. It was advised to ensure 100% Safety and compliance to SOP. LIC was advised to guide the officers in getting updated onall OISD standards applicable to Terminal. | SOD | Marketing | SWZ | 2026-06-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138616 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138616 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138616 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138616 | AUD-2026-06-2000012499ACN-2026-06-4000138616 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Regular meeting regarding SOP and pending compliance is conducted by LIC with location officers. Individual performance of all officers are ensured for 100% achievement. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138617 | Closed | DEVA DHRUVA | 2026-07-31 | Reviewed performance of all Officers and officers were found focussed on the Goals and Targets with emphasis on process/efficiency improvement | 1.2 | Performance review conducted | 1800 | HUBLI DEPOT | Team to focus on G&T for the year and come up with improvements process and work efficency. LIC advised to review the individual performance and advise officers to ensure 100% achievement. | SOD | Marketing | SWZ | 2026-06-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138617 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138617 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138617 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138617 | AUD-2026-06-2000012499ACN-2026-06-4000138617 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Additonal HSD Tank proposal submitted to Zone and HQO | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143114 | Closed | PURANAM PRAKASH | 2026-07-31 | HSD tank inadequate | 1.8 | Improvement plans discussed | 1777 | Hassan Terminal | Advised location to send proposal for additional 10 TKL HSD tank | SOD | Marketing | SWZ | 2026-08-31 | FATIGUE AND STRESS | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143114 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143114 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143114 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000014942ACN-2026-07-4000143114 | AUD-2026-07-2000014942ACN-2026-07-4000143114 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Lux levels checked, additional lights provided | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143115 | Closed | PURANAM PRAKASH | 2026-07-31 | Lux levels checked on 3-6-26 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1777 | Hassan Terminal | Lux level needs to be improved near ETP,secondary roads, Foam tank shed | SOD | Marketing | SWZ | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 9 | OCCUPATIONAL HEALTH | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143115 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143115 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143115 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143115 | AUD-2026-07-2000014942ACN-2026-07-4000143115 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 | G SADASIVAN | 2026-07-09 | 100 % CBAC Compliance. Security staff are trained every fortnight | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143116 | Closed | G SADASIVAN | 2026-07-09 | 1) Interacted with security and their awareness on emergency preparedness found to be satisfactory. 2) CBACS server is not workingon 24X7 basis. This is causing discontinuity in registering the visitors and both CBACS and Manual system are being sued alternately. 3) When Emergency Gate key box opened and local alarm came, No Main Gate Security responded but Patrolling duty security responded without knowing the situation. M/Gate security to be sensitised to be alert and respond instentaneously | 2.4 | Security alertness checked (night-halt / surprise checks) | 1777 | Hassan Terminal | 1) CBACS Server issue to be sorted incluidng the network connectivity so that 100% registration of visitors is done through CBACS itself and consistency has to be maintained. 2) Training to security staff to be intensified to respond to all forms of alerts inside and outside terminal. | SOD | Marketing | SWZ | 2026-07-15 | FAILURE TO FOLLOW PROCEDURES | 9 | EMERGENCY | S3 | F3 | 2026-07-15 | AUD-2026-07-2000014942ACN-2026-07-4000143116 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143116 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143116 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143116 | AUD-2026-07-2000014942ACN-2026-07-4000143116 | 21 | 21 | 27 | 80 | 1 | 2 | 46 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | All cameras are working | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143118 | Closed | PURANAM PRAKASH | 2026-07-31 | 37 out of 41 are wokring | 2.7 | VA alerts checked / analysed | 1777 | Hassan Terminal | 4 cameras to be rectified | SOD | Marketing | SWZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S4 | F2 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143118 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143118 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143118 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143118 | AUD-2026-07-2000014942ACN-2026-07-4000143118 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Around 100 routes corrected. Secondary routes created. | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143124 | Closed | PURANAM PRAKASH | 2026-07-31 | There are pending Route deviations to be corrected. Speed violations are on the higher side. | 3.3 | VTS deviations reviewed | 1777 | Hassan Terminal | All pending routes to be corrected in a timebound manner. Counselling and if required ITDG action to be initiated for controlling and achieving Nil in speed violations. | SOD | Marketing | SWZ | 2026-08-31 | POOR COMMUNICATION | 8 | CONTRACTOR SAFETY | S4 | F2 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143124 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143124 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143124 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143124 | AUD-2026-07-2000014942ACN-2026-07-4000143124 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Product contamination issue resolved. All control room officers are sensitized | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143129 | Closed | PURANAM PRAKASH | 2026-07-31 | Daily report of MFM Vs BCU totalizer being maintained, K-Factor changes report checked and no abnormalities found. Local loading details being maintained. Checked seals of BCU,MFM of Bay-06 and K-factors of MFMs matching with calibration certificate | 3.11 | MFM vs BCU totalizer comparison checked | 1777 | Hassan Terminal | While verifying the TAS Log Book, few days before 4-6-26 (Day of visit), it was noticed KA 13 C8848 had a contamination of MS compartment and 1298 L of HSD gone into MS compartment. As a mitigation measure, location has unloaded the entire compartment product (contaminated) into to UG Horizontal tank. THis was not the right procedure and in effect, the entire UG tank has become contaminated. Location (LIC & PLT officer) to look into this, take QC help and mitigate the entire tank product without blocking the same. | SOD | Marketing | SWZ | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 9 | PROCESS SAFETY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143129 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143129 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143129 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143129 | AUD-2026-07-2000014942ACN-2026-07-4000143129 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Radar project completed. Manual dips reduced drastically | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143128 | Closed | PURANAM PRAKASH | 2026-07-31 | Yes, Manual dips are posting in view of round the clock operations, month end. | 3.10 | TFMS/SAP reconciliation checked | 1777 | Hassan Terminal | To keep the number of tanks for which manual dips to be updated in view of PLT receipts to bare minimum | SOD | Marketing | SWZ | 2026-08-31 | POOR COMMUNICATION | 9 | ASSET INTEGRITY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143128 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143128 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143128 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143128 | AUD-2026-07-2000014942ACN-2026-07-4000143128 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Two officers are checking Ethanol. Records are being maintained | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143126 | Closed | PURANAM PRAKASH | 2026-07-31 | Yes Records maintained. However, physical verification of Ethanol TT dip rod to be done for each TT. There is abnormal variation between MFM reading and tank dip levels | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1777 | Hassan Terminal | Same to be checked and necessary CAPA to be made so that both readings are matching | SOD | Marketing | SWZ | 2026-08-31 | POOR COMMUNICATION | 9 | PROCESS SAFETY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143126 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143126 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143126 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143126 | AUD-2026-07-2000014942ACN-2026-07-4000143126 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | All TTs are being checked fully before taking for loading | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143122 | Closed | PURANAM PRAKASH | 2026-07-31 | Checked EM locks using intelligent key for TTs:KA54A0768 ,KA460802 ,KA458712 & KA13AA2028 and found to be ok | 3.1 | TT fittings & discipline checked | 1777 | Hassan Terminal | 1. Additional latch to be provided for TTs inside locking box. 2. Tyres of Trucks entering into premises to be checked at parkinggate and corrective action to be intimated to drivers. Tyres of KA 45 8712 and KA 06 AB 7296 to be changed. 3. Speed limit of trucks 10 KMPH to be maintained | SOD | Marketing | SWZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 9 | EMERGENCY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143122 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143122 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143122 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143122 | AUD-2026-07-2000014942ACN-2026-07-4000143122 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Lux levels found ok , Additional lights provided | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124078 | Closed | PURANAM PRAKASH | 2026-07-31 | Checked lux levels in all areas of operation | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1777 | Hassan Terminal | Lux level needs to be improved near ETP,secondary roads, Foam tank shed | SOD | Marketing | SWZ | 2026-03-31 | INADEQUATE SAFETY CULTURE | 9 | PROCESS SAFETY | S3 | F3 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124078 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124078 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124078 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124078 | AUD-2026-03-2000011172ACN-2026-03-4000124078 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 48
|  |  |  | Location to take corrective action | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146680 | Open | CH RAGHU | 2026-07-31 | Reviewed | 3.3 | VTS deviations reviewed | 1157 | BAREILLY DEPOT | Advised to identify the location/site where max trucks are halting with out any restaurent facility so as can inform police on suchsites | SOD | Marketing | NUZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146680 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146680 | 2026-07-16 | 95.7538 | 363 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146680 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015610ACN-2026-07-4000146680 |  | AUD-2026-07-2000015610ACN-2026-07-4000146680 | 21 |  | 27 | 80 | 3 | 3 | 52
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | 15 MT of MIsc scrap and 135 no. of audco valves have been disposed in March'26. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122024 | Closed | KUMAR ATUL | 2026-07-30 | location to identify and segragate scrap available in store room. Scrap like defective valves, cables, TAS panel, UPS, IT assets, lights etc are available for disposal. Location has been given 7 days time to prepare RFD. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122024 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122024 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122024 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122024 | AUD-2026-02-2000011111ACN-2026-02-4000122024 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | All trees near boundary wall & before admin building have been trimmed | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122025 | Closed | KUMAR ATUL | 2026-03-14 | Trees near boundary wall to be cut for clear night vision. | 6.1 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122025 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122025 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122025 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122025 | AUD-2026-02-2000011111ACN-2026-02-4000122025 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | 1" expansion line above TK6 has been painted | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122026 | Closed | KUMAR ATUL | 2026-03-25 | 1” Expansion line to be painted above TK6. | 6.2 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122026 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122026 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122026 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122026 | AUD-2026-02-2000011111ACN-2026-02-4000122026 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | Dyke cross over have been painted where ever required. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122027 | Closed | KUMAR ATUL | 2026-07-30 | Cross overs in dyke drain should be painted. | 6.3 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122027 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122027 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122027 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122027 | AUD-2026-02-2000011111ACN-2026-02-4000122027 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | Height of railing has been increased in TLF pump house manifold | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122028 | Closed | KUMAR ATUL | 2026-03-14 | TLF pump house manifold area hand rail height to be increased and toe guards to be provided. | 6.4 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122028 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122028 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122028 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122028 | AUD-2026-02-2000011111ACN-2026-02-4000122028 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | Access to HSD-1 pump TSV has been provided by making platform. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122029 | Closed | KUMAR ATUL | 2026-07-30 | Access to HSD-1 pump TSV to be provided. | 6.5 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122029 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122029 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122029 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122029 | AUD-2026-02-2000011111ACN-2026-02-4000122029 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | TSV leakage has been arrested | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122030 | Closed | KUMAR ATUL | 2026-03-14 | Minor leakage was observed from TSV of HSD pump-1. | 6.6 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122030 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122030 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122030 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122030 | AUD-2026-02-2000011111ACN-2026-02-4000122030 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | repaired the damaged RCC. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122031 | Closed | KUMAR ATUL | 2026-03-25 | Concrete found damaged, exposing reinforcement rods at one corner of gantry. | 6.7 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122031 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122031 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122031 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122031 | AUD-2026-02-2000011111ACN-2026-02-4000122031 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | The bulk air eleiminator is meant for open to sky so that mix air in product could be eliminated while loading. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122032 | Closed | KUMAR ATUL | 2026-03-25 | All air eliminator openings of gantry were found open to sky | 6.8 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122032 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122032 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122032 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122032 | AUD-2026-02-2000011111ACN-2026-02-4000122032 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | cover plate and toe guards have been provided to cover gaps in gratings | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122033 | Closed | KUMAR ATUL | 2026-03-14 | Gratings of TLF PH has wide gaps at two places (this was pointed out in Nov 25 also) | 6.9 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122033 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122033 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122033 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122033 | AUD-2026-02-2000011111ACN-2026-02-4000122033 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | Gratings provided at gaps. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122034 | Closed | KUMAR ATUL | 2026-03-25 | Gratings on front drain of TLF gantry are so laid that there are wide gaps towards one corner. | 6.10 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122034 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122034 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122034 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122034 | AUD-2026-02-2000011111ACN-2026-02-4000122034 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | For daily operations field workers removed the hinge mechanism for valve operation. All hinge strips have been installed back and Workershave been counselled not to remove the hinge strip. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122035 | Closed | KUMAR ATUL | 2026-07-30 | On some of the walkways on pump house manifold, provision of operating valves have been provided by replacing railing angles by removable chain. In almost all such places, chains are not in place. | 6.11 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122035 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122035 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122035 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122035 | AUD-2026-02-2000011111ACN-2026-02-4000122035 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | Following POs available for Maintenance Jobs: 5300046192- Civil Jobs 5300023942- Electrical Works 5300044766- Misc. Works Copy attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140820 | Closed | SINGH PREETI | 2026-07-31 | Standing order for Maintenance jobs to be placed. | 6.23 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140820 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140820 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140820 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140820 | AUD-2026-06-2000013929ACN-2026-06-4000140820 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-07-30 | Acces to TSVs have been provided in TLF manifold area. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122036 | Closed | KUMAR ATUL | 2026-07-30 | Some TSVs/ PRVs installed on TLF manifold are not accessible for testing | 6.12 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122036 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122036 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122036 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122036 | AUD-2026-02-2000011111ACN-2026-02-4000122036 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-14 | copper strip jumpers have been provided and wire jumpers have bee replaced | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122037 | Closed | KUMAR ATUL | 2026-03-14 | Ethanol pipeline dead end flange joints gave wire jumpers at some places. | 6.13 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122037 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122037 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122037 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122037 | AUD-2026-02-2000011111ACN-2026-02-4000122037 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
DEVA DHRUVA | 2026-07-31 |  |  | One CE taken wef 20.06.2026. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138620 | Closed | DEVA DHRUVA | 2026-07-31 | Additional experienced Man Power required for taking care of the projects and other compliances. | 1.5 | HQO / Zonal support required identified | 1800 | HUBLI DEPOT | Already approval for one Contract Engineer from HQO. LIC to identify suitable candidate and get CE appointed. | SOD | Marketing | SWZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 9 | ASSET INTEGRITY | S3 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138620 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138620 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138620 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138620 | AUD-2026-06-2000012499ACN-2026-06-4000138620 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
VIKAS CHANDRA | 2026-07-31 | KUMAR ATUL | 2026-03-25 | Provided with proper nut bolts and area cleared for the nozzle height. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122038 | Closed | KUMAR ATUL | 2026-03-25 | UG tank where calibration water is stored, has its manifold at ground level and secured in place by only a few nuts and bolts (thisobservation was there in Nov 25 also) | 6.14 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122038 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122038 | 2026-09-26 17:30 | 23.0247 | 333 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122038 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122038 | AUD-2026-02-2000011111ACN-2026-02-4000122038 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Daily 2 TTs are being checked by officers and included it in their KPI. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138623 | Closed | DEVA DHRUVA | 2026-07-31 | Checked knowledge of TT crew, contract workmen and officers and found satisfactory. Officers capacity to operate HVLR, WCF Monitor,MEFG and found competent to handle the same | 2.5 | Emergency response preparedness reviewed | 1800 | HUBLI DEPOT | Officers need to check daily 2 TTs and include it in their KPI. Also appropriate action needs to be taken against TT for ratification. | SOD | Marketing | SWZ | 2026-06-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 6 | ASSET INTEGRITY | S2 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138623 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138623 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138623 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138623 | AUD-2026-06-2000012499ACN-2026-06-4000138623 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
DEVA DHRUVA | 2026-07-31 |  |  | HVLR-4 near tank 2 rectified and put under operation. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138625 | Closed | DEVA DHRUVA | 2026-07-31 | Out of 6 High Volume Long Range (HVLR) monitors, 5 are in working condition. One HVLR is facing movement issue, Part reached the depot, AMC engineer awaited. Emergency Shutdown (ESD) buttons were found 100% functional. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1800 | HUBLI DEPOT | HVLR-4 near tank 2 needs to be rectified and put under operation at the earliest. | SOD | Marketing | SWZ | 2026-06-25 | INSTRUMENTATION OR ALARM FAILURES | 9 | PROCESS SAFETY | S3 | F3 | 2026-06-25 | AUD-2026-06-2000012499ACN-2026-06-4000138625 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138625 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138625 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138625 | AUD-2026-06-2000012499ACN-2026-06-4000138625 | 21 | 21 | 27 | 80 | 18 | 18 | 43 | 48
DEVA DHRUVA | 2026-07-31 |  |  | All officers are involved in every month fire drill. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138626 | Closed | DEVA DHRUVA | 2026-07-31 | During the visit, a hands-on equipment trial was conducted without contractual assistance. The following officers demonstrated successful operation: HVLR Operation: Marpu Babji Foam Monitor : Tharun Akula Sprinkler Operation: Madhav Kashyap and Anup agarwal | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1800 | HUBLI DEPOT | Officers need training and more involvement in fire drill. | SOD | Marketing | SWZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138626 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138626 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138626 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138626 | AUD-2026-06-2000012499ACN-2026-06-4000138626 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Regular monitoring of all TTs are done and action being taken as per ITDG guidelines. VTS violations are decreasing regularly. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138630 | Closed | DEVA DHRUVA | 2026-07-31 | Location is reviewing and taking corrective action on regular basis. | 3.3 | VTS deviations reviewed | 1800 | HUBLI DEPOT | Location to take necessary action in line with ITDG and minimise VTs violations | SOD | Marketing | SWZ | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-25 | AUD-2026-06-2000012499ACN-2026-06-4000138630 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138630 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138630 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138630 | AUD-2026-06-2000012499ACN-2026-06-4000138630 | 21 | 21 | 27 | 80 | 18 | 18 | 43 | 48
DEVA DHRUVA | 2026-07-31 |  |  | Corrective action taken and ensured better housekeeping of admin as well as tank farm area. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138632 | Closed | DEVA DHRUVA | 2026-07-31 | Housekeeping of the admin building as well as tank farm not found aqequate and need improvement. | 3.15 | Housekeeping & PPE usage checked | 1800 | HUBLI DEPOT | Location to ensure good housekeeping of admin as well as tank farm area. | SOD | Marketing | SWZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138632 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138632 | 2026-09-11 19:30 | 37.9413 | 333 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138632 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138632 | AUD-2026-06-2000012499ACN-2026-06-4000138632 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Suspected Lock is sent to Sterna by location for further inspection | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000126001 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Following TTs were checked using Intelligent key by GM-SOD, NWZ and details as below- 1. GJ12BV7887-Ganesh Automobile-19 Top-21963-Suspected abused lock. Bottom-21964-OK 2. GJ12BZ2965-R R Petroleum-22 Top-36498-Ok Bottom-52218-OK 3. GJ13AT6969-GIRIRAJ PETROLEUM-20 Top-21947-OK Bottom-27659-OK | 6.3 | EM Lock verification using Inetlligent Key | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011072ACN-2026-03-4000126001 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000126001 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000126001 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000126001 | AUD-2026-03-2000011072ACN-2026-03-4000126001 | 21 | 21 | 26 | 80 | 2 | 2 | 57 | 48
PURANAM PRAKASH | 2026-07-31 |  |  | Faulty locks of TT 2511 have been replaced and the same have been sent to Sterna Coimbatore for checking . | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143125 | Closed | PURANAM PRAKASH | 2026-07-31 | Checked EM locks using intelligent key for 1. KA13AA2231-EM HE34875 & HE34876 --> Ok 2. KA10A5319- EM HE5631 & HE 5632 --> Ok 3. KA46A0832- EM HE31223 & HE31224 --> Ok 4. KA11C2511 - EM 27031-OK & HE31343-Not OK | 3.5 | EM Lock SOP compliance verified | 1777 | Hassan Terminal | Not OK EM Lock to be replaced to the TT with a Joint Inspection Report and defective EM Lock to be sent to M/s. Sterna, Coimbatore for investigation and report to be submitted | SOD | Marketing | SWZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 9 | ASSET INTEGRITY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143125 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143125 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143125 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143125 | AUD-2026-07-2000014942ACN-2026-07-4000143125 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 48
SABLE RONAK MOHANKUMAR | 2026-07-31 | SINGH PREETI | 2026-07-31 | All three MOCs have been closed. Screenshot attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000140191 | Closed | SINGH PREETI | 2026-07-31 | 2 Nos of MOC are overdue for closure- 3200000761, 3200000772. Change of Safety officer at Palanpur Ter is under progress. Pending with LIC. | 3.17 | MOC status reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140191 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140191 | 2026-08-22 22:00 | 57.8372 | 333 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140191 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140191 | AUD-2026-06-2000013929ACN-2026-06-4000140191 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 | DAMARAKONDA VARSHITHA | 2026-07-31 | All the points under Safe 100 and MDSA 24-25 are complied and closed in SAP. covered in point 1.4 Ensured nill night driving ( 11.00PM till 05:00 AM ) 35 Routes corrected in the month of march and made cumulative correction of 188 routes. Reduced speed violation drastically by sensitizing TT crew and taking action (Suspending) | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123492 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | Role specific / officer specific points were discussed and communicated | 1.6 | Expectations clearly communicated to officers | 1937 | SURYAPET TERMINAL | All Safe 100, MDSA Points to be closed at the earliest, No pending indents, Monitoring of VTS/Route deviations, Speed Violations and Night Driving | SOD | Marketing | SCR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123492 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123492 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123492 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123492 | AUD-2026-03-2000011061ACN-2026-03-4000123492 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Term Card Updated | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137163 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Yes discussed and found satisfactory. 3 HPCL contact numbers are given in trem card. Out of these 3, 2 are not working. Trem card to be updated. Emergency contact number written over TT (2836-654507) found not working and printed on trem card. Contact number tobe updated. | 2.15 | TT crew roadside emergency procedures checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000012347ACN-2026-06-4000137163 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137163 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137163 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137163 | AUD-2026-06-2000012347ACN-2026-06-4000137163 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 48
TAK MITHLESH KUMAR | 2026-07-31 |  |  | Dryer is working fine for Air Compressor after minor repair. Loose Nut bolts fixed for cover of Air Dryer | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137180 | Closed | TAK MITHLESH KUMAR | 2026-07-31 | Dryer was kept in off condition while associated air compressor was in operation | 6.6 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000012347ACN-2026-06-4000137180 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137180 | 2026-08-16 | 64.7538 | 333 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137180 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137180 | AUD-2026-06-2000012347ACN-2026-06-4000137180 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 |  |  |  | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128220 | Closed |  |  | Improvement Plans discussed. | 1.8 | Improvement plans discussed | 1937 | SURYAPET TERMINAL | Stock loss to be monitored for Bio diesel to ensure to meet the targets. Dip elimination efn to be sent. All Scrap to be liquidated. | SOD | Marketing | SCR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128220 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128220 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128220 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128220 | AUD-2026-04-2000011400ACN-2026-04-4000128220 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 | DAMARAKONDA VARSHITHA | 2026-07-31 | Testing of earth pits was carried out: Grid resistances remain consistent with earlier values, around 0.02 to 0.06 ohms. Individual pit resistances were initially in the range of 5 to 15 ohms.(checked in additive shed of gantry) After soil conditioning, these values have been reduced to <2 ohms. Hence, the earth pit values are observed to be within the range for the individual andthe grid resistance values. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123650 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | 1. Gantry-2 structure earth pits (EP-224 & EP-225) showed varying resistance values. | 3.16 | Earth pits / boundary / vegetation control checked | 1937 | SURYAPET TERMINAL | Earth resistance tester to be checked and reasons for variation to be identified. Earth pit readings to be monitored frequently. | SOD | Marketing | SCR | 2026-01-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123650 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123650 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123650 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123650 | AUD-2026-03-2000011061ACN-2026-03-4000123650 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 | DAMARAKONDA VARSHITHA | 2026-07-31 | CCTV cameras have been re-aligned for proper coverage and other two cameras have been repaired. All the cameras are in the active status. | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128223 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | CCTV functioning checked . 22 out 25 cameras are active in VA . Out of the total 43 CCTV cameras , 3 cameras are not working. Two cameras sent for repair and one camera is beyond repair. CCTV camera 1C is blurred, ETP camera is hazy, ingate camera angle to be corrected,cameras near watch tower2 and 3 are hazy, pipeline inlet/outlet area camera angle to be adjusted,TT parking fixed camera angle to be adjusted. | 2.6 | CCTV functioning checked | 1937 | SURYAPET TERMINAL | CCTV cameras to be realigned for proper coverage . To follow up with vendor for repair of the two cameras , one new camera to be procured and also check the fluctuations in the no. of inactive cameras. | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128223 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128223 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128223 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128223 | AUD-2026-04-2000011400ACN-2026-04-4000128223 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 | DAMARAKONDA VARSHITHA | 2026-07-31 | This point has been covered in the initial audit point no:3.18 | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128228 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | MDSA 24-25 Pending Points are nil , ESA pending points nil and SSA two points pending, MDSA 25-26 5 points are pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1937 | SURYAPET TERMINAL | Pending MDSA and SSA point to be completed as per the given target dates | SOD | Marketing | SCR | 2026-05-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011400ACN-2026-04-4000128228 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128228 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128228 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128228 | AUD-2026-04-2000011400ACN-2026-04-4000128228 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 48
CHOPPA SANTHOSH KUMAR | 2026-07-31 | DAMARAKONDA VARSHITHA | 2026-07-31 | Pending route corrections have been completed | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128225 | Closed | DAMARAKONDA VARSHITHA | 2026-07-31 | VTS deviations reviewed | 3.3 | VTS deviations reviewed | 1937 | SURYAPET TERMINAL | Pending Route corrections to be completed. | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128225 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128225 | 2026-08-04 18:45 | 75.9726 | 333 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128225 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128225 | AUD-2026-04-2000011400ACN-2026-04-4000128225 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | surprise inspection is carried out by regularly now. Last surprise inspection carried out on 25.07.2026." | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146307 | Closed | SINGH KUNAL | 2026-07-31 | Surprise night inspection is not being done regularly by location. Ethanol empty TT check is not being done 2 officers. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146307 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146307 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146307 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146307 | AUD-2026-07-2000016503ACN-2026-07-4000146307 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | surplus assets has been uploaded on surplus asset portal | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146308 | Closed | SINGH KUNAL | 2026-07-31 | Location to ensure disposal of scrap material and shifting of surplus material to required location. | 1.8 | Improvement plans discussed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146308 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146308 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146308 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146308 | AUD-2026-07-2000016503ACN-2026-07-4000146308 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | testing date now mentioned on fire Hoses | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146313 | Closed | SINGH KUNAL | 2026-07-31 | HCD: TLF PH, HCD 54 & HCD 100 : checked and found working. HVLR: HVLR 1 operated by officer Manish and performed satisfactory. Hose box-146 was checked and found equipped with 2 hose pipes and 2 nozzles. Testing date was not mentioned, test date was faded. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146313 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146313 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146313 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146313 | AUD-2026-07-2000016503ACN-2026-07-4000146313 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | Suspected locks have been replaced with new locks. Suspected locks are currently in LOCATION's custody as communication has been sent to transporters to visit terminal for witnessing of lock checking but they have not visited the terminal. Location has remindedthe transporters verbally & also thru mail dt. 31.07.2026 for witnessing the suspected locks. The suspected lock will sent to sterna after sterna for TPI after witnessing by transporter. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146316 | Closed | SINGH KUNAL | 2026-07-31 | Following TTs checked by intelligent key . 1. Lock ids HE31671 and HE26764 of TT-GJ01FT4489 has checked and found lock id is HE31671 is good and lock id HE26764 is suspected. 2. Lock ids HE35242 and HE35241 of TT-GJ17XX8383 has checked and found both locks are good locks. 3. Lock ids HE553 and HE11287 of TT-GJ35T9726 has checked and found both locks are good locks. 4. Lock ids HE13361 andHE13362 of TT-GJ06BX0277 has checked and both locks have been found suspected. 5. Lock ids HE13155 and HE13156 of TT-GJ06BV5559 has checked and both locks have been found suspected. TT inspection/discipline observation: Checked for TT GJ20J8833 & GJ04W9549 and found ok | 3.1 | TT fittings & discipline checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146316 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146316 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146316 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146316 | AUD-2026-07-2000016503ACN-2026-07-4000146316 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | daily SST is being carried out with discussing the recent incident sharing as a learning and training session to enhance the TT crew attentiveness while TT driving | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146317 | Closed | SINGH KUNAL | 2026-07-31 | Location to strengthen control to ensure nil deviation | 3.3 | VTS deviations reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146317 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146317 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146317 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146317 | AUD-2026-07-2000016503ACN-2026-07-4000146317 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | Tanks dip difference was in mm not in cm, 3 mm difference is acceptable | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146318 | Closed | SINGH KUNAL | 2026-07-31 | 1. TK101B: Dip TAS: 1808 CM, Field: 1805 cm, Temp TAS: 33.09 Field: 33.1 2. 1. TK102C: Dip TAS: 1817.3 CM, Field: 1820 cm, Temp TAS: 33.5 Field: 34.5 | 3.7 | Inventory physical dip of minimum two tanks taken | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146318 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146318 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146318 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146318 | AUD-2026-07-2000016503ACN-2026-07-4000146318 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | Boards made available for earthpit which are in line while discarded earthpits are either dismantled or cross marked | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146320 | Closed | SINGH KUNAL | 2026-07-31 | Earthpit near admin building (fire engine side) has been tested. Following are the observation: (a) No identification board was available. (b) Electrode -2.62 ohm (c) Grid-0.18 ohm. It is later observed that the earth-pit has already been discarded and new earthipts have been constructed. Earthpit no -108 near Fire Engine Shed was tested. Following are the observation: (a) No board available. (b) Electrode -1.57 ohm (c)Grid-0.2 ohm | 3.16 | Earth pits / boundary / vegetation control checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146320 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146320 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146320 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146320 | AUD-2026-07-2000016503ACN-2026-07-4000146320 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | "Previously also, for project work MOC is taken such as MOC No. 3100001296 for TK106B cleaning for conversion from slop to MTO. In future also, whenever new project work will come up, Location will take MOC such as for upcoming ATF project, MOC no. 3100002240 already put up in system" | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146321 | Closed | SINGH KUNAL | 2026-07-31 | Location to check and confirm availability of MOC for project works. | 3.17 | MOC status reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146321 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146321 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146321 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146321 | AUD-2026-07-2000016503ACN-2026-07-4000146321 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | "1. strainer cleaning done for TT gantry . Date:- 20 to 26th June 2026 2. DG & fire engine logbooks updated regularly. 3. earthing done for limit switch of ROSOV 1702 of TK101B" | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146323 | Closed | SINGH KUNAL | 2026-07-31 | Strainer at TT gantry are overdue for cleaning. Quaterly check list of Fire engine and DG is not duly filled. Earthing arrangement found improper for ROSOV 1702. | 4.2 | Maintenance activities reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146323 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146323 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146323 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146323 | AUD-2026-07-2000016503ACN-2026-07-4000146323 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | concertina coil refixing works completed | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146326 | Closed | SINGH KUNAL | 2026-07-31 | Concertina coil installed over wall behind TT gantry & near weigh bridge found damaged. | 6.2 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146326 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146326 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146326 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146326 | AUD-2026-07-2000016503ACN-2026-07-4000146326 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-07-31 | SINGH KUNAL | 2026-07-31 | additional supports provided for avoiding sagging of line | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146327 | Closed | SINGH KUNAL | 2026-07-31 | Ethanol sagged near TT gantry. | 6.3 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146327 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146327 | 2026-09-10 21:00 | 38.8788 | 333 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146327 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146327 | AUD-2026-07-2000016503ACN-2026-07-4000146327 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | additional pipeline supports has been provided | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146328 | Closed | SINGH KUNAL | 2026-07-31 | Pipe line support for line less than 6 inch is not at 3 meter distance near TTG | 6.4 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146328 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146328 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146328 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146328 | AUD-2026-07-2000016503ACN-2026-07-4000146328 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | leakage arrested | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146329 | Closed | SINGH KUNAL | 2026-07-31 | Lube leak observed in ethanol pump P-108A | 6.5 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146329 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146329 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146329 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146329 | AUD-2026-07-2000016503ACN-2026-07-4000146329 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | proper reglanding of the cable for panel of HVLR no. 8 near ETP is done | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146333 | Closed | SINGH KUNAL | 2026-07-31 | HVLR 8: cable armor is exposed. | 6.9 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146333 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146333 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146333 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146333 | AUD-2026-07-2000016503ACN-2026-07-4000146333 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | "ETP SOP has been sent for re-printing. SOP board for Dyke Valve-1 (MS) has been refixed" | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146334 | Closed | SINGH KUNAL | 2026-07-31 | ETP SOP is faded. SOP board of Dyke Valve-1 (MS) was found fallen. | 6.10 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146334 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146334 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146334 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146334 | AUD-2026-07-2000016503ACN-2026-07-4000146334 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | sprinkler cleaned for TK101A | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146335 | Closed | SINGH KUNAL | 2026-07-31 | Sprinkler no L56, L52, L50, L22, L23, L22 of TK 101A found choked. | 6.11 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146335 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146335 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146335 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146335 | AUD-2026-07-2000016503ACN-2026-07-4000146335 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | RTGP register is updated | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146336 | Closed | SINGH KUNAL | 2026-07-31 | RTGP register kept with security gate is not updated as per online record. | 6.12 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146336 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146336 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146336 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146336 | AUD-2026-07-2000016503ACN-2026-07-4000146336 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | Work permit signed by personnel | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146337 | Closed | SINGH KUNAL | 2026-07-31 | Work permit closure date to written in work permit, JSA to be signed by responsible person, | 6.13 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146337 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146337 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146337 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146337 | AUD-2026-07-2000016503ACN-2026-07-4000146337 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | record is being made | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146338 | Closed | SINGH KUNAL | 2026-07-31 | No record available for dip check of first three load for calibrated TT. | 6.14 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146338 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146338 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146338 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146338 | AUD-2026-07-2000016503ACN-2026-07-4000146338 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | During emergency power shutdown, the control room entry/exit gate through CBACS opens is opening. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146342 | Closed | SINGH KUNAL | 2026-07-31 | During emergency power shutdown, the control room entry/exit gate through CBACS opens or not to be checked. | 6.18 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146342 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146342 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146342 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146342 | AUD-2026-07-2000016503ACN-2026-07-4000146342 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | grass cutting done | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146343 | Closed | SINGH KUNAL | 2026-07-31 | Grass was observed growing inside the cable tray near the air compressor shed | 6.19 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146343 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146343 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146343 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146343 | AUD-2026-07-2000016503ACN-2026-07-4000146343 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | housekeeping done for foam shed | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146344 | Closed | SINGH KUNAL | 2026-07-31 | Paper and cloth pieces were found stored in the foam shed. | 6.20 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146344 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146344 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146344 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146344 | AUD-2026-07-2000016503ACN-2026-07-4000146344 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | grating provided | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146346 | Closed | SINGH KUNAL | 2026-07-31 | Grating was not available for the platform of Hydrant Point HY-97 | 6.22 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146346 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146346 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146346 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146346 | AUD-2026-07-2000016503ACN-2026-07-4000146346 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | flexible hose provided for foam refilling near TK102C | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146347 | Closed | SINGH KUNAL | 2026-07-31 | Flexible hose pipe for foam refilling was not available near Tank 102C | 6.23 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146347 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146347 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146347 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146347 | AUD-2026-07-2000016503ACN-2026-07-4000146347 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
KAPIL DEV | 2026-08-01 | SINGH KUNAL | 2026-07-31 | 4 no. of camera has been repaired by HAIL on 30.07.2026, these to be installed by 01.08.2026. 3 Cameras that has power/ Network issue has been resolved. HAIL representative is at site attending non functional cameras. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146311 | Closed | SINGH KUNAL | 2026-07-31 | 79 cameras out of 91 are currently working. 6 CCTV is sent to M/s. Honeywell for repair which shall be repaired by 30.07.2026. 6 CCTV is having power issue which shall be repaired by 20.06.2026. | 2.6 | CCTV functioning checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146311 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146311 | 2026-09-10 21:00 | 38.8788 | 334 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146311 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146311 | AUD-2026-07-2000016503ACN-2026-07-4000146311 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139991 | Closed |  |  | A session was conducted with the TT crew to brief them on road safety. After the session, one DCP of TT no. HR38X5024 was operated and both the equipment and the TT driver operating it functioned as per requirement. However, the TT number was not marked on the DCP. TREM card was also available with all TT crew members. | 2.14 | TT crew fire extinguisher usage checked | 1334 | HPCL REWARI IRD | Location to ensure permanent incorporation of TT number on each DCP fire extinguisher owned by them. TREM card to be made availablewith all TT crew | SOD | Marketing | NZ | 2026-07-30 | THIRD PARTY ERRORS | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139991 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139991 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139991 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139991 | AUD-2026-06-2000013601ACN-2026-06-4000139991 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139988 | Closed |  |  | On-Site Mock Fire Drill (Single contingency) as well as Off-Shift Hour Mock Fire Drill was carried out on 11th Jun'2026. Positives of the drills were timely & efficient operation of all safety equipment. Few sprinklers nozzles of adjoining tanks were found choked. | 2.5 | Emergency response preparedness reviewed | 1334 | HPCL REWARI IRD | Sprinkler nozzles to be cleaned periodically. | SOD | Marketing | NZ | 2026-06-30 | THIRD PARTY ERRORS | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013601ACN-2026-06-4000139988 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139988 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139988 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139988 | AUD-2026-06-2000013601ACN-2026-06-4000139988 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139995 | Closed |  |  | Housekeeping - Housekeeping of the location is found to be Satisfactory with some areas requireing minor upkeep which were discussed during field round with location team, like moss accumilation in the dyke drains of Dyke no. 01. PPE - During visit it was observed that all Contract workers along with Officers are adhering to guidelines of PPE usage and adequate no of PPE's available at the location. List of PPE available at location is enclosed. | 3.15 | Housekeeping & PPE usage checked | 1334 | HPCL REWARI IRD | 1. Ware house to be reorganised and cleaned. 2. TT crew room to be painted 3. Old planning room to be utilised properly. | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000139995 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139995 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139995 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139995 | AUD-2026-06-2000013601ACN-2026-06-4000139995 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139996 | Closed |  |  | A total of 20 open MOCs are reflecting in the system. | 3.17 | MOC status reviewed | 1334 | HPCL REWARI IRD | Location to ensure timely closure of all the open MOCs. | SOD | Marketing | NZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000139996 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139996 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139996 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139996 | AUD-2026-06-2000013601ACN-2026-06-4000139996 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000139994 | Closed |  |  | Out of total 993 instances of reconciliations during the period 1st Apr'26 to 8th Jun'26, only 51 instances manual recos. found. Out of these 51 instances, only 9 instances are pertaining to dates which are not falling on month ends and four of these recos. were done on zero dips. | 3.8 | Auto vs Manual reconciliation checked | 1334 | HPCL REWARI IRD | Location to reduce the instance of Manual Reconciliations. | SOD | Marketing | NZ | 2026-07-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139994 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139994 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139994 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139994 | AUD-2026-06-2000013601ACN-2026-06-4000139994 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140000 | Closed |  |  | Projects under Hold. | 4.3 | Initiated all tender and sent all supporting documents with LPR to CPO, Expected PO placement of all tenders by 15th sep | 1334 | HPCL REWARI IRD | Location advised to do tendering and bring projects to Price bid opening stage | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000140000 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000140000 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000140000 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000140000 | AUD-2026-06-2000013601ACN-2026-06-4000140000 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140001 | Closed |  |  | Location disposed-off all the scrap accumulated during the last year and declared themselves as scrap free. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1334 | HPCL REWARI IRD | Disposal of any generated scrap to be disposed | SOD | Marketing | NZ | 2026-12-30 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | ASSET INTEGRITY | S1 | F1 | 2026-12-30 | AUD-2026-06-2000013601ACN-2026-06-4000140001 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000140001 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000140001 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000140001 | AUD-2026-06-2000013601ACN-2026-06-4000140001 | 21 | 21 | 27 | 80 | 1 | 1 | 70 | 48
TYAGI ATUL | 2026-08-01 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-06-4000140002 | Closed |  |  | HCD Hooter was not found functioning in the Control Room testing of HCDs in field. | 5.2 | Functioning of all Hooters in control room checked with electrician and currently working fine | 1334 | HPCL REWARI IRD | Location to carry out periodic testing of all Hooters in the Control Room. | SOD | Marketing | NZ | 2026-07-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000140002 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000140002 | 2026-09-10 17:00 | 39.0455 | 334 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000140002 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000140002 | AUD-2026-06-2000013601ACN-2026-06-4000140002 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Training provided on 30.04.2026 , 19.05.2026 to all Officers for Operation of fire fighting equipments e.g. Fire DCP, HVLR, Monitors etc. Monthly basis mock drill conducted and Safety committee meeting also conducted on 26.0626 for Q1, discussion helf for SOPs, Nearmiss reporting, MOCs and safety related issues. Level III mock drill conducted in coordination with District adminstration on 24.07.26. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127308 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | Officers are aware about fire figting facilties. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1436 | SAGAR DEPOT | Training needs to be imparted on regular basis to the newly joined officer. | SOD | Marketing | CEN | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 12 | PROCESS SAFETY | S3 | F4 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127308 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127308 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127308 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127308 | AUD-2026-03-2000011238ACN-2026-03-4000127308 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Work completed, integrated with new channel | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127307 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | HVLR/HCD/ESD functionality was checked. Throw of HVLR was reaching the roof of tanks and functioing smoothly. All ESD were checked and found to be working condition. Alarms are coming in control room and at security room. HCD of TK3 open path type is generating false alarms in the system. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1436 | SAGAR DEPOT | Location to take up with the AST vendor for resolution of TK3 open path type HCD alarm. | SOD | Marketing | CEN | 2026-05-30 | INSUFFICIENT SUPERVISION | 12 | ASSET INTEGRITY | S4 | F3 | 2026-05-30 | AUD-2026-03-2000011238ACN-2026-03-4000127307 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127307 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127307 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127307 | AUD-2026-03-2000011238ACN-2026-03-4000127307 | 21 | 21 | 26 | 80 | 4 | 2 | 39 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-05-20 | CCTV no 4 made functional. HQO doing centralised CCTV amc tender. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127304 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | CCTV functioning was checked for storage of period of 93 days. TK4 camera is not functional. CAMC of CCTV is not done at location. | 2.6 | CCTV functioning checked | 1436 | SAGAR DEPOT | Location to take immediate action and place CAMC for CCTV camera. | SOD | Marketing | CEN | 2026-04-30 | COST-CUTTING COMPROMISING SAFETY | 12 | PROCESS SAFETY | S3 | F4 | 2026-04-30 | AUD-2026-03-2000011238ACN-2026-03-4000127304 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127304 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127304 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127304 | AUD-2026-03-2000011238ACN-2026-03-4000127304 | 21 | 21 | 26 | 80 | 4 | 2 | 35 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | ARAFFF received at location and inventory is sufficient as per OISD requirment. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127306 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | Foam inventory was checked and verified for location. Location is having required foam for fire fighting during emergency situation. Location has also ordered 12 KL foam. | 2.9 | Foam inventory verified | 1436 | SAGAR DEPOT | Location to follow up with vendor for expediting foam delivery. | SOD | Marketing | CEN | 2026-03-31 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127306 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127306 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127306 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127306 | AUD-2026-03-2000011238ACN-2026-03-4000127306 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | All TTs were verified by Phistream (TPI ) and concerened driver and Transporter has been advised to ensure Nil deviation from SOP and ensure compliance of safety fittings. Surprise inspection done by officers for any deviation in safety fittings. Training provided to all Security as per OISD 154 for frisking of TT drivers and TT before entring main gate. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127309 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | TT crew roadsoide emergency procedure was checked and found that some of the TTs have not maintained spill kit, first aid box properly. | 2.15 | TT crew roadside emergency procedures checked | 1436 | SAGAR DEPOT | Location to check and take appropriate action for compliances. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127309 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127309 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127309 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127309 | AUD-2026-03-2000011238ACN-2026-03-4000127309 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Records of TT safety check compliance maintained as per format. However monthly TT inspection done by Phistream. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127310 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | TT fittings & discipline was checked. Verified records maintained at location for pre checks. It is observed that after compliance reports are not maintained properly. | 3.1 | TT fittings & discipline checked | 1436 | SAGAR DEPOT | Location to maintain the records after complaince of point during pre-checks. | SOD | Marketing | CEN | 2026-06-30 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127310 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127310 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127310 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127310 | AUD-2026-03-2000011238ACN-2026-03-4000127310 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | All pending secondary routes created by SO and same approved. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127312 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | VTS deviations was reviewed for the locations. Noted deviations were happened due to route corrections pending from Sales Officers. | 3.3 | VTS deviations reviewed | 1436 | SAGAR DEPOT | Location to follow up with SO for route correction and secondary route updation so that route devaition can be minimised. | SOD | Marketing | CEN | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127312 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127312 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127312 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127312 | AUD-2026-03-2000011238ACN-2026-03-4000127312 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Work completed, integrated with new channel | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127317 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | MFM vs BCU totalizer comparison was checked and variation was within limits. MFM for Bay 3 & Bay 4 was not communicating as Terminal server of 10.2.12.180 is down. | 3.11 | MFM vs BCU totalizer comparison checked | 1436 | SAGAR DEPOT | Location to follow up with TAS vendor for integrating the new terminal server in TAS Revamping Project. | SOD | Marketing | CEN | 2026-04-15 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-15 | AUD-2026-03-2000011238ACN-2026-03-4000127317 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127317 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127317 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127317 | AUD-2026-03-2000011238ACN-2026-03-4000127317 | 21 | 21 | 26 | 80 | 4 | 2 | 33 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Allpending MOC closed. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127318 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | MOC status was reviewed. MOC to be closed for completed work. | 3.17 | MOC status reviewed | 1436 | SAGAR DEPOT | Location to review and close the MOC for completed work. | SOD | Marketing | CEN | 2026-03-31 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127318 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127318 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127318 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127318 | AUD-2026-03-2000011238ACN-2026-03-4000127318 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Daily gate meeting conducted before operations and records maintained. Training also conducted for all TT crew as per OISD 154. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127320 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | Interaction with TT crew/workmen was during gate meeting with officer to reinforce safety behaviour. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1436 | SAGAR DEPOT | Location to continue and increase frequency of daily safety gate meetings . | SOD | Marketing | CEN | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 15 | CONTRACTOR SAFETY | S3 | F5 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127320 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127320 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127320 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127320 | AUD-2026-03-2000011238ACN-2026-03-4000127320 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 48
BANTHIYA RITESH DEELIP | 2026-08-01 | PANWAR VIPIN SINGH | 2026-08-01 | Scrap disposed for Misc iron scrap and PVC drums. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127323 | Closed | PANWAR VIPIN SINGH | 2026-08-01 | Location has ongoing scarp disposal of 3 TON MS steel and PVC drums. Further, scrap are being generated due to ongoing project work. Consolidated action to be taken by location for disposal of the scrap. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1436 | SAGAR DEPOT | Location to complete the process of scarp disposal on time. | SOD | Marketing | CEN | 2026-03-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127323 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127323 | 2026-08-07 19:00 | 72.9622 | 334 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127323 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011238ACN-2026-03-4000127323 | AUD-2026-03-2000011238ACN-2026-03-4000127323 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 48
ARYA VIPIN KUMAR | 2026-08-01 | VERMA RAHUL | 2026-08-01 | Rivets has been provided on top chequered plate of TT no. UP85FT1609. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122090 | Closed | VERMA RAHUL | 2026-08-01 | Tank top chequered plated is found fixed with Self crew instead of rivets on TT UP85FT1609 | 6.2 |  | 1128 | MATHURA TERMINAL | Location to review and corrective action to be taken. | SOD | Marketing | NUZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122090 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122090 | 2026-09-18 | 31.7538 | 334 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122090 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122090 | AUD-2026-02-2000010909ACN-2026-02-4000122090 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 48
CHANDRAKANTH JOSHI | 2026-08-01 | ROY TAVARES | 2026-08-01 | Tranining session was conducted by location in charge for all the officers on OISD standards on 21.07.2027. All applicable standards were explained | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138565 | Closed | ROY TAVARES | 2026-08-01 | Gulbarga IRD Team of officers are fully motivated with enthusiasm and zeal to perform at peak of their potential to not only meet the set Goals & Targets but also excel in the same. | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1797 | GULBARGA NEW IRD | Officers were appreciated for their efforts and maintaining the Depot in super notch level. They were advised to maintain the same tempo and ensure 100% Safety and compliance to SOP. LIC was advised to guide the officers in getting updated on all OISD standards applicable to Depot. | SOD | Marketing | SWZ | 2026-06-30 | INADEQUATE SAFETY CULTURE | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138565 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138565 | 2026-08-19 18:00 | 61.0038 | 334 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138565 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138565 | AUD-2026-06-2000013300ACN-2026-06-4000138565 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 48
CHANDRAKANTH JOSHI | 2026-08-01 | ROY TAVARES | 2026-08-01 | Non working HVLR 3 has been rectified and is now working fine same has been recitified by Vimal Fire service . | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138574 | Closed | ROY TAVARES | 2026-08-01 | 2 High Volume Long Range (HVLR) monitors are working and 1 HVLR is under maintenance . Emergency Shutdown (ESD) buttons were found 100% functional. HCD checked in pump house and TK-05 | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1797 | GULBARGA NEW IRD | The non-working HVLR-3 is to be corrected at earliest. HCD audible alarm to be rectified for pump house | SOD | Marketing | SWZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S4 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138574 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138574 | 2026-08-19 18:00 | 61.0038 | 334 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138574 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138574 | AUD-2026-06-2000013300ACN-2026-06-4000138574 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 48
CHANDRAKANTH JOSHI | 2026-08-01 | ROY TAVARES | 2026-07-31 | HVLR has been repaired by service provider M/s Vimal Fire Serrvice | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122838 | Closed | ROY TAVARES | 2026-07-31 | HVLR No.-3 for HSD dyke is not working due to Panel Issue. ,The same needs to be corrected. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1797 | GULBARGA NEW IRD | PO for PLC for HVLR panel placed on 9/2/26 | SOD | Marketing | SWZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122838 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122838 | 2026-08-19 18:00 | 61.0038 | 334 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122838 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010764ACN-2026-03-4000122838 | AUD-2026-03-2000010764ACN-2026-03-4000122838 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | All pending HQO deliverables and performance metrics have been reviewed, responsibilities assigned, and timelines communicated to ensure timely completion. Progress is being monitored regularly by the Location In-Charge. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143787 | Closed | SELVAN J | 2026-07-30 | Performance review was discussed with Officers. While 2 Officers had submitted the G&Ts as per timelines, DSO has joined a month back while the two JEOs are in their training period and yet to confirm. During discussions, it was emphasised that SOD HQO deliverables like Opex monitoring, MEB Control, MIS Submission, QC Index, Self-Audits, ESA Compliance, HLSA Compliance, Re-validation of all SOP's at location, Improving Tank Turns, Tank Inspection should be the prime focus during the current year. | 1.2 | Performance review conducted | 1973 | CASSIMODE BLACK OIL TERMINAL | Officers to maintain focus on the metrics | SOD | Marketing | SZ | 2027-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2027-03-31 | AUD-2026-07-2000015706ACN-2026-07-4000143787 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143787 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143787 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143787 | AUD-2026-07-2000015706ACN-2026-07-4000143787 | 21 | 21 | 27 | 80 | 0 | 0 | 83 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | All location SOPs are being reviewed with the concerned officers, and necessary awareness sessions have been conducted to ensure understanding and compliance. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143788 | Closed | SELVAN J | 2026-07-30 | As one of the oldest Officers at location, Mr. A Santhosh Kumar has been transferred to Manmad, all the new Officers were assured that Zonal Support is available whenever required. They should become proficient in their work areas and improve their standards. AllSOPs to be adhered to. | 1.5 | HQO / Zonal support required identified | 1973 | CASSIMODE BLACK OIL TERMINAL | Officers to review the SOPs at location and amend if required. | SOD | Marketing | SZ | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143788 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143788 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143788 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143788 | AUD-2026-07-2000015706ACN-2026-07-4000143788 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | Speed violations are being monitored through the Novex system, and deviations are promptly communicated to the concerned transporters for immediate corrective action. All OCC tickets are tracked and closed within the stipulated timeline. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143789 | Closed | SELVAN J | 2026-07-30 | Location is found following circulars and maintaining records in CCTV monitoring, VTS monitoring, TT checks etc. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | Close monitoring by LIC on Speed violations and ensure that OCC Tickets are closed in time bound manner. | SOD | Marketing | SZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143789 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143789 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143789 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143789 | AUD-2026-07-2000015706ACN-2026-07-4000143789 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | VTS monitoring has been implemented to review the daily movement of randomly selected Tank Trucks (TTs). Route deviations and Novexalerts are reviewed promptly, corrective actions are taken with the concerned transporter/TT crew, and OCC tickets are closed within the prescribed timeline. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143794 | Closed | SELVAN J | 2026-07-30 | The location is randomly selecting five Transport tank trucks (TTs) each day to review their entire route through the VTS system for any deviations. Any deviations identified are examined on a case-by-case basis with the transporter and TT crew. Further loading is permitted only after valid reasons for the deviations have been established. Wherever route corrections are required, the matter is promptly taken up with I&C Region. Additionally, Novex alerts generated through the system are regularly reviewed, and appropriatecorrective actions are taken as required. | 3.3 | VTS deviations reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | Close monitoring by LIC on Speed violations and ensure that OCC Tickets are closed in time bound manner. | SOD | Marketing | SZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143794 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143794 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143794 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143794 | AUD-2026-07-2000015706ACN-2026-07-4000143794 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | New officers have been trained in manual stock reconciliation procedures. Manual reconciliation is being carried out regularly in SAP, and reconciliation is within the prescribed limits. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143796 | Closed | SELVAN J | 2026-07-30 | Location is doing manual reco on regular basis is SAP. Ambient Stock loss report in maintained separately. | 3.8 | Auto vs Manual reconciliation checked | 1973 | CASSIMODE BLACK OIL TERMINAL | New Officers to achieve proficiency in manual reconciliation is within limits. | SOD | Marketing | SZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000143796 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143796 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143796 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143796 | AUD-2026-07-2000015706ACN-2026-07-4000143796 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | A schedule for periodic alarm review has been prepared, and all alarms are being reviewed. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143797 | Closed | SELVAN J | 2026-07-30 | Alarms are cleared with comments | 3.12 | Critical alarms checked & corrective actions reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | New Officers sensitised on compliance of alarms with proper justification. | SOD | Marketing | SZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015706ACN-2026-07-4000143797 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143797 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143797 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143797 | AUD-2026-07-2000015706ACN-2026-07-4000143797 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 48
M MAHESH BABU | 2026-08-03 | SELVAN J | 2026-07-30 | The repair estimate and detailed scope of work have been prepared and submitted to HQO-M&I for approval and fund allocation. TK-2 has been isolated and kept under outage until completion of the repair work. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143799 | Closed | SELVAN J | 2026-07-30 | The pending MDSA/SSA observations pertaining to tank inspection were reviewed. Metal thickness loss was observed in the wind girderarea of Tank-2 (TK-2). Accordingly, TK-2 has been taken out of service (under outage) for detailed investigation and necessary repair works. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | Location to take estimate of repairs and timeline of completion for seeking funds from HQO-M&I. | SOD | Marketing | SZ | 2026-07-15 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-15 | AUD-2026-07-2000015706ACN-2026-07-4000143799 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143799 | 2026-09-22 17:00 | 27.0455 | 336 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143799 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143799 | AUD-2026-07-2000015706ACN-2026-07-4000143799 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Solar AR Extenion file note received from HQO and Expenditure booked and AR closed in SAP. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122603 | Closed | M.RAJKUMAR | 2026-08-03 | Solar project - physical works related to Solar panels completed. Net-metering approved and generation commenced effective 04.02.2026. Officially inaugurated on 12.02.2026. Awaiting ECM minutes from HQO for extension of AR till Feb '26 to make payment and close the AR. | 1.3 | Pending issues reviewed | 1856 | COIMBATORE DEPOT | To expediate the closure of AR and monitor the solar generation on daily basis for expected output. | SOD | Marketing | SZ | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S4 | F2 | 2026-02-28 | AUD-2026-03-2000010712ACN-2026-03-4000122603 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122603 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122603 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010712ACN-2026-03-4000122603 | AUD-2026-03-2000010712ACN-2026-03-4000122603 | 21 | 21 | 26 | 80 | 0 | 1 | 26 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | 1. RFDs pertaining to E-Waste - Disposal Completed. 2. Fire Extinguisher Upliftment completed. 3. Automation Panels, Misc Scrap, Old DG Set, Electrical Panels disposal completed. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122604 | Closed | M.RAJKUMAR | 2026-08-03 | Location complied with the timelined for closure of ESA points. Location also has made good progrees in RFD as per plan given in last review | 1.4 | Earlier action points status checked | 1856 | COIMBATORE DEPOT | Location to expediate the disposal of scrap at the earliest. | SOD | Marketing | SZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 9 | PROCESS SAFETY | S3 | F3 | 2026-03-31 | AUD-2026-03-2000010712ACN-2026-03-4000122604 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122604 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122604 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010712ACN-2026-03-4000122604 | AUD-2026-03-2000010712ACN-2026-03-4000122604 | 21 | 21 | 26 | 80 | 0 | 1 | 31 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | ECM Minutes obtained, payment processed and AR closed. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122605 | Closed | M.RAJKUMAR | 2026-08-03 | Awaiting ECM minutes from HQO for extension of AR till Feb '26 to make payment and close the AR. | 1.5 | HQO / Zonal support required identified | 1856 | COIMBATORE DEPOT | Location to continously follow up with HQO/Zone for minutes of ECM. | SOD | Marketing | SZ | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S4 | F2 | 2026-02-28 | AUD-2026-03-2000010712ACN-2026-03-4000122605 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122605 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122605 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010712ACN-2026-03-4000122605 | AUD-2026-03-2000010712ACN-2026-03-4000122605 | 21 | 21 | 26 | 80 | 0 | 1 | 26 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | E diary is implemented and Location incharge is submitting daily observations in e diary | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142952 | Closed | M.RAJKUMAR | 2026-08-03 | Officers were advised to take physical rounds of the location and contribute to the betterment of location. Officers to leave legacy behind of doing something good for location before moving to another location. | 1.8 | Improvement plans discussed | 1856 | COIMBATORE DEPOT | e-diary implementation by location incharge and submit the same on daily basis on e-diary portal | SOD | Marketing | SZ | 2027-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2027-03-31 | AUD-2026-07-2000015339ACN-2026-07-4000142952 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142952 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142952 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142952 | AUD-2026-07-2000015339ACN-2026-07-4000142952 | 21 | 21 | 27 | 80 | 0 | 1 | 83 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Officers were involved in operation of all fire fighting equipments and all other contract workmen are trained to operate the Extinguisher and Basic fire gifhting facilites regularly. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142953 | Closed | M.RAJKUMAR | 2026-08-03 | Checked knowledge of TT crew, contract workmen and officers and found satisfactory. | 2.5 | Emergency response preparedness reviewed | 1856 | COIMBATORE DEPOT | XX | SOD | Marketing | SZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015339ACN-2026-07-4000142953 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142953 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142953 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142953 | AUD-2026-07-2000015339ACN-2026-07-4000142953 | 21 | 21 | 27 | 80 | 0 | 1 | 57 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Location is deploying officers for checking the dips of trucks. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142955 | Closed | M.RAJKUMAR | 2026-08-03 | Two TTs(TN36AA6401 ,TN36BU6288 dip verified and both found with in tolerance limit. Details being entered in SAP for 5% of the Tanktrucks. | 3.2 | Post-loading dip checks verified | 1856 | COIMBATORE DEPOT | Location to ensure that random checking by different officers should be done to have effective controls. | SOD | Marketing | SZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142955 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142955 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142955 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142955 | AUD-2026-07-2000015339ACN-2026-07-4000142955 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Letters are being issued and TT crew is being counseled for any violations. Daily gate meetings are being conducted for sharing theincidents and safe driving practices. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142956 | Closed | M.RAJKUMAR | 2026-08-03 | Location is randomly selecting 5 TPT TTs & 2 DCT TTs daily for reviewing the entire route in the VTS system for any deviations andentering the same in VTS Monitoring portal. Deviations if any, is taken up on case-to-case basis with the Transporter/TT Crew, randomly after establishing valid reasons the TTs are allotted further loads. Any requirement of Route corrections are also promptly takenup with the concerned Sales Officer. Records for the same are being maintained. Also, Novex alerts generated are beingreviewed and actions are being taken. | 3.3 | VTS deviations reviewed | 1856 | COIMBATORE DEPOT | TT crew and Transporters to be counselled and TTs to be released only with proper justification. | SOD | Marketing | SZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142956 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142956 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142956 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142956 | AUD-2026-07-2000015339ACN-2026-07-4000142956 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Security Supervisor is daily reviewing CCTV recordings of previous day and the records are being maintained. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142959 | Closed | M.RAJKUMAR | 2026-08-03 | CCTV monitoring by Head Guard | 6.1 | Additional Observations | 1856 | COIMBATORE DEPOT | Security Head guard advised to monitor CCTV and make an entry in the register | SOD | Marketing | SZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142959 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142959 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142959 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142959 | AUD-2026-07-2000015339ACN-2026-07-4000142959 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 48
POTHALA VENKATA RAO | 2026-08-03 | M.RAJKUMAR | 2026-08-03 | Gate connecting with the Railway siding is being kept in closed conditions and during wagon unloading, same will be manned with onegaurd. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142960 | Closed | M.RAJKUMAR | 2026-08-03 | Railway Gate | 6.2 | Additional Observations | 1856 | COIMBATORE DEPOT | Railway Gate to be manned or kept in locked condition. | SOD | Marketing | SZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142960 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142960 | 2026-08-28 17:00 | 52.0455 | 336 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142960 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142960 | AUD-2026-07-2000015339ACN-2026-07-4000142960 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 48
SUJEET KUMAR | 2026-08-03 | SAXENA UMESH CHANDRA | 2026-08-03 | All recommendations of previous senior mgmt audit have been complied with. CAPA of previous sr mgmt audit is enclosed for evidence. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000135375 | Closed | SAXENA UMESH CHANDRA | 2026-08-03 | Yes, to be closed. | 1.4 | Earlier action points status checked | 1457 | INDORE DEPOT | Previous visit open points to be closed on priority. | SOD | Marketing | CEN | 2026-06-30 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135375 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135375 | 2026-09-09 19:00 | 39.9622 | 336 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135375 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135375 | AUD-2026-06-2000012547ACN-2026-06-4000135375 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 48
SUJEET KUMAR | 2026-08-03 | SAXENA UMESH CHANDRA | 2026-07-24 | Adiitional lights have been provided in control room and MCC room. Pictures of lux levels measured at above-mentioned two places at20:00 hrs on 24.07.2026 are enclosed as evidence. Lux levels are now meeting the norms. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000135377 | Closed | SAXENA UMESH CHANDRA | 2026-07-24 | Lux level checked and found to be inadequate in MCC room. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1457 | INDORE DEPOT | Additional fixtures to be provided in MCC room to improve the lux level. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135377 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135377 | 2026-09-09 19:00 | 39.9622 | 336 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135377 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135377 | AUD-2026-06-2000012547ACN-2026-06-4000135377 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 48
SUJEET KUMAR | 2026-08-03 | SAXENA UMESH CHANDRA | 2026-08-03 | Same recommendation is already captured under sub-code 1.6 which is open. Hence this dulicate point can be closed. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000135385 | Closed | SAXENA UMESH CHANDRA | 2026-08-03 | OISD - 0, SSA - 0 and MDSA - 22 pending against total observation point of 42. Targeted to complete it by Dec' 2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1457 | INDORE DEPOT | Closure of 22 Open MDSA points to be expedited within set timeline. | SOD | Marketing | CEN | 2026-12-31 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 8 | PROCESS SAFETY | S2 | F4 | 2026-12-31 | AUD-2026-06-2000012547ACN-2026-06-4000135385 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135385 | 2026-09-09 19:00 | 39.9622 | 336 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135385 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012547ACN-2026-06-4000135385 | AUD-2026-06-2000012547ACN-2026-06-4000135385 | 21 | 21 | 27 | 80 | 0 | -3 | 70 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Nilpending indents. Monitoring of VTS/Route deviations, Speed Violations and Night Driving are done. TT crew are being counselled during gate meetings. In case of repeat violations, same are being taken up with transporter. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123047 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Role specific / officer specific points were discussed and communicated | 1.6 | Expectations clearly communicated to officers | 1915 | RAMAGUNDAM DEPOT | All Safe 100, MDSA Points to be closed at the earliest, No pending indents, Monitoring of VTS/Route deviations, Speed Violations and Night Driving | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010863ACN-2026-03-4000123047 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123047 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123047 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123047 | AUD-2026-03-2000010863ACN-2026-03-4000123047 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. Only 2 MDSA observations pending which are infrastructure type where PO already in place. Similarly for SSA, Out of 4 pending observations, 2 are infrastructure type where PO is already in place and works are in progress. 1 observation can be closed after completing all MDSA observations. 1 observation related to tank inspection of 7 tanks. Of which 6 tanks are already inspected, only 1 HSD AG tank is pending which is planned in Jun26. MS stock losses reduced in H2. Reduced overall stock loss from -0.395 to -0.22 . Dip elimination file note submitted to Zone. 100% scrap disposal completed. Solar performance is being monitored. Improvement for solar generation, support being taken from other vendors. Current generation is around 77%. Dormant keys are beinghandled as per SOP. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123048 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1915 | RAMAGUNDAM DEPOT | Stock loss, Electrical Expenses, Solar Performance, Dormant Keys, SSA /MDSA compliance, CCTV, Dip Elimination File note, M&I Projects, Scrap Disposal | SOD | Marketing | SCR | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010863ACN-2026-03-4000123048 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123048 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123048 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123048 | AUD-2026-03-2000010863ACN-2026-03-4000123048 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. Security supervisor Shri. K.Naresh has Heavy vehicle driving license with DL: 21783/DL/PKL valid till 22-08-2027 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123701 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Location does not have any trained personnel with HVD/HZA Endorsement | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1915 | RAMAGUNDAM DEPOT | Location to get security/ Other staff to get HVD/HZA endorsement for movingTT 50–100m in case of any emergency | SOD | Marketing | SCR | 2026-04-30 | THIRD PARTY ERRORS | 5 | EMERGENCY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010863ACN-2026-03-4000123701 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123701 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123701 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123701 | AUD-2026-03-2000010863ACN-2026-03-4000123701 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-22 | Leak control kit, Adsorbent booms, Megaphone, FLP torch and helmet for fire suit procured. All items in emregency trolley are present. Live fire training to Contract workmen carried out on 11-05-2026 by M/s Safensafety solutions pvt ltd. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123049 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-22 | Reviewed emergency trolley equipment. Some of the items were found missing and not in the designated compartments. Interacted with officers & security personnel about their roles and resposibilities during emergencies | 2.5 | Emergency response preparedness reviewed | 1915 | RAMAGUNDAM DEPOT | Emergency trolley to be regularly inspected & all equipment to be placed at their designated compartments. Live fire traininng to be imparted to all contract workmen. | SOD | Marketing | SCR | 2026-02-28 | INADEQUATE SAFETY CULTURE | 5 | EMERGENCY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000010863ACN-2026-03-4000123049 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123049 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123049 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123049 | AUD-2026-03-2000010863ACN-2026-03-4000123049 | 21 | 21 | 26 | 80 | 2 | 2 | 26 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. 3 nos CCTV repaired. 4th one parking camera is under repair. 2 new camera installed in the parking area as an additional measure. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123700 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Checked . 4 cameras are down. Location has identified the issues & necessary action is initiated . | 2.6 | CCTV functioning checked | 1915 | RAMAGUNDAM DEPOT | Location to ensure that 4 nos CCTV put back into service on priority basis. | SOD | Marketing | SCR | 2026-03-31 | THIRD PARTY ERRORS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010863ACN-2026-03-4000123700 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123700 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123700 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123700 | AUD-2026-03-2000010863ACN-2026-03-4000123700 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Alarms are being monitored accordingly action being taken. If any critical alarms are found but the field conditions are good, thensame are being taken up with TAS vendor. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123705 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Critical alarms were reviewed for past one month | 3.12 | Critical alarms checked & corrective actions reviewed | 1915 | RAMAGUNDAM DEPOT | Location advised to carefully monitor the alarms and not acknowledge them without going into detail of the reason for it | SOD | Marketing | SCR | 2026-02-14 | COMPLACENCY OR RISK NORMALIZATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-14 | AUD-2026-03-2000010863ACN-2026-03-4000123705 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123705 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123705 | 532 | 8294 | 21 | 8294 | 247 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123705 | AUD-2026-03-2000010863ACN-2026-03-4000123705 | 21 | 21 | 26 | 80 | 2 | 2 | 24 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied, taken up with vendor. From Mar26, the MFM meter factor change is not peresent. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123706 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Checked.MFM meter factor change was observed in many instances at the time of power outage which reverted back to original after power resumption. | 3.13 | K-factor changes reviewed (if any) | 1915 | RAMAGUNDAM DEPOT | To take up the issue with AST for checking and necessary modifications if required. | SOD | Marketing | SCR | 2026-02-14 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-14 | AUD-2026-03-2000010863ACN-2026-03-4000123706 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123706 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123706 | 532 | 8294 | 21 | 8294 | 247 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123706 | AUD-2026-03-2000010863ACN-2026-03-4000123706 | 21 | 21 | 26 | 80 | 2 | 2 | 24 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | TT dips are being checked. In case of any excess product due to power failure during loading or due to any other reason, same is being removed from truck. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123702 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Two filled TTs dips checked at TT Gantry . TT no TG 22 T 1629 dips found excess in Compt 1 and 3. Compt 1 excess of 6 lires and compt 2 excess of 4 litrs. For Compt 1 BCU qty is 5002 litres i.e. 2 litres excess. TT no AP 39 UG3564 TT dips found ok for all 3 compartments. | 3.2 | Post-loading dip checks verified | 1915 | RAMAGUNDAM DEPOT | Officers to check TT dips regularly and corrective action to be taken for any deviations | SOD | Marketing | SCR | 2026-02-14 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-14 | AUD-2026-03-2000010863ACN-2026-03-4000123702 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123702 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123702 | 532 | 8294 | 21 | 8294 | 247 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123702 | AUD-2026-03-2000010863ACN-2026-03-4000123702 | 21 | 21 | 26 | 80 | 2 | 2 | 24 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. Locks replaced and these locks sent to EM locking vendor for analysis. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123703 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Checked locks for trucks AP29W2928,AP28TE8686,AP39UG3564,TS22T1629,TS08UK2491 with intelligent key . In 2 TTs AP39UG3564 and TS22T1629 the Key was not going inside the lock. | 3.5 | EM Lock SOP compliance verified | 1915 | RAMAGUNDAM DEPOT | Location advised to send the locks to TPI for checking and replace the locks as per SOP | SOD | Marketing | SCR | 2026-02-14 | THIRD PARTY ERRORS | 5 | ENVIRONMENTAL | S1 | F5 | 2026-02-14 | AUD-2026-03-2000010863ACN-2026-03-4000123703 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123703 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123703 | 532 | 8294 | 21 | 8294 | 247 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123703 | AUD-2026-03-2000010863ACN-2026-03-4000123703 | 21 | 21 | 26 | 80 | 2 | 2 | 24 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | All tank dips within limits during Feb 26 month-end physical dip report. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123704 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Physical dip has been checked for TK P6 . TAS dip observed: 148.1 cms Physical dip observed: 147.6 Cms Variation : 5 mm | 3.7 | Inventory physical dip of minimum two tanks taken | 1915 | RAMAGUNDAM DEPOT | Location to take up with tas vendor and ensure that variations remain with in tolerance limit of 3 mm | SOD | Marketing | SCR | 2026-02-25 | THIRD PARTY ERRORS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-25 | AUD-2026-03-2000010863ACN-2026-03-4000123704 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123704 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123704 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123704 | AUD-2026-03-2000010863ACN-2026-03-4000123704 | 21 | 21 | 26 | 80 | 2 | 2 | 26 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. 100% PM jobs completed each month. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123709 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | PM orders are being closed in month end. Advised location to complete PM orders as per given time frame. | 4.4 | Quality of PM compliance reviewed | 1915 | RAMAGUNDAM DEPOT | PM orders to be completed in time | SOD | Marketing | SCR | 2026-02-14 | FAILURE TO FOLLOW PROCEDURES | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-14 | AUD-2026-03-2000010863ACN-2026-03-4000123709 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123709 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123709 | 532 | 8294 | 21 | 8294 | 247 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123709 | AUD-2026-03-2000010863ACN-2026-03-4000123709 | 21 | 21 | 26 | 80 | 2 | 2 | 24 | 48
LINGAMPALLI SRIHARSHA | 2026-08-03 | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Complied. Scrap disposed on 18-02-2026 inv: TS0150148788 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123710 | Closed | SUDDAPALLI CHANDRA SEKHAR | 2026-05-23 | Scrap was sold in auction. Delivery orders were issued to remove scrap. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1915 | RAMAGUNDAM DEPOT | Location to coordinate and remove scrap at earliest | SOD | Marketing | SCR | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-02-25 | AUD-2026-03-2000010863ACN-2026-03-4000123710 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123710 | 2026-08-26 18:00 | 54.0038 | 336 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123710 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123710 | AUD-2026-03-2000010863ACN-2026-03-4000123710 | 21 | 21 | 26 | 80 | 2 | 2 | 26 | 48
NIDAMARTHI NAGA KIRAN | 2026-08-04 | SATYENDRA CHOURASIA | 2026-06-13 | Continuous efforts are ongoing for Solar Performance, Dormant Keys, SSA /MDSA compliance, CCTV, Dip Elimination File note, M&I Projects, Scrap Disposal | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123662 | Closed | SATYENDRA CHOURASIA | 2026-06-13 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1919 | SECUNDERABAD TERMINAL | Solar Performance, Dormant Keys, SSA /MDSA compliance, CCTV, Dip Elimination File note, M&I Projects, Scrap Disposal | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011062ACN-2026-03-4000123662 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123662 | 2026-08-06 19:00 | 73.9622 | 337 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123662 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123662 | AUD-2026-03-2000011062ACN-2026-03-4000123662 | 21 | 21 | 26 | 80 | 1 | -12 | 31 | 49
NIDAMARTHI NAGA KIRAN | 2026-08-04 | SATYENDRA CHOURASIA | 2026-07-15 | Solar readings are being monitored daily and generation improved. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129565 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | Solar readings to be monitored on daily basis | 6.4 |  | 1919 | SECUNDERABAD TERMINAL | Solar readings to be checked and improved generation | SOD | Marketing | SCR | 2026-05-20 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129565 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129565 | 2026-08-06 19:00 | 73.9622 | 337 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129565 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129565 | AUD-2026-05-2000012102ACN-2026-05-4000129565 | 21 | 21 | 27 | 80 | 1 | -12 | 38 | 49
NIDAMARTHI NAGA KIRAN | 2026-08-04 | SATYENDRA CHOURASIA | 2026-07-15 | VC with sterna team for resolution of EM Keys was conducted at Zonal Level. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129567 | Closed | SATYENDRA CHOURASIA | 2026-07-15 | EM keys pending issues | 6.6 |  | 1919 | SECUNDERABAD TERMINAL | Have VC with sterna team for resolution of EM Keys. | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129567 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129567 | 2026-08-06 19:00 | 73.9622 | 337 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129567 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129567 | AUD-2026-05-2000012102ACN-2026-05-4000129567 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 49
NIDAMARTHI NAGA KIRAN | 2026-08-04 | SATYENDRA CHOURASIA | 2026-06-13 | Continuous efforts are ongoing all Safe 100, MDSA Points closure, No pending indents, Monitoring of VTS/Route deviations, Speed Violations and Night Driving | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123661 | Closed | SATYENDRA CHOURASIA | 2026-06-13 | Role specific / officer specific points were discussed and communicated | 1.6 | Expectations clearly communicated to officers | 1919 | SECUNDERABAD TERMINAL | All Safe 100, MDSA Points to be closed at the earliest, No pending indents, Monitoring of VTS/Route deviations, Speed Violations and Night Driving | SOD | Marketing | SCR | 2026-01-27 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-27 | AUD-2026-03-2000011062ACN-2026-03-4000123661 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123661 | 2026-08-06 19:00 | 73.9622 | 337 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123661 | 532 | 8294 | 21 | 8294 | 265 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123661 | AUD-2026-03-2000011062ACN-2026-03-4000123661 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 49
[5 empty] | LOCATION VISIT-SANGRUR_15-17.07.26 | 2026-07-17 | AUD-2026-08-2000016412 | 2026-07-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147000 | Open |  |  | Discussion held with BPC Sangrur regarding a patch of land available in the vicinity owned by BPC. | 1.3 | Pending issues reviewed | 1180 | SANGRUR DEPOT | Proposal to be given by Location. | SOD | Marketing | NFZ | 2026-08-31 |  | 2 |  | S2 | F1 | 2026-08-31 | AUD-2026-08-2000016412ACN-2026-08-4000147000 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016412ACN-2026-08-4000147000 | 2026-07-17 | 94.7538 | 364 | >20 | AUD-2026-08-2000016412 - ACN-2026-08-4000147000 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016412ACN-2026-08-4000147000 |  | AUD-2026-08-2000016412ACN-2026-08-4000147000 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | LOCATION VISIT-SANGRUR_15-17.07.26 | 2026-07-17 | AUD-2026-08-2000016412 | 2026-07-15 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-08-4000147003 | Open |  |  | BSPL is under stablization hence MFM based accounting has not been started | 5.1 | MFM based accounting at Pipeline and OMC location | 1180 | SANGRUR DEPOT | 03 Month data collection to be started after MFM calibration | SOD | Marketing | NFZ | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-08-2000016412ACN-2026-08-4000147003 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016412ACN-2026-08-4000147003 | 2026-07-17 | 94.7538 | 486 | >20 | AUD-2026-08-2000016412 - ACN-2026-08-4000147003 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016412ACN-2026-08-4000147003 |  | AUD-2026-08-2000016412ACN-2026-08-4000147003 | 21 |  | 27 | 80 | 0 | 0 | 70
MONISH KUMAR | 2026-08-04 | JHA RAJAN KUMAR | 2026-08-01 | Sprinkler nozzles of Tank no. 5/6/17/18 have been cleaned. | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-05-4000131526 | Closed | JHA RAJAN KUMAR | 2026-08-01 | Sprinklers no 102 to 105 and 118 of Tk4 found choked. | 6.21 | Quarterly Inspection | 1723 | PATNA DEPOT | Periodic checking and clearing blockages of Sprinkler nozzles needs to be done | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131526 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131526 | 2026-08-03 | 77.7538 | 337 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131526 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131526 | AUD-2026-05-2000012310ACN-2026-05-4000131526 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
MONISH KUMAR | 2026-08-04 | JHA RAJAN KUMAR | 2026-08-01 | Choking in Foam line was removed both at Foam pourer and near Foam tank. Working fine . | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-05-4000131527 | Closed | JHA RAJAN KUMAR | 2026-08-01 | None of the three foam pourers of Tk02 generated foam. | 6.22 | Quarterly Inspection | 1723 | PATNA DEPOT | regular inspection of Foam pourers needs to be done and the foam pourers to be made effective | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131527 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131527 | 2026-08-03 | 77.7538 | 337 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131527 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012310ACN-2026-05-4000131527 | AUD-2026-05-2000012310ACN-2026-05-4000131527 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | CCTV at the time of audit have been restored. follow-up being done reguarly with vendor for handling of current repairs. Point is kept open in subsequent Audit | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124091 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | CCTV functioning checked. Out of 78 cameras, 5 nos cameras are found down. | 2.6 | CCTV functioning checked | 1895 | MANGALORE TERMINAL | Location has taken up with CCTV vendor. Same to be expediated. | SOD | Marketing | SWZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011174ACN-2026-03-4000124091 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124091 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124091 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011174ACN-2026-03-4000124091 | AUD-2026-03-2000011174ACN-2026-03-4000124091 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | OEM Visit completed and anamolies rectified | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124093 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Dips of Tank-19, 20 & 21 in TAS are found to be different from actual. | 3.7 | Inventory physical dip of minimum two tanks taken | 1895 | MANGALORE TERMINAL | It is learnt that Tankmaster data for these tanks is not transferred into TAS. To be rectified. | SOD | Marketing | SWZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 9 | ASSET INTEGRITY | S3 | F3 | 2026-04-15 | AUD-2026-03-2000011174ACN-2026-03-4000124093 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124093 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124093 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011174ACN-2026-03-4000124093 | AUD-2026-03-2000011174ACN-2026-03-4000124093 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | OEM Visit completed and anamolies rectified | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124094 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Dips of Tank-2, 3, 5, 19, 20, 21 & U35 are not posted into SAP. | 3.8 | Auto vs Manual reconciliation checked | 1895 | MANGALORE TERMINAL | Issues of zero density, wrong water level & problems of communication to be rectified. | SOD | Marketing | SWZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 16 | ASSET INTEGRITY | S4 | F4 | 2026-04-15 | AUD-2026-03-2000011174ACN-2026-03-4000124094 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124094 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124094 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | HIGH |  | AUD-2026-03-2000011174ACN-2026-03-4000124094 | AUD-2026-03-2000011174ACN-2026-03-4000124094 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | OEM Visit completed and anamolies rectified | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124095 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Dips of Tank-2, 3, 5, 19, 20, 21 & U35 are not posted into SAP. | 3.10 | TFMS/SAP reconciliation checked | 1895 | MANGALORE TERMINAL | Issues of zero density, wrong water level & problems of communication to be rectified. | SOD | Marketing | SWZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 16 | ASSET INTEGRITY | S4 | F4 | 2026-04-15 | AUD-2026-03-2000011174ACN-2026-03-4000124095 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124095 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124095 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | HIGH |  | AUD-2026-03-2000011174ACN-2026-03-4000124095 | AUD-2026-03-2000011174ACN-2026-03-4000124095 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | MOC initiated | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124096 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | All MOC's are up to date. MOC for induction of 2 new officers to be done immediately. | 3.17 | MOC status reviewed | 1895 | MANGALORE TERMINAL | MOC for 2 new officers to be done | SOD | Marketing | SWZ | 2026-03-05 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-05 | AUD-2026-03-2000011174ACN-2026-03-4000124096 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124096 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124096 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011174ACN-2026-03-4000124096 | AUD-2026-03-2000011174ACN-2026-03-4000124096 | 21 | 21 | 26 | 80 | 2 | 2 | 27 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Rotation of officers being done. TAS officer is assigned planning duties, M&R officer is assigned Vessel handling/Rake handling etc. Same will be continued. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138603 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Interacted with all Officers except TAS officer who was on leave and understood their roles & responsiobilities. Emphasised on the need to focus in depth on their respective roles and excel in each area. | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1895 | MANGALORE TERMINAL | Officers need to gel and work as a cohesive team, overlapping and mutually contributing towards each other. To create a positivework atmosphere so that any task can be carried out in line with Zonal/ HQO expectations. | SOD | Marketing | SWZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138603 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138603 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138603 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138603 | AUD-2026-06-2000013350ACN-2026-06-4000138603 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | This is Repeat point. Scrap related point no 4.5 is kept open and this is being closed. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138604 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Pending issues of getting the land from MRPL & registering the same, Disposal of Scrap lying for long time, TFMS performance to be improved were discussed and clear time targets arrived | 1.3 | Pending issues reviewed | 1895 | MANGALORE TERMINAL | To ensure 100% Scrap Disposal and make location scrap free by Dec-2026. RFDs should be processed in June 2026. | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138604 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138604 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138604 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138604 | AUD-2026-06-2000013350ACN-2026-06-4000138604 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | OEM visit completed and issues rectified | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138605 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Work on TAS related pending issues, bottom loading to be expedited. | 1.6 | Expectations clearly communicated to officers | 1895 | MANGALORE TERMINAL | To encusre timely completion of TAS issues and bottom loading issues | SOD | Marketing | SWZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138605 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138605 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138605 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138605 | AUD-2026-06-2000013350ACN-2026-06-4000138605 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | lux levels are maintained properly at all operational areas | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138607 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Lux levels checked randomly near admin area and TWG area. Found okay. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1895 | MANGALORE TERMINAL | Loaction to maintain appropiate Lux level at all areas in terminal | SOD | Marketing | SWZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000013350ACN-2026-06-4000138607 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138607 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138607 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138607 | AUD-2026-06-2000013350ACN-2026-06-4000138607 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | required list of manpower from petronet and railways obtained and entry of manpower done after checking with approved list. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138609 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Security entry registers at Vistor gate and hazardous gate checked. Found okay CCTV recoridngs of Security frisking at vistir gateand TT checks before parking area entry checked randomly. Found okay, however scope for improvement found | 2.8 | Access control systems checked | 1895 | MANGALORE TERMINAL | 1) Railway outgate security allowing only based on Name List given (By PMHBL,Rlys etc) and not checking Identity. Training to Security staff to be given and ensure proper checks of TT's and Persons at respective gates to be improved. Monitoring to be done. 2) Technica Gate Barrier to be installed and commissioned | SOD | Marketing | SWZ | 2026-06-30 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138609 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138609 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138609 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138609 | AUD-2026-06-2000013350ACN-2026-06-4000138609 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | rectification of issues done after OEM visit. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138610 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Dips of Tank 2, 3, 5, 7, 9, U-35 are not posted into SAP. Wrong dip posted for Tank 19, 20,21 | 3.12 | Auto vs Manual reconciliation checked | 1895 | MANGALORE TERMINAL | Issues of zero density, wrong water level & problems of communication to be rectified. | SOD | Marketing | SWZ | 2026-07-31 | COMPLACENCY OR RISK NORMALIZATION | 16 | ASSET INTEGRITY | S4 | F4 | 2026-07-31 | AUD-2026-06-2000013350ACN-2026-06-4000138610 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138610 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138610 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | HIGH |  | AUD-2026-06-2000013350ACN-2026-06-4000138610 | AUD-2026-06-2000013350ACN-2026-06-4000138610 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | rectification of issues done after OEM visit. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138611 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Dips of Tank-2, 3, 5, 7, 9 & U35 are not posted into SAP. Wrong dip posted for Tank 19, 20,21 | 3.14 | TFMS/SAP reconciliation checked | 1895 | MANGALORE TERMINAL | Issues of zero density, wrong water level & problems of communication to be rectified. | SOD | Marketing | SWZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 16 | ASSET INTEGRITY | S4 | F4 | 2026-07-31 | AUD-2026-06-2000013350ACN-2026-06-4000138611 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138611 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138611 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | HIGH |  | AUD-2026-06-2000013350ACN-2026-06-4000138611 | AUD-2026-06-2000013350ACN-2026-06-4000138611 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | This is Repeat point. Scrap related point no 4.5 is kept open and this is being closed. | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138613 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | Scrap: 1) Old Jetty Arms, Bitumen Gantry (After HQO Confirmation) and Bitumen corroded tanks to be disposed off 2) Old Bitumen Drums 24 Nos to be scrapped 3) Near TW Gantry Pipeline Scrap | 6.1 | Scrap Disposal | 1895 | MANGALORE TERMINAL | To process RFDs immediately to get approval by 20.06.2026 and physical disposal by 30.09.2026 | SOD | Marketing | SWZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138613 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138613 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138613 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138613 | AUD-2026-06-2000013350ACN-2026-06-4000138613 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
KAUSHIK ANIL | 2026-08-04 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | CABCS rectiied and in order | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138614 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-08-04 | CBACs server down last 2 days. CBACS @Delicensed to Licensed Not Working | 6.2 | CBACs | 1895 | MANGALORE TERMINAL | To rectify the same and put back into operation | SOD | Marketing | SWZ | 2026-05-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-05-31 | AUD-2026-06-2000013350ACN-2026-06-4000138614 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138614 | 2026-07-29 17:00 | 82.0455 | 337 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138614 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138614 | AUD-2026-06-2000013350ACN-2026-06-4000138614 | 21 | 21 | 27 | 80 | 2 | 2 | 39 | 49
SINGWAL DEEPAK | 2026-08-05 | CHAHAR ALKESH KUMAR | 2026-08-03 | The local display and audio alarm for Dyke Valve indicator for Dyke-2, was checked and found that supply was fed from lighting system, which was OFF during day time. Supply from UPS system has been provided and issue is resolved. | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141721 | Closed | CHAHAR ALKESH KUMAR | 2026-08-03 | HVLR-3 near TK-19 was oeprated and throw observed was adequate. Operated Point type HCD of Dyke-I and Open path HCD of TLF Gantry. Both worked fine. Dyke Valve indicator operated for Dyke-2, the local display and audio found to be non - working. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1435 | GWALIOR DEPOT | Location to carryout repairing of Audio - Visual of Dyke valve indicator installed at Dyke-2 on top priority. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 15 | ASSET INTEGRITY | S3 | F5 | 2026-06-30 | AUD-2026-06-2000015012ACN-2026-06-4000141721 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141721 | 2026-08-22 19:00 | 57.9622 | 338 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141721 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141721 | AUD-2026-06-2000015012ACN-2026-06-4000141721 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 49
SINGWAL DEEPAK | 2026-08-05 | CHAHAR ALKESH KUMAR | 2026-08-03 | TT MP07 ZJ 9011 was checked at calibration tower and variation was observed. Transporter has advised for re-calibration. | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141723 | Closed | CHAHAR ALKESH KUMAR | 2026-08-03 | Yes, verified 3 TT's. TT Nos: MP07 ZL 7010, MP07 ZJ 9011 and MP07 HB 6747. Variation upto 4 mm observed in Bay No. 3. | 3.2 | Post-loading dip checks verified | 1435 | GWALIOR DEPOT | Location is advised to keep the bay under observation for another 3 days by checking Dips of other TT's. If the problem persist, then location to recalibrate the bay / TT thru W&M Dept. | SOD | Marketing | CEN | 2026-07-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-30 | AUD-2026-06-2000015012ACN-2026-06-4000141723 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141723 | 2026-08-22 19:00 | 57.9622 | 338 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141723 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141723 | AUD-2026-06-2000015012ACN-2026-06-4000141723 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Periodic interaction with officers for guidance and mentoring is being done by LIC | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141866 | Closed | PATHAK AHELI | 2026-07-31 | Interacted with officers (LIC+9) of terminal on 24.06.2026 except two officers who were on leave (Puneet & Jyoti). A case study wasdisucssed giving details of the lacunae, do's & dont's were explained. New & young officers were encouraged to go through relevant SOP's and advised them to stay updated on ongoing activities at terminal irrespective of their portfolio. | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1775 | BENGALURU TERMINAL | LIC shall have periodic interaction with officers for guidance and mentoring. | SOD | Marketing | SWZ | 2026-07-31 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141866 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141866 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141866 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141866 | AUD-2026-06-2000014499ACN-2026-06-4000141866 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Stopper provided | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141877 | Closed | PATHAK AHELI | 2026-07-31 | Yes, Fire fighting training was given to young officers near TT gantry. Hydrant monitor operated by Prashant Sharma, hose handling in mobile foam trolley by Megha Meena and fire fighting by Aheli Pathak & Megha Meena. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1775 | BENGALURU TERMINAL | Stopper for mobile foam trolley shall be provided | SOD | Marketing | SWZ | 2026-07-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141877 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141877 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141877 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141877 | AUD-2026-06-2000014499ACN-2026-06-4000141877 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | All FFE made fully functional. | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141876 | Closed | PATHAK AHELI | 2026-07-31 | Checked. HVLR-02 was observed not moving in one direction when operated through remote panel. Foam throw in MEFG in Tank-18 was notsatisfactory. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1775 | BENGALURU TERMINAL | All FFE to be made fully functional. | SOD | Marketing | SWZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141876 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141876 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141876 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141876 | AUD-2026-06-2000014499ACN-2026-06-4000141876 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | All are made available in VA | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141875 | Closed | PATHAK AHELI | 2026-07-31 | 48/51 Cameras are working in VA. No pending alerts. | 2.7 | VA alerts checked / analysed | 1775 | BENGALURU TERMINAL | Remaining cameras to be made available in VA. | SOD | Marketing | SWZ | 2026-07-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-06-2000014499ACN-2026-06-4000141875 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141875 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141875 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141875 | AUD-2026-06-2000014499ACN-2026-06-4000141875 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | All Cameras in working condition | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141874 | Closed | PATHAK AHELI | 2026-07-31 | 56 /58 Cameras working. 1 FLP camera sent to OEM for repairs. | 2.6 | CCTV functioning checked | 1775 | BENGALURU TERMINAL | 2 nos. remaining cameras to be made operational. | SOD | Marketing | SWZ | 2026-07-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-06-2000014499ACN-2026-06-4000141874 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141874 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141874 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141874 | AUD-2026-06-2000014499ACN-2026-06-4000141874 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141878 | Closed | PATHAK AHELI | 2026-07-31 | Few TT's were observed without branding (KA53AA9281) or faded branding. Safety checks were doen by Aheli/Sangeeta/Megha in TT's KA 53 AA 9281, KA 01 AN 5856 & KA 01 AQ 9964, no deviations observed. | 3.1 | TT fittings & discipline checked | 1775 | BENGALURU TERMINAL | TT branding to be complied in all TT's | SOD | Marketing | SWZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141878 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141878 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141878 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141878 | AUD-2026-06-2000014499ACN-2026-06-4000141878 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Corrected and ensured | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141879 | Closed | PATHAK AHELI | 2026-07-31 | Checked and observed within limits. | 3.7 | Inventory physical dip of minimum two tanks taken | 1775 | BENGALURU TERMINAL | Density variation in Tk 20,21 & 22 to be rectified. | SOD | Marketing | SWZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141879 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141879 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141879 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141879 | AUD-2026-06-2000014499ACN-2026-06-4000141879 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | RFD initiated | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141880 | Closed | PATHAK AHELI | 2026-07-31 | Inventory verification done and found ok.MS and HDPE barrels are under MSTC auctioning. Unused assets and surplus materials updatedin surplus portal | 3.9 | Abnormal variations / unused assets reviewed | 1775 | BENGALURU TERMINAL | RFD for balance items to be initiated. | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141880 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141880 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141880 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141880 | AUD-2026-06-2000014499ACN-2026-06-4000141880 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Banding provided | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141887 | Closed | PATHAK AHELI | 2026-07-31 | TT congestion at sealing platform observed. | 6.2 | Additional Observations | 1775 | BENGALURU TERMINAL | Arrow marks/banding shall be provided to limit TT placement within that area | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141887 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141887 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141887 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141887 | AUD-2026-06-2000014499ACN-2026-06-4000141887 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141889 | Closed | PATHAK AHELI | 2026-07-31 | Canopy to be placed over ethanol pump-motor assembly and silica gel to be replaced | 6.4 | Additional Observations | 1775 | BENGALURU TERMINAL | To be complied | SOD | Marketing | SWZ | 2026-07-10 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141889 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141889 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141889 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141889 | AUD-2026-06-2000014499ACN-2026-06-4000141889 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 49
KUMAR CHAKRABORTI ALOK | 2026-08-05 | PATHAK AHELI | 2026-07-31 | Barrels removed | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141890 | Closed | PATHAK AHELI | 2026-07-31 | Barrels stored near UG pump house to be removed | 6.5 | Additional Observations | 1775 | BENGALURU TERMINAL | To be expedited | SOD | Marketing | SWZ | 2026-07-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141890 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141890 | 2026-09-24 17:00 | 25.0455 | 338 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141890 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141890 | AUD-2026-06-2000014499ACN-2026-06-4000141890 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | Faulty Lights replaced, now lux level meeting at control room | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130671 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | Lux level checked and found to be inadequate in control room and security room. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1436 | SAGAR DEPOT | Location is advised to put additional light fixtures to meet desired lux level as per OISD norms. | SOD | Marketing | CEN | 2026-05-22 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-22 | AUD-2026-05-2000012507ACN-2026-05-4000130671 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130671 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130671 | 532 | 8294 | 21 | 8294 | 150 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130671 | AUD-2026-05-2000012507ACN-2026-05-4000130671 | 21 | 21 | 27 | 80 | 4 | 2 | 38 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | Issue resolved after follow up with vendor. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130672 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | All 62 CCTV cameras are working and 90 days recording is also verified. PTZ camera near TK-02 is giving false indication. | 2.6 | CCTV functioning checked | 1436 | SAGAR DEPOT | Location is advised to check with the vendor and get it corrected. | SOD | Marketing | CEN | 2026-05-31 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012507ACN-2026-05-4000130672 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130672 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130672 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130672 | AUD-2026-05-2000012507ACN-2026-05-4000130672 | 21 | 21 | 27 | 80 | 4 | 2 | 39 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | All three area CBAC system working ( main gate, Hazardous area entry ) | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130673 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | Access control system is down at 3 places, One at Security Cabin and 2 places at Delicensed to licensed area. The card reader is non-functional. | 2.8 | Access control systems checked | 1436 | SAGAR DEPOT | Location is advised to get it repaired on top priority. | SOD | Marketing | CEN | 2026-05-31 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012507ACN-2026-05-4000130673 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130673 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130673 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130673 | AUD-2026-05-2000012507ACN-2026-05-4000130673 | 21 | 21 | 27 | 80 | 4 | 2 | 39 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | Hooter of TK-3 and visual of TK-17 repaired by TAS vendor AST. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130674 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | Checked and found in working condition. HCD of TK-3, Hooter was not activated. Also, visual for TK-17 is having issue. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1436 | SAGAR DEPOT | Location to get Hooter of TK-3 and visual of TK-17 repaired on priority. | SOD | Marketing | CEN | 2026-06-15 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-15 | AUD-2026-05-2000012507ACN-2026-05-4000130674 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130674 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130674 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130674 | AUD-2026-05-2000012507ACN-2026-05-4000130674 | 21 | 21 | 27 | 80 | 4 | 2 | 41 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | Old open MOCs closed in system and new MOC raised. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130676 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | 7 MOC's are open - (TAS Revamp, Bottom Loading Facility, CBAC, Rly Siding Sprinkler Work, Rly siding Modification of FW System, DipElimination, Product Reco by Manual Dip Gauging) | 3.17 | MOC status reviewed | 1436 | SAGAR DEPOT | Location to follow up and expedite closure of all MOC's in a time bound manner. | SOD | Marketing | CEN | 2026-12-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-05-2000012507ACN-2026-05-4000130676 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130676 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130676 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130676 | AUD-2026-05-2000012507ACN-2026-05-4000130676 | 21 | 21 | 27 | 80 | 4 | 2 | 70 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-05 | Pump repaired. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130678 | Closed | PANWAR VIPIN SINGH | 2026-08-05 | Yes, Ethanol Pump is under maintenance for TK-11 tank. Issue with pump shaft. | 4.2 | Maintenance activities reviewed | 1436 | SAGAR DEPOT | Location is advised to put back the pump back into service by 31.05.2026. | SOD | Marketing | CEN | 2026-05-26 | FATIGUE AND STRESS | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-26 | AUD-2026-05-2000012507ACN-2026-05-4000130678 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130678 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130678 | 532 | 8294 | 21 | 8294 | 146 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130678 | AUD-2026-05-2000012507ACN-2026-05-4000130678 | 21 | 21 | 27 | 80 | 4 | 2 | 39 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  | Coupler issue resolved for FE-02. Rotor Seal Changed. | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000125669 | Closed | OWEEZ HAQQANI | 2026-08-06 | FE-02 is having problem with the coupler. | 6.2 | Fire Engine Shed | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-04-25 | POOR EQUIPMENT MAINTENANCE | 12 | ASSET INTEGRITY | S3 | F4 | 2026-04-25 | AUD-2026-04-2000010791ACN-2026-04-4000125669 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125669 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125669 | 532 | 8294 | 21 | 8294 | 177 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010791ACN-2026-04-4000125669 | AUD-2026-04-2000010791ACN-2026-04-4000125669 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  | Wheel restoredand inflated. | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000125668 | Closed | OWEEZ HAQQANI | 2026-08-06 | Checked, found one of the wheel gone flat. | 6.1 | Emergency Trolly | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-04-25 | POOR EQUIPMENT MAINTENANCE | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-25 | AUD-2026-04-2000010791ACN-2026-04-4000125668 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125668 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125668 | 532 | 8294 | 21 | 8294 | 177 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010791ACN-2026-04-4000125668 | AUD-2026-04-2000010791ACN-2026-04-4000125668 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  | Location has utilized Misc. Scrap for OISD Project work & to be utilized under OISD Projects. | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000125667 | Closed | OWEEZ HAQQANI | 2026-08-06 | Location has identified Miscellanous scrap, disposal to be expedited | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1265 | LEH DEPOT | Location to dispose misc. scrap. | SOD | Marketing | NFZ | 2026-05-15 | INADEQUATE SAFETY CULTURE | 4 | ENVIRONMENTAL | S1 | F4 | 2026-05-15 | AUD-2026-04-2000010791ACN-2026-04-4000125667 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125667 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125667 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010791ACN-2026-04-4000125667 | AUD-2026-04-2000010791ACN-2026-04-4000125667 | 21 | 21 | 27 | 80 | 0 | 0 | 37 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  | HCDs installed in Tank Farm Area. | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000125666 | Closed | OWEEZ HAQQANI | 2026-08-06 | Location has 2 point type HCD, 1 open path HCD, 9 ESDs all are functioning properly. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1265 | LEH DEPOT | 2 point type HCD to be installed in Tank manifold of new tank farm. | SOD | Marketing | NFZ | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-15 | AUD-2026-04-2000010791ACN-2026-04-4000125666 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125666 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125666 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010791ACN-2026-04-4000125666 | AUD-2026-04-2000010791ACN-2026-04-4000125666 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  |  | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000125665 | Closed |  |  | Yes, lux level at all operating areas meets OISD STD 244 and are checked monthly and records maintained | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1265 | LEH DEPOT | Location advised to mark spots where lux levels are checked. | SOD | Marketing | NFZ | 2026-04-22 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-22 | AUD-2026-04-2000010791ACN-2026-04-4000125665 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125665 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125665 | 532 | 8294 | 21 | 8294 | 180 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010791ACN-2026-04-4000125665 | AUD-2026-04-2000010791ACN-2026-04-4000125665 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 49
OWEEZ HAQQANI | 2026-08-06 |  |  | Off Shift Drill Conducted Dated. 24.07.2026. | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000125664 | Closed | OWEEZ HAQQANI | 2026-08-06 | Yes, monthly Fire Drills conducted as per Location conditions. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1265 | LEH DEPOT | Off shift drill to be conducted. | SOD | Marketing | NFZ | 2026-04-22 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-22 | AUD-2026-04-2000010791ACN-2026-04-4000125664 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125664 | 2026-10-07 09:00 | 12.3788 | 339 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125664 | 532 | 8294 | 21 | 8294 | 180 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010791ACN-2026-04-4000125664 | AUD-2026-04-2000010791ACN-2026-04-4000125664 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-06 | Calibration done and records maintained however location doing regular check of dip road and maintaining surprise check records. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127311 | Closed | PANWAR VIPIN SINGH | 2026-08-06 | Post-loading dip surprise checks was done for TT. TT MP16H 1847 was checked and dips were found ok. However, TT proof level recordsto TT was not correct in report for calibration, which was done on 09.02.26. | 3.2 | Post-loading dip checks verified | 1436 | SAGAR DEPOT | Location to follow up with W&M for correcting the calibration report. | SOD | Marketing | CEN | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 9 | PROCESS SAFETY | S3 | F3 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127311 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127311 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127311 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127311 | AUD-2026-03-2000011238ACN-2026-03-4000127311 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-06 | Programming audit llog report generated for TTs on regular basis and audit key logs also checked on random basis. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127313 | Closed | PANWAR VIPIN SINGH | 2026-08-06 | EM Lock SOP compliance was checked. Programming audit log report was also checked for the location. For some TT audit key is pending for more then 30 days. | 3.5 | EM Lock SOP compliance verified | 1436 | SAGAR DEPOT | Location to review the reports and share the detailed reports for the deviations. | SOD | Marketing | CEN | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127313 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127313 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127313 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127313 | AUD-2026-03-2000011238ACN-2026-03-4000127313 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-06 | Location improved stock loss performance. Regular dip verification done in presence of officer. Recently location took ITDG action on TT MP20ZN5417of Narmada Sugar Pvt. Ltd. for irregularity. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127314 | Closed | PANWAR VIPIN SINGH | 2026-08-06 | Ethanol TT dip before & after unloading verified at location. No dip shortage was observed before unloading. Details of stock w.r.ttanks opening & closing was checked and found having minor variations due underground tank behaviour. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1436 | SAGAR DEPOT | Location to improve the stock loss performance for Ethanol. | SOD | Marketing | CEN | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127314 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127314 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127314 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127314 | AUD-2026-03-2000011238ACN-2026-03-4000127314 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-06 | Veriation issue resolved as of now under tas revamp project. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127315 | Closed | PANWAR VIPIN SINGH | 2026-08-06 | Inventory physical dip guaging of minimum two tanks TK1 & TK3 was done and variation observed within the limits between physical and auto dips. | 3.7 | Inventory physical dip of minimum two tanks taken | 1436 | SAGAR DEPOT | Location to follow up with the vendor for completing the TAS Revamping Project at the ealiest possible. | SOD | Marketing | CEN | 2026-06-30 | INSTRUMENTATION OR ALARM FAILURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127315 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127315 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127315 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127315 | AUD-2026-03-2000011238ACN-2026-03-4000127315 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 49
BANTHIYA RITESH DEELIP | 2026-08-06 | PANWAR VIPIN SINGH | 2026-08-06 | Location following manual dip checking SOP and regularly maintaining dip register at gantry. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127316 | Closed | PANWAR VIPIN SINGH | 2026-08-06 | Location is doing reconcilation on manual dip as per approved MOC 3200000586 due to TAS Revamping Project. | 3.8 | Auto vs Manual reconciliation checked | 1436 | SAGAR DEPOT | Location to continue doing the reconcilations on manual dips as per approved MOC and maintain the variation sheet for auto vs manual dips | SOD | Marketing | CEN | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-31 | AUD-2026-03-2000011238ACN-2026-03-4000127316 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127316 | 2026-08-07 19:00 | 72.9622 | 339 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127316 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127316 | AUD-2026-03-2000011238ACN-2026-03-4000127316 | 21 | 21 | 26 | 80 | 4 | 2 | 31 | 49
PURANAM PRAKASH | 2026-08-06 |  |  | All cameras are working now | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124081 | Closed | PURANAM PRAKASH | 2026-08-06 | 37 out of 41 are wokring | 2.7 | VA alerts checked / analysed | 1777 | Hassan Terminal | 4 cameras to be rectified | SOD | Marketing | SWZ | 2026-03-31 | POOR COMMUNICATION | 8 | EMERGENCY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124081 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124081 | 2026-09-22 17:00 | 27.0455 | 339 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124081 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124081 | AUD-2026-03-2000011172ACN-2026-03-4000124081 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 49
PURANAM PRAKASH | 2026-08-06 |  |  | Point complied by enhancing checking at security | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124085 | Closed | PURANAM PRAKASH | 2026-08-06 | Checked EM locks using intelligent key for TTs:KA54A0768 ,KA460802 ,KA458712 & KA13AA2028 and found to be ok | 3.1 | TT fittings & discipline checked | 1777 | Hassan Terminal | 1. Additional latch to be provided for TTs inside locking box. 2. Tyres of Trucks entering into premises to be checked at parking gate and corrective action to be intimated to drivers. Tyres of KA 45 8712 and KA 06 AB 7296 to be changed. 3. Speed limit of trucks 10 KMPH to be maintained | SOD | Marketing | SWZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 9 | ASSET INTEGRITY | S3 | F3 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124085 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124085 | 2026-09-22 17:00 | 27.0455 | 339 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124085 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124085 | AUD-2026-03-2000011172ACN-2026-03-4000124085 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 49
PURANAM PRAKASH | 2026-08-06 |  |  | Complied | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124082 | Closed | NARAYANA RAO RAMACHANDRAN | 2026-03-10 | Checked open patch HCD of TK-102 alarm triggered in Control room, main gate and local hooter also activated, Storm water dyke valveopened for TK-102 local hooter activated, alarm trigerred in control room and main gate | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1777 | Hassan Terminal | HCD integration of TK-302 to be completed | SOD | Marketing | SWZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S4 | F2 | 2026-03-15 | AUD-2026-03-2000011172ACN-2026-03-4000124082 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124082 | 2026-09-22 17:00 | 27.0455 | 339 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124082 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124082 | AUD-2026-03-2000011172ACN-2026-03-4000124082 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 49
PURANAM PRAKASH | 2026-08-06 |  |  | All route correction made | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124086 | Closed | PURANAM PRAKASH | 2026-08-06 | Carried out | 3.3 | VTS deviations reviewed | 1777 | Hassan Terminal | Route correction by 31.03.2026 | SOD | Marketing | SWZ | 2026-03-31 | FATIGUE AND STRESS | 8 | ASSET INTEGRITY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011172ACN-2026-03-4000124086 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124086 | 2026-09-22 17:00 | 27.0455 | 339 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124086 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124086 | AUD-2026-03-2000011172ACN-2026-03-4000124086 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 49
TILKAN RAVINDRA KUMAR | 2026-08-06 | Sreelal P P | 2026-08-06 | Functionality of Level switch and solenoid valve has been reviewed and verified for all HVLR daughter tanks. Foam line is not keptfilled to prevent corrosion damage | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141183 | Closed | Sreelal P P | 2026-08-06 | Foam Inventory is adequate as per OISD STD 244 and 117. AFFF Requirement - 8.08 AFFF Available - 10KL ARAFFF Requirement - 8.88KL ARAFFF Available - 20KL | 2.9 | Foam inventory verified | 1845 | IRUMPANAM TERMINAL | Auto-filling functionality of the foam system to be checked, tested, and confirmed. | SOD | Marketing | CZR | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141183 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141183 | 2026-09-02 16:30 | 47.0663 | 339 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141183 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141183 | AUD-2026-06-2000013833ACN-2026-06-4000141183 | 21 | 21 | 27 | 80 | 1 | -4 | 48 | 49
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-08-4000146720 | Open |  |  | 1. HSD 5 & 4 pumps not in use. No display found. 2. Oil leakage from gland found at HSD1 and MS1 pumps. 3. Emergency light not marked at the pump house. 4. CCTV view not proper at TWD Pump house | 6.4 | Quarterly Inspection | 1723 | PATNA DEPOT | 1. Location to place Not in use signage. 2. Location to arrest Oil leakage and clean the area of oil spil. 3. Location to ensure marking emergency light at the pump house. 4. CCTV view to be to be adjusted covering all pumps. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146720 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146720 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146720 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146720 |  | AUD-2026-08-2000016222ACN-2026-08-4000146720 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-08-4000146721 | Open |  |  |  | 6.5 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to use proper sampling thief, find the reasons for difference in water level between TAS actual and take corrective action. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146721 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146721 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146721 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146721 |  | AUD-2026-08-2000016222ACN-2026-08-4000146721 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-08-4000146722 | Open |  |  | No SOP board and line diagram found in STP area. Officer found unaware of functioning of STP | 6.6 | Quarterly Inspection | 1723 | PATNA DEPOT | SOP board and line diagram to be updated. All officers to be updated on functioning of STP | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146722 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146722 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146722 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146722 |  | AUD-2026-08-2000016222ACN-2026-08-4000146722 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-08-4000146724 | Open |  |  | 1.Eathpit no 117, near STP, which was partially hidden under vegetation, was having no earthpit cover. There was another earthpit near it which did not have any Earthpit board. For both eathpits double bolt connection was not there and clamps were not touching each other directly 2. Wire earthing connection of manifold light of Tk6 found snapped . 3. On random checking, it has been found the earthpits 33, 58, 59, were not having proper boublr both connection and proper surface connection between clamps 4. 2 earth stripat railway siding was found to be over lapping and in contact. | 6.8 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC, HSE officer and M&I officer to visit work areas regularly, by taking atleast one round daily to detect misses/ shortcomings and take corrective action. 4. Location to ensure earth pits do not over lap and have proper isolaton in case of crossing. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146724 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146724 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146724 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146724 |  | AUD-2026-08-2000016222ACN-2026-08-4000146724 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-08-4000146725 | Open |  |  | There is no monitoring of sampling and related QC activities and entire activity has been left to contrat workmen, as 1. Locationdoes not use proper sampling thief for sampling. Open mouth sampling thief is used for taking any type of sample (it was observed during last visit also). 2. Record of daily TT gantry samples found not updated for many days Even samples are not sealed and stacked on the same day. Unsealed samples with old tags and loose seals found kept on Sample room floor 3. Sample disposal register is also not having any signature of any officer since 18/02/2026. 4. Similar is the case with TW QC register, which bears no signatureof any officer since 27/02/2026 | 6.9 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC to monitor QC activities | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146725 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146725 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146725 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146725 |  | AUD-2026-08-2000016222ACN-2026-08-4000146725 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-08-4000146727 | Open |  |  | History cards are not being maintained properly. One Ethanol pump is under maintenance. However, histrory card is silent on it. Replacement of lube oil, filters of DGs, fire engine are also mentioned in History cards with erroneous information. Similar is the case with history cards of Fire extinguishers. | 6.11 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC to review and monitor M&I activities and records | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146727 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146727 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146727 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146727 |  | AUD-2026-08-2000016222ACN-2026-08-4000146727 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-08-4000146729 | Open |  |  | Bay no 5: TT no BR27G9590: Comp 1: ok, Comp 2: +1 mm, Comp 3: ok Bay no 6: TT no JH05BD3375: Comp 1: ok, Comp 2: +1 mm, Comp 3: +1mm Bay no 7: TT no BR06GA3962: Comp 1: +1 mm, Comp 2: ok, Comp 3:+2 mm Bay no 4: TT no BR05GA1951: Comp 1: +5mm, Comp 2: +4 mm, Comp 3: ok Bay no 3: TT no BR01GF9691: Comp 1: +1mm, Comp 2: ok, Comp 3: ok, Comp 4: ok | 6.13 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to check a few more TTs loaded in this bay, check calibration of TT no BR05GA1951. Also check accuracy of MFMs of this bay, if such difference is found in multiple TTs | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146729 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146729 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146729 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146729 |  | AUD-2026-08-2000016222ACN-2026-08-4000146729 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-08-4000146730 | Open |  |  | Around 30 TT crew were interacted with. Except one driver, none were aware of functioning of VTS emergency button, which was explained to them. Safe driving practices, importance of sharing experiences of any unsafe conditions on the route amongst fellow TT crews, parking of TT at only safe places and not parking them near suspected places, route deviation, etc. were discussed.Safe driving habits on water logged roads TT crew were also asked to express their opinion about TT crew amenties and express their expectations, if any. They expressed their satisfaction about existing amenities | 6.14 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to continue such small team meetings with TT crew to promote safety in transportation | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146730 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146730 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146730 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146730 |  | AUD-2026-08-2000016222ACN-2026-08-4000146730 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-08-4000146732 | Open |  |  | Fire drill was conducted at Rly siding with scenario of mock fire from flange of one wagon.. Following were the observations: 1. The DCP fire extinguisher worked properly. 2. Hydrant points and monitors worked properly. 3. Evacuation of injured person was handled efficiently. Scopes of improvement: 1.First responder went too close to fire spot. 2. Before the Fire extinguisher discharge was completed. Monitor was operated targetting the spot, tough it was immediately stopped also. 3. Adjacent wagons were not cooled. 4. Auxiliary team members were left to work as per their understanding, as the team leader did not reach the spot, till almost endof the drill 5. Updating Fire chief on situation, from time to time, direction from Fire Chief to team leaders was not there. 6. Even after completion of drill, fire clock was not set correct. 7. Head count , post drill was not done properly. 8. The emergencytrolley did not reach site. When it was moved to reach site, its cabinet doors started getting opened, creating further delay in taking the emergency trolley to site. 9.Though fire hose lines were laid properly, but in absence of water cum foam branch pipe, thearrangement could not be utilized for fire fighting. 10. Role of different team leaders in taking stockof things and guiding team members, left scopes of improvement 11. LEL activity was not prompt and as required person was suiting up at the admin building rather than at the site of operation. 12. leaders of all firefighting team need to be more active. | 6.16 | Quarterly Inspection | 1723 | PATNA DEPOT | Take corrective action of scopes of improvement, mentioned | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146732 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146732 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146732 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016222ACN-2026-08-4000146732 |  | AUD-2026-08-2000016222ACN-2026-08-4000146732 | 21 |  | 27 | 80 | 0 | 0 | 55
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | 1. SCBA sets are periodically inspected and properly maintained to ensure their effective use during emergencies. 2. Training and awareness regarding the proper use of PPEs are given to all contract workmens | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143483 | Closed | DAS DARSHAN | 2026-07-30 | Last Mock Drill was conducted on Dtd: 02-04-2026, with scenerion of leakeage of oil from inlet valve while rake unloading and whilearresting due to non utilization of non-sparking tools Fire brole out. Response time was found to be satisfactory as per records. Following short comings were observed during the drill: 1. SCABA to be checked and maintained for effective usage during emergency. 2. Training on PPEs to be strengthened. 3. Matter needs to be taken up with mutual aid partners for participation during mock drills. 4. DCP Fire extinguishers usage to be ensured as first aid fire fighting equipment's during drills. 5. Portable MEFG to be putis use for targeting the spot for effective combat operation. Location worked on the short comings and all the observations/recommendations have been complied with. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1292 | LUCKNOW DEPOT | 1. SCBA sets need to be periodically inspected and properly maintained to ensure their effective use during emergencies. 2. Training and awareness regarding the proper use of PPEs need to be strengthened. Records to be maintained | SOD | Marketing | NCR | 2026-07-20 | THIRD PARTY ERRORS | 6 | PROCESS SAFETY | S3 | F2 | 2026-07-20 | AUD-2026-06-2000013451ACN-2026-07-4000143483 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143483 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143483 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013451ACN-2026-07-4000143483 | AUD-2026-06-2000013451ACN-2026-07-4000143483 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | The identified gaps have been addressed and validated during subsequent mock drills. | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143484 | Closed | DAS DARSHAN | 2026-07-30 | Location is a single-contingency location. A mock drill was conducted on 26/05/2026 in the presence of the Zonal Team. The overall response time was found to be satisfactory; however, the following shortcomings were observed during the drill: 1. During casualty evacuation, the casualty was carried with the head positioned incorrectly and in the opposite direction, which could adversely affect safe handling and transportation. 2. Personnel operating the fire hose were not adequately familiar with the locking position andwere observed handling the equipment in an improper manner. 3. During the simulated maintenance activity, no fire extinguisher wasdeployed at the affected work site, indicating non-compliance with basic fire safety requirements. | 2.2 | Double contingency scenario simulated; observations recorded | 1292 | LUCKNOW DEPOT | The mock drill response was generally satisfactory. However, focused training and periodic practical demonstrations should be conducted to improve casualty handling techniques, ensure personnel are proficient in the operation of fire-fighting equipment, and reinforce compliance with fire safety requirements, including mandatory deployment of fire extinguishers during maintenance activities. The identified gaps should be addressed and validated during subsequent mock drills. | SOD | Marketing | NCR | 2026-06-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013451ACN-2026-07-4000143484 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143484 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143484 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143484 | AUD-2026-06-2000013451ACN-2026-07-4000143484 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | All Faulty Camera have been rectified and hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143485 | Closed | DAS DARSHAN | 2026-07-30 |  | 2.6 | CCTV functioning checked | 1292 | LUCKNOW DEPOT | Location to ensure 100% uptime of all CCTVs. Faulty Camera to be rectified. | SOD | Marketing | NCR | 2026-08-15 | THIRD PARTY ERRORS | 6 | PROCESS SAFETY | S3 | F2 | 2026-08-15 | AUD-2026-06-2000013451ACN-2026-07-4000143485 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143485 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143485 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013451ACN-2026-07-4000143485 | AUD-2026-06-2000013451ACN-2026-07-4000143485 | 21 | 21 | 27 | 80 | 0 | 0 | 50 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | All Faulty Camera have been rectified and hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143486 | Closed | DAS DARSHAN | 2026-07-30 | A total of 75 CCTVs are integrated with the VA system, out of which 02 CCTVs are currently non-functional. MOC has been raised videMOC no: 3100002112 as verified on 21/05/2026. Nil VA alerts were generated pending as on date. | 2.7 | VA alerts checked / analysed | 1292 | LUCKNOW DEPOT | Location to ensure 100% uptime of all CCTVs. Faulty Camera to be rectified. | SOD | Marketing | NCR | 2026-08-15 | THIRD PARTY ERRORS | 6 | PROCESS SAFETY | S3 | F2 | 2026-08-15 | AUD-2026-06-2000013451ACN-2026-07-4000143486 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143486 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143486 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013451ACN-2026-07-4000143486 | AUD-2026-06-2000013451ACN-2026-07-4000143486 | 21 | 21 | 27 | 80 | 0 | 0 | 50 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | PAMS system is be used for Visitor Management at location. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143487 | Closed | DAS DARSHAN | 2026-07-30 | During the Visit Access control at main gate was checked and found that CBAC Systen was fully functional along with Biomatric operational at Main gate, entry to Licence area and Control room. The PAMS visitor management system is not being used for all the visitors entrering the premises. | 2.8 | Access control systems checked | 1292 | LUCKNOW DEPOT | PAMS system to to be used for Visitor Management at location. | SOD | Marketing | NCR | 2026-07-05 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-05 | AUD-2026-06-2000013451ACN-2026-07-4000143487 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143487 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143487 | 532 | 8294 | 21 | 8294 | 106 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143487 | AUD-2026-06-2000013451ACN-2026-07-4000143487 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | HCD was installed by MSA approved vendor and the height is as per design . Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143490 | Closed | DAS DARSHAN | 2026-07-30 | The height of the point-type HCD installed near the VRU shed is more and should be reduced to facilitate easy accessibility during emergency situations | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Reduce the installation height of the point-type HCD located near the VRU shed to ensure easy accessibility and prompt operation during emergency situations. | SOD | Marketing | NCR | 2026-08-20 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-20 | AUD-2026-06-2000013451ACN-2026-07-4000143490 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143490 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143490 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143490 | AUD-2026-06-2000013451ACN-2026-07-4000143490 | 21 | 21 | 27 | 80 | 0 | 0 | 51 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | Hooter No. 10 has been securely fixed and hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143493 | Closed | DAS DARSHAN | 2026-07-30 | Hooter No. 10 is not properly secured and shall be fixed appropriately to ensure reliable operation. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Securely fix Hooter No. 10 and verify its functionality to ensure reliable operation during emergency situations. | SOD | Marketing | NCR | 2026-07-07 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-07 | AUD-2026-06-2000013451ACN-2026-07-4000143493 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143493 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143493 | 532 | 8294 | 21 | 8294 | 104 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143493 | AUD-2026-06-2000013451ACN-2026-07-4000143493 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | There is no ESD in the VRU shed. The push button placed in VRU shed is to stop functioning of VRU operations in case of emergency in VRU shed | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143489 | Closed | DAS DARSHAN | 2026-07-30 | The VRU ESD name plate shall be prominently displayed alongside the Cause & Effect Matrix for easy identification and operational reference. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Display the VRU ESD nameplate prominently and place it alongside the Cause & Effect Matrix to facilitate quick identification and effective response during emergencies. | SOD | Marketing | NCR | 2026-07-07 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-07 | AUD-2026-06-2000013451ACN-2026-07-4000143489 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143489 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143489 | 532 | 8294 | 21 | 8294 | 104 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143489 | AUD-2026-06-2000013451ACN-2026-07-4000143489 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | all unused PLT lines have been Positively isolated by providing blind flanges. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143498 | Closed | DAS DARSHAN | 2026-07-30 | Unused PLT lines (from IOC) should be positively isolated by providing blind flanges wherever not provided. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Positively isolate all unused PLT lines by providing blind flanges and update the line isolation records accordingly to eliminate the risk of inadvertent product transfer. | SOD | Marketing | NCR | 2026-07-05 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-05 | AUD-2026-06-2000013451ACN-2026-07-4000143498 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143498 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143498 | 532 | 8294 | 21 | 8294 | 106 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143498 | AUD-2026-06-2000013451ACN-2026-07-4000143498 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
VED PRAKASH | 2026-08-06 | DAS DARSHAN | 2026-07-30 | Identification board of eyewash is placed near ethanol gantry | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143491 | Closed | DAS DARSHAN | 2026-07-30 | During visit name tag/identification marking not provided near eyewash stations near the Ethanol Gantry, ethanol pumps etc. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Location to ensure that proper name tags/identification markings for all field equipment for ease in equipment identification and operational safety. | SOD | Marketing | NCR | 2026-07-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-06-2000013451ACN-2026-07-4000143491 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143491 | 2026-09-03 | 46.7538 | 339 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143491 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143491 | AUD-2026-06-2000013451ACN-2026-07-4000143491 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | Location has reviewed the reports and necessary action wherever required is taken. Finalised reports expected to be received by 25.08.2026 | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000146388 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Compliance of pending observations of last visit and other audits at the location were reviewed and location advised for action wherever required. Manpower issue at location was discussed | 1.3 | Pending issues reviewed | 1259 | SRINAGAR DEPOT | Comprehensive Inspection of AG Tanks completed, Location to review the reports critically and take necessay action wherever required. | SOD | Marketing | NFZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 2 | ASSET INTEGRITY | S2 | F1 | 2026-08-31 | AUD-2026-08-2000016703ACN-2026-08-4000146388 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146388 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146388 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146388 | AUD-2026-08-2000016703ACN-2026-08-4000146388 | 21 | 21 | 27 | 80 | 2 | 1 | 52 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | Vegetation removed from gantry area | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000146389 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Housekeeping found in order. | 3.15 | Housekeeping & PPE usage checked | 1259 | SRINAGAR DEPOT | However, vegetation to be removed from TT Gantry area. | SOD | Marketing | NFZ | 2026-08-04 | INSUFFICIENT SUPERVISION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-08-04 | AUD-2026-08-2000016703ACN-2026-08-4000146389 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146389 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146389 | 532 | 8294 | 21 | 8294 | 76 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146389 | AUD-2026-08-2000016703ACN-2026-08-4000146389 | 21 | 21 | 27 | 80 | 2 | 1 | 49 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000146390 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Checked, one MOC of Tank Inspection found open. | 3.17 | MOC status reviewed | 1259 | SRINAGAR DEPOT | MOC closed by the Location during the visit. | SOD | Marketing | NFZ | 2026-08-01 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-01 | AUD-2026-08-2000016703ACN-2026-08-4000146390 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146390 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146390 | 532 | 8294 | 21 | 8294 | 79 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146390 | AUD-2026-08-2000016703ACN-2026-08-4000146390 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | location has initiated the proposal for budget . Location has darfted an action plan and compliances shall be ensured in a timebound manner | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000146391 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Pending compliances of OISD held in November were reviewed & necessary advice given for expediting the same. Location to initiate all proposals for compliance immediately for timely closure. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1259 | SRINAGAR DEPOT | Pending compliances to be closed in time bound manner. | SOD | Marketing | NFZ | 2026-12-31 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S3 | F2 | 2026-12-31 | AUD-2026-08-2000016703ACN-2026-08-4000146391 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146391 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146391 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016703ACN-2026-08-4000146391 | AUD-2026-08-2000016703ACN-2026-08-4000146391 | 21 | 21 | 27 | 80 | 2 | 1 | 70 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | project closure shall be ensured in time bound manner | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000146392 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Location to ensure timely closure of project - DG Set, Swing ladder and ATF Tank farm canopy | 4.3 | Project progress reviewed | 1259 | SRINAGAR DEPOT | Location to ensure closure of Projects in time bound manner. | SOD | Marketing | NFZ | 2026-12-31 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-12-31 | AUD-2026-08-2000016703ACN-2026-08-4000146392 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146392 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146392 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146392 | AUD-2026-08-2000016703ACN-2026-08-4000146392 | 21 | 21 | 27 | 80 | 2 | 1 | 70 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | RFD for all scrap initiated. scrap shall be disposed off in q2 | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000146393 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | RFD for all scrap Initiated at location, Follow up to be maintained for timely disposal | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1259 | SRINAGAR DEPOT | Location to follow-up and dispose the scrap at the earliest. | SOD | Marketing | NFZ | 2026-08-30 | INSUFFICIENT SUPERVISION | 6 | OCCUPATIONAL HEALTH | S2 | F3 | 2026-08-30 | AUD-2026-08-2000016703ACN-2026-08-4000146393 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146393 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146393 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016703ACN-2026-08-4000146393 | AUD-2026-08-2000016703ACN-2026-08-4000146393 | 21 | 21 | 27 | 80 | 2 | 1 | 52 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000146394 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | No tracability found | 6.1 | Hoses at TT Gantry | 1259 | SRINAGAR DEPOT | Tagging of hoses to be done | SOD | Marketing | NFZ | 2026-08-15 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-15 | AUD-2026-08-2000016703ACN-2026-08-4000146394 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146394 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146394 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146394 | AUD-2026-08-2000016703ACN-2026-08-4000146394 | 21 | 21 | 27 | 80 | 2 | 1 | 50 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied | LOCATION VISIT-SRINAGAR_22-24.07.26 | 2026-07-24 | AUD-2026-08-2000016703 | 2026-07-22 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-08-4000146395 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Double earthing of Air Compressor/Dryer not found | 6.2 | Air Compressor Shed | 1259 | SRINAGAR DEPOT | Earthing to be done | SOD | Marketing | NFZ | 2026-08-10 | INSUFFICIENT SUPERVISION | 2 | ASSET INTEGRITY | S2 | F1 | 2026-08-10 | AUD-2026-08-2000016703ACN-2026-08-4000146395 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016703ACN-2026-08-4000146395 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-08-2000016703 - ACN-2026-08-4000146395 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016703ACN-2026-08-4000146395 | AUD-2026-08-2000016703ACN-2026-08-4000146395 | 21 | 21 | 27 | 80 | 2 | 1 | 49 | 49
KOCHARA ASWINI KUMAR | 2026-08-07 | VIVEK KUMAR SAROJ | 2026-06-10 | The pending differential payment has been disbursed. | LOCATION VISIT-BATHINDA_10-11.03.26 | 2026-03-11 | AUD-2026-04-2000010747 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128564 | Closed | VIVEK KUMAR SAROJ | 2026-06-10 | Additional TTs to be inducted. Differential payment to be given to transporters. | 1.3 | Pending issues reviewed | 1164 | BHATINDA TERMINAL | Location to coordinate with Zonal Transportation for expediting the jobs. | SOD | Marketing | NFZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 12 | PROCESS SAFETY | S3 | F4 | 2026-04-30 | AUD-2026-04-2000010747ACN-2026-04-4000128564 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010747ACN-2026-04-4000128564 | 2026-09-28 19:00 | 20.9622 | 340 | >20 | AUD-2026-04-2000010747 - ACN-2026-04-4000128564 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010747ACN-2026-04-4000128564 | AUD-2026-04-2000010747ACN-2026-04-4000128564 | 21 | 21 | 26 | 80 | 1 | -2 | 35 | 49
KOCHARA ASWINI KUMAR | 2026-08-07 | VIVEK KUMAR SAROJ | 2026-06-10 | Bay No. 13 has been recalibrated. The product quantity is now in line with the totalizer reading, and no discrepancy is observed. | LOCATION VISIT-BATHINDA_10-11.03.26 | 2026-03-11 | AUD-2026-04-2000010747 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128565 | Closed | VIVEK KUMAR SAROJ | 2026-06-10 | Physical dip of TT No.PB03BT9941 checked at Bay#13 randomly and difference of 15 Litres found in one chamber & 10 Litres in anotherchamber. | 3.1 | TT discipline- fittings, post-loading dip checks, VTS deviations, ethanol blending performance, EM lock SOP compliance, Ethanol TT before & after unloading | 1164 | BHATINDA TERMINAL | Location advised to check the bay calibration. | SOD | Marketing | NFZ | 2026-04-15 | POOR PLANNING OR RISK ASSESSMENT | 12 | PROCESS SAFETY | S3 | F4 | 2026-04-15 | AUD-2026-04-2000010747ACN-2026-04-4000128565 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010747ACN-2026-04-4000128565 | 2026-09-28 19:00 | 20.9622 | 340 | >20 | AUD-2026-04-2000010747 - ACN-2026-04-4000128565 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010747ACN-2026-04-4000128565 | AUD-2026-04-2000010747ACN-2026-04-4000128565 | 21 | 21 | 26 | 80 | 1 | -2 | 33 | 49
KOCHARA ASWINI KUMAR | 2026-08-07 | VIVEK KUMAR SAROJ | 2026-06-10 |  | LOCATION VISIT-BATHINDA_10-11.03.26 | 2026-03-11 | AUD-2026-04-2000010747 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128566 | Closed |  |  | RFD processed, auction done & payment received. Final disposal awaited. | 4.3 | ) Progress on scrap disposal and unkeep of location to maintain a scrap-free environment | 1164 | BHATINDA TERMINAL | To be completed and capitalized before 31.03.2026 | SOD | Marketing | NFZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 8 | ENVIRONMENTAL | S2 | F4 | 2026-03-31 | AUD-2026-04-2000010747ACN-2026-04-4000128566 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010747ACN-2026-04-4000128566 | 2026-09-28 19:00 | 20.9622 | 340 | >20 | AUD-2026-04-2000010747 - ACN-2026-04-4000128566 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010747ACN-2026-04-4000128566 | AUD-2026-04-2000010747ACN-2026-04-4000128566 | 21 | 21 | 26 | 80 | 1 | -2 | 31 | 49
KOCHARA ASWINI KUMAR | 2026-08-07 | VIVEK KUMAR SAROJ | 2026-06-10 |  | LOCATION VISIT-BATHINDA_10-11.03.26 | 2026-03-11 | AUD-2026-04-2000010747 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128567 | Closed |  |  | 1. Few TTs at Gantry were found with earthing clip connected one over the another. | 5.0999999999999996 | TT Gantry | 1164 | BHATINDA TERMINAL | Location to take necessary corrective action | SOD | Marketing | NFZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-04-2000010747ACN-2026-04-4000128567 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010747ACN-2026-04-4000128567 | 2026-09-28 19:00 | 20.9622 | 340 | >20 | AUD-2026-04-2000010747 - ACN-2026-04-4000128567 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000010747ACN-2026-04-4000128567 | AUD-2026-04-2000010747ACN-2026-04-4000128567 | 21 | 21 | 26 | 80 | 1 | -2 | 31 | 49
KOCHARA ASWINI KUMAR | 2026-08-07 | VIVEK KUMAR SAROJ | 2026-06-10 |  | LOCATION VISIT-BATHINDA_10-11.03.26 | 2026-03-11 | AUD-2026-04-2000010747 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128568 | Closed |  |  | 2. Safety precautions to be taken for Bottom Loading TTs were discussed with the Location team in the wake of recent Sangrur incident. | 5.2 | TT Gantry | 1164 | BHATINDA TERMINAL | Location to take necessary corrective action | SOD | Marketing | NFZ | 2026-03-31 | FATIGUE AND STRESS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-04-2000010747ACN-2026-04-4000128568 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010747ACN-2026-04-4000128568 | 2026-09-28 19:00 | 20.9622 | 340 | >20 | AUD-2026-04-2000010747 - ACN-2026-04-4000128568 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010747ACN-2026-04-4000128568 | AUD-2026-04-2000010747ACN-2026-04-4000128568 | 21 | 21 | 26 | 80 | 1 | -2 | 31 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | 57 VA Camera's made live now | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138457 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Yes, VA alerts are checked and anlysed regularly, all CCTV's are down in VA. | 2.7 | VA alerts checked / analysed | 1397 | HPCL MANMAD IRD | Location to find out root cause for non-working VA & take up with vendor to resolve the issue | SOD | Marketing | WZ | 2026-06-30 | THIRD PARTY ERRORS | 12 | ASSET INTEGRITY | S3 | F4 | 2026-06-30 | AUD-2026-06-2000013154ACN-2026-06-4000138457 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138457 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138457 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013154ACN-2026-06-4000138457 | AUD-2026-06-2000013154ACN-2026-06-4000138457 | 21 | 21 | 27 | 80 | 7 | 7 | 44 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Proper housekeeping being done regularly. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138458 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Housekeeping of CP room was not found satisfactory | 6.1 | Housekeeping | 1397 | HPCL MANMAD IRD | Proper housekeeping to be maintained in CP room | SOD | Marketing | WZ | 2026-06-18 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-18 | AUD-2026-06-2000013154ACN-2026-06-4000138458 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138458 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138458 | 532 | 8294 | 21 | 8294 | 123 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013154ACN-2026-06-4000138458 | AUD-2026-06-2000013154ACN-2026-06-4000138458 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Panel filters being cleaned weekly now. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138459 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | PLC panel filters in the MCC room were found dusty, which may restrict airflow and affect proper cooling of the PLC system. | 6.2 | Housekeeping | 1397 | HPCL MANMAD IRD | Maintain clean filters to ensure adequate PLC panel cooling | SOD | Marketing | WZ | 2026-06-18 | INSUFFICIENT SUPERVISION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-18 | AUD-2026-06-2000013154ACN-2026-06-4000138459 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138459 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138459 | 532 | 8294 | 21 | 8294 | 123 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013154ACN-2026-06-4000138459 | AUD-2026-06-2000013154ACN-2026-06-4000138459 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Proper floor matting is provided in MCC panel room. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138460 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Proper floor matting not found in MCC room | 6.3 | General | 1397 | HPCL MANMAD IRD | Provide proper floor matting in MCC room to enhance safety. | SOD | Marketing | WZ | 2026-06-17 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-17 | AUD-2026-06-2000013154ACN-2026-06-4000138460 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138460 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138460 | 532 | 8294 | 21 | 8294 | 124 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013154ACN-2026-06-4000138460 | AUD-2026-06-2000013154ACN-2026-06-4000138460 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Emergency gate direction board provided. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138461 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Emergency gate direction board not found infront of gantry. | 6.4 | General | 1397 | HPCL MANMAD IRD | Emergency gate direction board to be placed as advised | SOD | Marketing | WZ | 2026-06-20 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-20 | AUD-2026-06-2000013154ACN-2026-06-4000138461 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138461 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138461 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013154ACN-2026-06-4000138461 | AUD-2026-06-2000013154ACN-2026-06-4000138461 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Ensured. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138462 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Gate separating license & delicensed area found open. | 6.5 | General | 1397 | HPCL MANMAD IRD | Gate separating license & delicensed area should be kept closed always. | SOD | Marketing | WZ | 2026-06-17 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-17 | AUD-2026-06-2000013154ACN-2026-06-4000138462 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138462 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138462 | 532 | 8294 | 21 | 8294 | 124 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013154ACN-2026-06-4000138462 | AUD-2026-06-2000013154ACN-2026-06-4000138462 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
MEHETRE KIRAN K | 2026-08-07 | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Proper cable dressing done. | ZONAL VISIT MANMAD IRD 030626 | 2026-06-03 | AUD-2026-06-2000013154 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138463 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-07 | Cable dressing beneath the solar panels was found to be improper. | 6.6 | General | 1397 | HPCL MANMAD IRD | Ensure proper cable dressing and secure routing beneath solar panels. | SOD | Marketing | WZ | 2026-06-17 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-06-17 | AUD-2026-06-2000013154ACN-2026-06-4000138463 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013154ACN-2026-06-4000138463 | 2026-09-08 | 41.7538 | 340 | >20 | AUD-2026-06-2000013154 - ACN-2026-06-4000138463 | 532 | 8294 | 21 | 8294 | 124 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013154ACN-2026-06-4000138463 | AUD-2026-06-2000013154ACN-2026-06-4000138463 | 21 | 21 | 27 | 80 | 7 | 7 | 42 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | comprehensive inspection completed | LOCATION VISIT-SRINAGAR_29.04.26 | 2026-04-29 | AUD-2026-05-2000011854 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129573 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Compliance of pending observations of last visit and other audits at the location were reviewed and location advised for action wherever required. Manpower issue at location was discussed | 1.3 | Pending issues reviewed | 1259 | SRINAGAR DEPOT | Location to make followup with Party for Starting Comprehensive Inspection of AG Tanks | SOD | Marketing | NFZ | 2026-11-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S3 | F1 | 2026-11-30 | AUD-2026-05-2000011854ACN-2026-05-4000129573 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011854ACN-2026-05-4000129573 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-05-2000011854 - ACN-2026-05-4000129573 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011854ACN-2026-05-4000129573 | AUD-2026-05-2000011854ACN-2026-05-4000129573 | 21 | 21 | 27 | 80 | 2 | 1 | 65 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied | LOCATION VISIT-SRINAGAR_29.04.26 | 2026-04-29 | AUD-2026-05-2000011854 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129574 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | All CCTV cameras working. Feed of CCTV No 27, 11,13 & 14 was checked. | 2.6 | CCTV functioning checked | 1259 | SRINAGAR DEPOT | Location to put Remote Door Lock on wicket gate for enhanced security | SOD | Marketing | NFZ | 2026-05-15 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-05-15 | AUD-2026-05-2000011854ACN-2026-05-4000129574 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011854ACN-2026-05-4000129574 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-05-2000011854 - ACN-2026-05-4000129574 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011854ACN-2026-05-4000129574 | AUD-2026-05-2000011854ACN-2026-05-4000129574 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied. RFDs initiated . scrap shall be disposed off by Q@ ending | LOCATION VISIT-SRINAGAR_29.04.26 | 2026-04-29 | AUD-2026-05-2000011854 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129575 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | RFD for all scrap Initiated at location, Follow up to be maintained for timely disposal | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1259 | SRINAGAR DEPOT | Location to ensure folowup and dispose the Scrap at the earliest. | SOD | Marketing | NFZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-09-30 | AUD-2026-05-2000011854ACN-2026-05-4000129575 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011854ACN-2026-05-4000129575 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-05-2000011854 - ACN-2026-05-4000129575 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000011854ACN-2026-05-4000129575 | AUD-2026-05-2000011854ACN-2026-05-4000129575 | 21 | 21 | 27 | 80 | 2 | 1 | 57 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | complied | LOCATION VISIT-SRINAGAR_18-19.03.26 | 2026-03-19 | AUD-2026-03-2000010828 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126113 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Two nos. HVLR operated. Two nos. HCD of Tank farm not functioning, sent to OEM for repair. Location advised to keep spare HCDs. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1259 | SRINAGAR DEPOT | Location to follow up for HCD repair and seek procurement of spare HCDs | SOD | Marketing | NFZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-07-30 | AUD-2026-03-2000010828ACN-2026-03-4000126113 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010828ACN-2026-03-4000126113 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-03-2000010828 - ACN-2026-03-4000126113 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010828ACN-2026-03-4000126113 | AUD-2026-03-2000010828ACN-2026-03-4000126113 | 21 | 21 | 26 | 80 | 2 | 1 | 48 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | matter taken up with the trasnporter and FE of both TTs replaced | LOCATION VISIT-SRINAGAR_18-19.03.26 | 2026-03-19 | AUD-2026-03-2000010828 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126114 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | Fire Extinguisher of TT No. JK05H2360 & JK01F9356 operated randomly both of which did not work. | 2.14 | TT crew fire extinguisher usage checked | 1259 | SRINAGAR DEPOT | Location to take up with transporter. | SOD | Marketing | NFZ | 2026-03-25 | INSUFFICIENT SUPERVISION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-25 | AUD-2026-03-2000010828ACN-2026-03-4000126114 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010828ACN-2026-03-4000126114 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-03-2000010828 - ACN-2026-03-4000126114 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010828ACN-2026-03-4000126114 | AUD-2026-03-2000010828ACN-2026-03-4000126114 | 21 | 21 | 26 | 80 | 2 | 1 | 30 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | RFDs alraaedy initiated. shall be disposed off by ending Q2 | LOCATION VISIT-SRINAGAR_18-19.03.26 | 2026-03-19 | AUD-2026-03-2000010828 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126115 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | RFD for Scrap available already done, pending for disposal. | 3.9 | Abnormal variations / unused assets reviewed | 1259 | SRINAGAR DEPOT | scrap disposal to be completed by 30.08.2026 | SOD | Marketing | NFZ | 2026-08-30 | INSUFFICIENT SUPERVISION | 2 | ENVIRONMENTAL | S1 | F2 | 2026-08-30 | AUD-2026-03-2000010828ACN-2026-03-4000126115 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010828ACN-2026-03-4000126115 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-03-2000010828 - ACN-2026-03-4000126115 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010828ACN-2026-03-4000126115 | AUD-2026-03-2000010828ACN-2026-03-4000126115 | 21 | 21 | 26 | 80 | 2 | 1 | 52 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | Water purifier and NVB projects already closed. 400 KVA DG set and swing ladders are in closing phase | LOCATION VISIT-SRINAGAR_18-19.03.26 | 2026-03-19 | AUD-2026-03-2000010828 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126116 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | 4 projects are in progress at location. | 4.3 | Project progress reviewed | 1259 | SRINAGAR DEPOT | To be completed and capitalized before 31.03.2026 | SOD | Marketing | NFZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010828ACN-2026-03-4000126116 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010828ACN-2026-03-4000126116 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-03-2000010828 - ACN-2026-03-4000126116 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010828ACN-2026-03-4000126116 | AUD-2026-03-2000010828ACN-2026-03-4000126116 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 49
WANI MOHAMMAD IDRESS | 2026-08-07 | GANIE IRFAN AHMAD | 2026-08-07 | RFD initiated | LOCATION VISIT-SRINAGAR_18-19.03.26 | 2026-03-19 | AUD-2026-03-2000010828 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126117 | Closed | GANIE IRFAN AHMAD | 2026-08-07 | RFD for Scrap available already done, pending for disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1259 | SRINAGAR DEPOT | location to dispose misc. scrap | SOD | Marketing | NFZ | 2026-08-30 | INSUFFICIENT SUPERVISION | 4 | ENVIRONMENTAL | S2 | F2 | 2026-08-30 | AUD-2026-03-2000010828ACN-2026-03-4000126117 | JK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010828ACN-2026-03-4000126117 | 2026-08-22 | 58.7538 | 340 | >20 | AUD-2026-03-2000010828 - ACN-2026-03-4000126117 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010828ACN-2026-03-4000126117 | AUD-2026-03-2000010828ACN-2026-03-4000126117 | 21 | 21 | 26 | 80 | 2 | 1 | 52 | 49
KOSHLENDRA SINGH YADAV | 2026-08-07 | SINGH YASHDEEP | 2026-08-07 | Revised budget has been alloted against all GL codes and Nalagarh bridging process has been smoothned from reporting till dispatch. | LOCATION VISIT-SANGRUR_20-23.05.26 | 2026-05-23 | AUD-2026-07-2000015041 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142656 | Closed | SINGH YASHDEEP | 2026-08-07 | Pending issue related to Budget, proposal , Shifting ot Nalagarh bridging reviewd | 1.3 | Pending issues reviewed | 1254 | JALANDHAR DEPOT | XX | SOD | Marketing | NFZ | 2026-06-15 | OUTDATED OR COMPLEX SOPS | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-15 | AUD-2026-07-2000015041ACN-2026-07-4000142656 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015041ACN-2026-07-4000142656 | 2026-08-21 | 59.7538 | 340 | >20 | AUD-2026-07-2000015041 - ACN-2026-07-4000142656 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015041ACN-2026-07-4000142656 | AUD-2026-07-2000015041ACN-2026-07-4000142656 | 21 | 21 | 27 | 80 | 0 | -21 | 41 | 49
KOSHLENDRA SINGH YADAV | 2026-08-07 | SINGH YASHDEEP | 2026-08-07 |  | LOCATION VISIT-SANGRUR_20-23.05.26 | 2026-05-23 | AUD-2026-07-2000015041 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142657 | Closed |  |  | Barrier for Calibration TT movement to be done on emergency route. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1254 | JALANDHAR DEPOT | Corrective action to be taken. | SOD | Marketing | NFZ | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | EMERGENCY | S2 | F2 | 2026-06-15 | AUD-2026-07-2000015041ACN-2026-07-4000142657 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015041ACN-2026-07-4000142657 | 2026-08-21 | 59.7538 | 340 | >20 | AUD-2026-07-2000015041 - ACN-2026-07-4000142657 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015041ACN-2026-07-4000142657 | AUD-2026-07-2000015041ACN-2026-07-4000142657 | 21 | 21 | 27 | 80 | 0 | -21 | 41 | 49
KOSHLENDRA SINGH YADAV | 2026-08-07 | SINGH YASHDEEP | 2026-08-07 |  | LOCATION VISIT-SANGRUR_20-23.05.26 | 2026-05-23 | AUD-2026-07-2000015041 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142659 | Closed |  |  | Scrap observed at Location & found it to be already in the process of disposal. 1) Possibility of shifting Old DGs to Noida/Bhatinda housing to be explored. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1254 | JALANDHAR DEPOT | Physical disposal to be expedited | SOD | Marketing | NFZ | 2026-06-30 | POOR COMMUNICATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015041ACN-2026-07-4000142659 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015041ACN-2026-07-4000142659 | 2026-08-21 | 59.7538 | 340 | >20 | AUD-2026-07-2000015041 - ACN-2026-07-4000142659 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015041ACN-2026-07-4000142659 | AUD-2026-07-2000015041ACN-2026-07-4000142659 | 21 | 21 | 27 | 80 | 0 | -21 | 44 | 49
KOSHLENDRA SINGH YADAV | 2026-08-07 | SINGH YASHDEEP | 2026-08-07 |  | LOCATION VISIT-SANGRUR_20-23.05.26 | 2026-05-23 | AUD-2026-07-2000015041 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142658 | Closed |  |  | Adequate foam invetory is available for both AFFF & ARAFFF 1) ARAFFF SOP to be provided 2) Extra cable & pole from foam shed is to be removed. 3) Cross over to be provided in foam shed | 2.9 | Foam inventory verified | 1254 | JALANDHAR DEPOT | Corrective action to be taken. | SOD | Marketing | NFZ | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-06-15 | AUD-2026-07-2000015041ACN-2026-07-4000142658 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015041ACN-2026-07-4000142658 | 2026-08-21 | 59.7538 | 340 | >20 | AUD-2026-07-2000015041 - ACN-2026-07-4000142658 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015041ACN-2026-07-4000142658 | AUD-2026-07-2000015041ACN-2026-07-4000142658 | 21 | 21 | 27 | 80 | 0 | -21 | 41 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Contaminated product disposed of on 24.07.2026. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122482 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Yes, to dispose off 12 Kl contaminated product. | 1.3 | Pending issues reviewed | 1485 | AKOLA DEPOT | To follow up MRII for disposal. | SOD | Marketing | WZ | 2026-06-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011118ACN-2026-03-4000122482 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122482 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122482 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122482 | AUD-2026-03-2000011118ACN-2026-03-4000122482 | 21 | 21 | 26 | 80 | 3 | 3 | 44 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Point repeated from point no. 2.11 from Senior inspection audit dtd. 02.06.26 | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122488 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Location has 4 HVLR, 3 point type HCD, 5 open path HCD, 12+1 ESDs all are functioning properly | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1485 | AKOLA DEPOT | Replace ESD buttons from break glass type to push type | SOD | Marketing | WZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 3 | ASSET INTEGRITY | S3 | F1 | 2026-03-31 | AUD-2026-03-2000011118ACN-2026-03-4000122488 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122488 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122488 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122488 | AUD-2026-03-2000011118ACN-2026-03-4000122488 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Complied | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122484 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Reviewed and found OK | 2.5 | Emergency response preparedness reviewed | 1485 | AKOLA DEPOT | Location to replace existing hand siren with new with in built wailing sound mechanism | SOD | Marketing | WZ | 2026-03-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-15 | AUD-2026-03-2000011118ACN-2026-03-4000122484 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122484 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122484 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122484 | AUD-2026-03-2000011118ACN-2026-03-4000122484 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Area wise CCTV templates prepared for CCTV monitoring. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122485 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Location is having 68 CCTVs and all are working | 2.6 | CCTV functioning checked | 1485 | AKOLA DEPOT | Location to provide areawise CCTV view templates in security display at main gate | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011118ACN-2026-03-4000122485 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122485 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122485 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122485 | AUD-2026-03-2000011118ACN-2026-03-4000122485 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Ticket raised for the false alarm and now, no false alarms generating. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122486 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Yes, VA alerts are checked and anlysed regularly, all CCTVs in VA are working, fake alarms are generating at location related to lower LUX levels at Emergency Gate | 2.7 | VA alerts checked / analysed | 1485 | AKOLA DEPOT | Location to raise the tickets for all such fake alarms if any in Avathon Portal as provision is there to raise such issues | SOD | Marketing | WZ | 2026-03-15 | INSTRUMENTATION OR ALARM FAILURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011118ACN-2026-03-4000122486 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122486 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122486 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122486 | AUD-2026-03-2000011118ACN-2026-03-4000122486 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Complied | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122490 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Yes PPE are used by location and housekeeping is in proper condition. Depot roads observed clean but the fine stone aggregates have chipped off from bitumen | 3.15 | Housekeeping & PPE usage checked | 1485 | AKOLA DEPOT | Location to take corrective action on same to avoid further deterioration and slipping in case of any emergency | SOD | Marketing | WZ | 2026-05-15 | THIRD PARTY ERRORS | 2 | ASSET INTEGRITY | S2 | F1 | 2026-05-15 | AUD-2026-03-2000011118ACN-2026-03-4000122490 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122490 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122490 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122490 | AUD-2026-03-2000011118ACN-2026-03-4000122490 | 21 | 21 | 26 | 80 | 3 | 3 | 37 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Complied. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122492 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Yes, full field round taken and covered all the sites. At wagon gantry few hoses were found with open ends | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1485 | AKOLA DEPOT | Location to ensure that Wagon decantation product pipes are kept with ends closed | SOD | Marketing | WZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 3 | PROCESS SAFETY | S1 | F3 | 2026-03-15 | AUD-2026-03-2000011118ACN-2026-03-4000122492 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122492 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122492 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122492 | AUD-2026-03-2000011118ACN-2026-03-4000122492 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Location procured 2 no.s of Emergency Escape Sets 15 min. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122493 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Emergency Trolly does not have 15 min Emergency Escape Set | 6.1 | Emergency Trolly | 1485 | AKOLA DEPOT | Location to procure 2 sets of 15 min Emergency Escape Set and ensure its availability and functioning | SOD | Marketing | WZ | 2026-03-15 | INADEQUATE SAFETY CULTURE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-15 | AUD-2026-03-2000011118ACN-2026-03-4000122493 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122493 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122493 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122493 | AUD-2026-03-2000011118ACN-2026-03-4000122493 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Pressure gauges tested and faulty pressure gauges replaced. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122495 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Pressure Guage at cooling water line of fire engine 2 is not working | 6.4 | Fire Engine Shed | 1485 | AKOLA DEPOT | Location to replace the gauge or rectify the exisiting gauge | SOD | Marketing | WZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 3 | ASSET INTEGRITY | S1 | F3 | 2026-03-15 | AUD-2026-03-2000011118ACN-2026-03-4000122495 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122495 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122495 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122495 | AUD-2026-03-2000011118ACN-2026-03-4000122495 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Contaminated product disposed off on 24.07.26. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146513 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Yes, to dispose off 12 Kl contaminated product. | 1.3 | Pending issues reviewed | 1485 | AKOLA DEPOT | To follow up MRII for disposal. | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146513 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146513 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146513 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146513 | AUD-2026-06-2000013155ACN-2026-07-4000146513 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Delivery box of TT No. 6061 is repaired. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146516 | Closed | BAGADE AMAR ARUN | 2026-08-07 | TPI records were available and verified. However, during a random check of TT No. 6061, the delivery box was found in poor condition | 3.1 | TT fittings & discipline checked | 1485 | AKOLA DEPOT | Rectify the condition of the delivery box of TT No. 6061 and strengthen periodic inspection to ensure compliance. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146516 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146516 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146516 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013155ACN-2026-07-4000146516 | AUD-2026-06-2000013155ACN-2026-07-4000146516 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Lady security guard is deployed in general shift at location. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146519 | Closed | BAGADE AMAR ARUN | 2026-08-07 | No lady security guard is available at the depot. | 6.2 | Lady Security unavailibilty | 1485 | AKOLA DEPOT | To engage a lady security guard through the existing security contract | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146519 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146519 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146519 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146519 | AUD-2026-06-2000013155ACN-2026-07-4000146519 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Repeatability of Point no. 6.1 of the current audit. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146525 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Fire engines were found operating satisfactorily in Auto mode as per logic. However, leakage was observed in Fire Engine-2 (FE-2). | 6.8 | Fire engie 2 operation | 1485 | AKOLA DEPOT | Rectify the leakage in FE-2 and ensure proper operation of the fire engine. | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146525 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146525 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146525 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146525 | AUD-2026-06-2000013155ACN-2026-07-4000146525 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 49
KATAKAM SRINIVAS | 2026-08-07 | BAGADE AMAR ARUN | 2026-08-07 | Repeated point no. 6.1 and 6.8 mentioned. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146526 | Closed | BAGADE AMAR ARUN | 2026-08-07 | Cooling water line of fire engine is in close loop, thus difficult to ensure its flowability | 6.9 | Fire Engine Shed | 1485 | AKOLA DEPOT | To provide in consultation with OEM | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146526 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146526 | 2026-08-24 | 56.7538 | 340 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146526 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013155ACN-2026-07-4000146526 | AUD-2026-06-2000013155ACN-2026-07-4000146526 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 49
|  | RANA PULKIT | 2026-08-08 | Lux level maintained as per OISD 244 | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125603 | Completed | RANA PULKIT | 2026-08-08 | Yes, lux level at all operating areas meets OISD STD 244 and are checked monthly and records maintained | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1509 | SHOLAPUR TERMINAL | Location to review for improvement in LUX levels at gantry, and ethanol unloading gantry | SOD | Marketing | WZ | 2026-04-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011316ACN-2026-03-4000125603 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125603 | 2026-09-19 | 30.7538 | 241 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125603 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125603 |  | AUD-2026-03-2000011316ACN-2026-03-4000125603 | 21 |  | 26 | 80 | 0 | 0 | 35
|  | RANA PULKIT | 2026-08-08 | All turnstile working now | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125604 | Completed | RANA PULKIT | 2026-08-08 | Location has 6 turnstiles for access control system and are working, except for turnstile at Control room and near 103A | 2.8 | Access control systems checked | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-04-30 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011316ACN-2026-03-4000125604 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125604 | 2026-09-19 | 30.7538 | 241 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125604 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125604 |  | AUD-2026-03-2000011316ACN-2026-03-4000125604 | 21 |  | 26 | 80 | 0 | 0 | 35
|  | RANA PULKIT | 2026-08-08 | currently stock is meeting the requirement | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125605 | Completed | RANA PULKIT | 2026-08-08 | Requirement-18.9 KL(AFFF), 4.45KL(AR-AFFF) Total Qty as on date -12KL(AFFF), 700LTR(AR-AFFF), INTRANSIT- 7.6KL(AFFF), 4.3(AR-AFFF). | 2.9 | Foam inventory verified | 1509 | SHOLAPUR TERMINAL | Foam qty to be maintained as per OISD requirement | SOD | Marketing | WZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125605 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125605 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125605 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125605 |  | AUD-2026-03-2000011316ACN-2026-03-4000125605 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | RANA PULKIT | 2026-08-08 | All break-glass type ESDs replaced with Push-pull button ESD | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125606 | Completed | RANA PULKIT | 2026-08-08 | Location has 7 HVLR, 10 point type HCD, 7 open path HCD, 18+1 ESDs all are functioning properly | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1509 | SHOLAPUR TERMINAL | Replace ESD buttons from break glass type to push type | SOD | Marketing | WZ | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011316ACN-2026-03-4000125606 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125606 | 2026-09-19 | 30.7538 | 302 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125606 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125606 |  | AUD-2026-03-2000011316ACN-2026-03-4000125606 | 21 |  | 26 | 80 | 0 | 0 | 44
|  | RANA PULKIT | 2026-08-08 | projects completed and closed in SAP | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125608 | Completed | RANA PULKIT | 2026-08-08 | 2 projects are in progress at location. | 4.3 | Project progress reviewed | 1509 | SHOLAPUR TERMINAL | To be completed and capitalized before 31.03.2026 | SOD | Marketing | WZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125608 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125608 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125608 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125608 |  | AUD-2026-03-2000011316ACN-2026-03-4000125608 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | RANA PULKIT | 2026-08-08 | PM jobs completed | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125609 | Completed | RANA PULKIT | 2026-08-08 | Following is the PM performance of location for last 3 month Dec 25-100% Jan 26-100% Feb 26-100% Mar 26-0% | 4.4 | Quality of PM compliance reviewed | 1509 | SHOLAPUR TERMINAL | PM jobs for March'26 to be completed before 31.03.2026 | SOD | Marketing | WZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125609 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125609 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125609 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125609 |  | AUD-2026-03-2000011316ACN-2026-03-4000125609 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | RANA PULKIT | 2026-08-08 | all items maintained as per checklist of trolley | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125611 | Completed | RANA PULKIT | 2026-08-08 | Checked, found ok Second breathing appratus to be kept inside trolley, items to be rearranged as per name plate on shelf | 6.1 | Emergency Trolly | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125611 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125611 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125611 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125611 |  | AUD-2026-03-2000011316ACN-2026-03-4000125611 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | RANA PULKIT | 2026-08-08 | repairing done, leakage arrested | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125612 | Completed | RANA PULKIT | 2026-08-08 | FE-03 has some water leakage issued from head, same to be rectified at the earliest | 6.3 | Fire Engine Shed | 1509 | SHOLAPUR TERMINAL | location to take necessary corrective action | SOD | Marketing | WZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125612 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125612 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125612 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125612 |  | AUD-2026-03-2000011316ACN-2026-03-4000125612 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | KUMAR KULDEEP | 2026-08-08 | All scrap has been dsiposed off. Other assets lying at Bijwasan belong to DRO and Aviation. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122497 | Completed | KUMAR KULDEEP | 2026-08-08 | 1. Delhi Terminal has four company-owned, 23 KL tank trucks. These TTs are presently underutilized due to non-availability of matching indents. The TTs have been offered to other locations; however, no response has been received. As per norms, these TTs can be operated for a maximum period of 10 years. They have already completed 8 years of service and, in any case, will be required to be declared obsolete after completion of their service life. 2. Bijwasan Terminal Land of approx 15 acre is under control of Delhi Terminal. Delhi Terminal has provided very limited security i.e One guard in each sift to avoid any encroachment and manning of main Gate. However different SBU's are storing like Retail, Aviation and INC are storing their various materials in this premises. These SBU's has already been conveyed to review safety, security, ward and watch of their material. | 1.3 | Pending issues reviewed | 1221 | DELHI TERMINAL | 1. Transfer of Company owned TT's to another Location. | SOD | Marketing | NZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011120ACN-2026-03-4000122497 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000122497 | 2026-08-27 | 53.7538 | 211 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000122497 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011120ACN-2026-03-4000122497 |  | AUD-2026-03-2000011120ACN-2026-03-4000122497 | 21 |  | 26 | 80 | 3 | 3 | 31
ALBY ABRAHAM ARACKAL | 2026-08-08 | SRIJIN S | 2026-08-08 | Legal compliance report is being maintained on quarterly basis with applicable rules and acts with due dates. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130103 | Closed | SRIJIN S | 2026-08-08 | All Compliance reviewed and complied | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1833 | COCHIN BLACK TERMINAL | Maintain a register of compliances for all satutory licenses with applicable clauses | SOD | Marketing | CZR | 2026-05-31 | FAILURE TO FOLLOW PROCEDURES | 6 | OCCUPATIONAL HEALTH | S2 | F3 | 2026-05-31 | AUD-2026-05-2000012202ACN-2026-05-4000130103 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130103 | 2026-09-08 16:00 | 41.0872 | 341 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130103 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130103 | AUD-2026-05-2000012202ACN-2026-05-4000130103 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 49
ALBY ABRAHAM ARACKAL | 2026-08-08 | SRIJIN S | 2026-08-08 | HIRA available and all the associated risks are available and updated in the HIRA.FFE availability Vs requirement chart available. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130107 | Closed | SRIJIN S | 2026-08-08 | Reviewed during visit; found satisfactory. | 2.5 | Emergency response preparedness reviewed | 1833 | COCHIN BLACK TERMINAL | Advise to maintain risk register. Develop FFE availability Vs requirement chart | SOD | Marketing | CZR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 2 | OCCUPATIONAL HEALTH | S1 | F2 | 2026-06-30 | AUD-2026-05-2000012202ACN-2026-05-4000130107 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130107 | 2026-09-08 16:00 | 41.0872 | 341 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130107 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130107 | AUD-2026-05-2000012202ACN-2026-05-4000130107 | 21 | 21 | 27 | 80 | 2 | 0 | 44 | 49
ALBY ABRAHAM ARACKAL | 2026-08-08 | SRIJIN S | 2026-08-08 | HMV license available with 2 security guards. In case of emergency and none of the TT drivers are available, the security guards may operate the TT to a safe position. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130109 | Closed | SRIJIN S | 2026-08-08 | Not available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1833 | COCHIN BLACK TERMINAL | Security Gaurds with HVD HZA endorsement to be identified | SOD | Marketing | CZR | 2026-05-30 | POOR PLANNING OR RISK ASSESSMENT | 2 | EMERGENCY | S2 | F1 | 2026-05-30 | AUD-2026-05-2000012202ACN-2026-05-4000130109 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130109 | 2026-09-08 16:00 | 41.0872 | 341 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130109 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130109 | AUD-2026-05-2000012202ACN-2026-05-4000130109 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 49
|  | LAD SARTHAK DILIP | 2026-08-08 | Fire Engine display are in working condition | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125724 | Open | LAD SARTHAK DILIP | 2026-08-08 | Checked working of Fire engines and found working. FE display needs to be made functional and ensure correct values are displayed. | 2.5 | Emergency response preparedness reviewed | 1504 | MIRAJ TERMINAL | Display parameters to be checked and corrected | SOD | Marketing | WZ | 2026-05-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-15 | AUD-2026-03-2000010875ACN-2026-03-4000125724 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125724 | 2026-09-01 | 48.7538 | 256 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125724 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010875ACN-2026-03-4000125724 |  | AUD-2026-03-2000010875ACN-2026-03-4000125724 | 21 |  | 26 | 80 | 0 | -1 | 37
DEWADE SHAHAJI NAGORAO | 2026-08-08 | LAD SARTHAK DILIP | 2026-08-08 | Needful is done | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125731 | Closed | LAD SARTHAK DILIP | 2026-08-08 | Color code is same as Ethanol pump color code | 6.3 | SLOP color code | 1504 | MIRAJ TERMINAL | SLOP pump color coding to be changed to grey or black | SOD | Marketing | WZ | 2026-04-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010875ACN-2026-03-4000125731 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125731 | 2026-09-01 | 48.7538 | 341 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125731 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125731 | AUD-2026-03-2000010875ACN-2026-03-4000125731 | 21 | 21 | 26 | 80 | 0 | -1 | 33 | 49
DEWADE SHAHAJI NAGORAO | 2026-08-08 | LAD SARTHAK DILIP | 2026-08-08 | Corrective action is taken. RSFPS is in working condition now. | MIRAJ LOCATION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016453 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146540 | Closed | LAD SARTHAK DILIP | 2026-08-08 | Rim seal protection one module of tank 101A was not operated. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1504 | MIRAJ TERMINAL | Corrective action to be taken | SOD | Marketing | WZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016453ACN-2026-07-4000146540 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016453ACN-2026-07-4000146540 | 2026-09-01 | 48.7538 | 341 | >20 | AUD-2026-07-2000016453 - ACN-2026-07-4000146540 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016453ACN-2026-07-4000146540 | AUD-2026-07-2000016453ACN-2026-07-4000146540 | 21 | 21 | 27 | 80 | 0 | -1 | 44 | 49
DEWADE SHAHAJI NAGORAO | 2026-08-08 | LAD SARTHAK DILIP | 2026-08-08 | Containment area is provided near to pipeline manifold and TLF pump house. | MIRAJ LOCATION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016453 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146541 | Closed | LAD SARTHAK DILIP | 2026-08-08 | Contianment area is not provided for drain near pump house | 6.2 | Drain near pump house | 1504 | MIRAJ TERMINAL | Location to check and provide the containment area for pipeline manifold and TLF pump house. | SOD | Marketing | WZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016453ACN-2026-07-4000146541 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016453ACN-2026-07-4000146541 | 2026-09-01 | 48.7538 | 341 | >20 | AUD-2026-07-2000016453 - ACN-2026-07-4000146541 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016453ACN-2026-07-4000146541 | AUD-2026-07-2000016453ACN-2026-07-4000146541 | 21 | 21 | 27 | 80 | 0 | -1 | 44 | 49
DEWADE SHAHAJI NAGORAO | 2026-08-08 | LAD SARTHAK DILIP | 2026-08-08 | Required modifications are done in the dyke drain valve of 101A, 101B & 103A | MIRAJ LOCATION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016453 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146542 | Closed | LAD SARTHAK DILIP | 2026-08-08 | Provision for diverting the dyke outlet either to storm water or OWS is not available for tank 101A, 101B and 103A. Modification required in piping. | 6.3 | dyke drain | 1504 | MIRAJ TERMINAL | Corrective action to be taken | SOD | Marketing | WZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016453ACN-2026-07-4000146542 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016453ACN-2026-07-4000146542 | 2026-09-01 | 48.7538 | 341 | >20 | AUD-2026-07-2000016453 - ACN-2026-07-4000146542 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016453ACN-2026-07-4000146542 | AUD-2026-07-2000016453ACN-2026-07-4000146542 | 21 | 21 | 27 | 80 | 0 | -1 | 44 | 49
SUJEET KUMAR | 2026-08-09 | SAXENA UMESH CHANDRA | 2026-08-08 | A three-day Fire Extinguisher Check-up Camp was organized at Indore New IRD from 27.07.2026 to 29.07.2026 for inspection and checking of fire extinguishers installed on Tank Trucks (TTs). The report of the camp is enclosed as documentary evidence. Further, training on the operation and proper use of fire extinguishers was imparted to TT crew and contract workmen on 04.08.2026. Photographs of the training are enclosed as evidence. Going forward, periodic training on the operation and use of fire extinguishers to TT crew shall be continued to reinforce their competency and ensure effective response during fire emergencies. In view of the above actions taken and documentary evidence enclosed, the audit observation may kindly be treated as complied with and closed. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000135380 | Closed | SAXENA UMESH CHANDRA | 2026-08-08 | Yes, operated thru one cleaner of TT Nos: NL07 AA 2448 and MP09 AM 9954 . There was a leakage from one of the hose pipe of Fire Extinhuisher (TT No: MP09 AM 9954). | 2.14 | TT crew fire extinguisher usage checked | 1457 | INDORE DEPOT | Refresher training to be imparted to all the TT crew. Also, the periodical checking/testing of hose of Fire Extinuisher is to be done. | SOD | Marketing | CEN | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | EMERGENCY | S1 | F4 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135380 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135380 | 2026-09-09 19:00 | 39.9622 | 342 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135380 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135380 | AUD-2026-06-2000012547ACN-2026-06-4000135380 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 49
KUNDU DEBARUN | 2026-08-09 | ISLAM SK WAHIUL | 2026-08-09 | 1. Dry Leaves cleaned beside TT planning room under de-licenced area. Housekkeping maintained properly. 2. Green Grass trimmed around entire black oil dyke. Vegetations removed below black oil pipeline. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143416 | Closed | ISLAM SK WAHIUL | 2026-08-09 | During last visit, it was advised to have good housekeeping specially in the backside of the black oil tanks. Location had improvedsignificantly w.r.t last visit however following were observed : 1. Dry Leaves beside TT planning room under de-licenced area 2. Green Grass observed the pipeline across black oil | 1.4 | Earlier action points status checked | 1650 | HALDIA TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143416 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143416 | 2026-08-20 00:14 | 60.7441 | 342 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143416 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143416 | AUD-2026-07-2000015092ACN-2026-07-4000143416 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 49
KUNDU DEBARUN | 2026-08-09 | ISLAM SK WAHIUL | 2026-08-09 | SDD replaced. VA service is online and all the CCTV are active over VA. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | SDD REPLACED. VA SERVICE IS ONLINE AND A | ACN-2026-07-4000143425 | Closed | ISLAM SK WAHIUL | 2026-08-09 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. CCTVs were not active over VA. It was given to understand that there was issue in VA server for which SDD replacement is required. | 2.7 | VA alerts checked / analysed | 1650 | HALDIA TERMINAL | Location to closely coordinate with vendor and get the VA active. | SOD | Marketing | EZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143425 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143425 | 2026-08-20 00:14 | 60.7441 | 342 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143425 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143425 | AUD-2026-07-2000015092ACN-2026-07-4000143425 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 49
KUNDU DEBARUN | 2026-08-09 | ISLAM SK WAHIUL | 2026-08-09 | b. PPE usage is more strengthened. SST conducted at regular intervals and as VA is active, any deviation can be immediately addressed. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143436 | Closed | ISLAM SK WAHIUL | 2026-08-09 | a. Housekeeping practice is found satisfactory. b. PPE usages to be more streamlined and strengthened. | 3.15 | Housekeeping & PPE usage checked | 1650 | HALDIA TERMINAL | b. Corrective action to be taken. | SOD | Marketing | EZ | 2026-06-30 | INADEQUATE SAFETY CULTURE | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143436 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143436 | 2026-08-20 00:14 | 60.7441 | 342 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143436 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143436 | AUD-2026-07-2000015092ACN-2026-07-4000143436 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 49
KUNDU DEBARUN | 2026-08-09 | ISLAM SK WAHIUL | 2026-08-09 | EBP checks done daily of the loaded trucks and records maintained. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143430 | Closed | ISLAM SK WAHIUL | 2026-08-09 | Random checking of EBP done from the all level sample of TT WB354344 & WB33D8985 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1650 | HALDIA TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143430 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143430 | 2026-08-20 00:14 | 60.7441 | 342 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143430 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143430 | AUD-2026-07-2000015092ACN-2026-07-4000143430 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 49
DEVA DHRUVA | 2026-08-09 |  |  | Location conducted balanced 3 fire drill scenario and all ERDMP scenario covered. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122788 | Closed | DEVA DHRUVA | 2026-08-09 | Locations tankages are less than 30k and hence is single contingency. Drills conducted in 10 out of total 13 ERDMP scenarios . Observation recorded and corrective actions taken. Safety committee conducted on 23-12-2026. 4 Recommendation were recorded . One pending to be complied. | 2.2 | Double contingency scenario simulated; observations recorded | 1800 | HUBLI DEPOT | Location shall conduct fire drill in balance 3 sceneraio also in next four months | SOD | Marketing | SWZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-03-2000011030ACN-2026-03-4000122788 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122788 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122788 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122788 | AUD-2026-03-2000011030ACN-2026-03-4000122788 | 21 | 21 | 26 | 80 | 18 | 18 | 48 | 49
DEVA DHRUVA | 2026-08-09 |  |  | All RFD initiated by location. Auction pending at CPO for pending MSTC agreement and soon RFD will be completed. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122799 | Closed | DEVA DHRUVA | 2026-08-09 | Close monitoring and compliance is required. | 4.5 | 2 no of RFD in process, oit of 10 lots 3 lots were reauctioned.Opening on 23.03.26 | 1800 | HUBLI DEPOT | Close monitoring and compliance is required. | SOD | Marketing | SWZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011030ACN-2026-03-4000122799 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122799 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122799 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122799 | AUD-2026-03-2000011030ACN-2026-03-4000122799 | 21 | 21 | 26 | 80 | 18 | 18 | 31 | 49
DEVA DHRUVA | 2026-08-09 |  |  | Eye checkup completed and all TT crew, contract workmen, Security and GAT did the checkup. Spectacles given to required ones. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138628 | Closed | DEVA DHRUVA | 2026-08-09 | Medical Eye check up is scheduled on 25th and 26th May, 2026. Vendor confirmed the schedule for the awareness. | 2.16 | Eyesight / colour-blindness awareness checked | 1800 | HUBLI DEPOT | To complete the Eye Check Up and send report with photos | SOD | Marketing | SWZ | 2026-06-25 | POOR COMMUNICATION | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-06-25 | AUD-2026-06-2000012499ACN-2026-06-4000138628 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138628 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138628 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138628 | AUD-2026-06-2000012499ACN-2026-06-4000138628 | 21 | 21 | 27 | 80 | 18 | 18 | 43 | 49
DEVA DHRUVA | 2026-08-09 |  |  | Location vegetation and housekeeping has been improved significantly. Regularly grass cutting in all the depot area is being done. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138633 | Closed | DEVA DHRUVA | 2026-08-09 | Vegitation issue is there due to long rainy season. However regular grass cutting is under progress. | 3.16 | Earth pits / boundary / vegetation control checked | 1800 | HUBLI DEPOT | Location to ensure good housekeeping and clear vegetation growth regularly. | SOD | Marketing | SWZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-06-2000012499ACN-2026-06-4000138633 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138633 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138633 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138633 | AUD-2026-06-2000012499ACN-2026-06-4000138633 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 49
DEVA DHRUVA | 2026-08-09 |  |  | Bay no. 7 bottom loading arm leak rectified. All bays checked and ensured nil leakage and better housekeeping. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138635 | Closed | DEVA DHRUVA | 2026-08-09 | All operational areas were inspected and observed to be satisfactory | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1800 | HUBLI DEPOT | Bay no. 7 bottom loading arm was leaking. All bay to be checked and ensured nil leakage and better housekeeping. | SOD | Marketing | SWZ | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 9 | PROCESS SAFETY | S3 | F3 | 2026-06-15 | AUD-2026-06-2000012499ACN-2026-06-4000138635 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138635 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138635 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012499ACN-2026-06-4000138635 | AUD-2026-06-2000012499ACN-2026-06-4000138635 | 21 | 21 | 27 | 80 | 18 | 18 | 41 | 49
DEVA DHRUVA | 2026-08-09 |  |  | All RFD initiated by location. Auction pending at CPO for pending MSTC agreement and soon RFD will be completed. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138638 | Closed | DEVA DHRUVA | 2026-08-09 | Location already scrapped 10.9 MT of misc scrap having value of around 6 lakhs. Remaining are under auction pjase. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1800 | HUBLI DEPOT | There are many scrap items lying at many places to be disposed off. To process RFDs immediately and dispose them off in H1. | SOD | Marketing | SWZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-06-2000012499ACN-2026-06-4000138638 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138638 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138638 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138638 | AUD-2026-06-2000012499ACN-2026-06-4000138638 | 21 | 21 | 27 | 80 | 18 | 18 | 57 | 49
DEVA DHRUVA | 2026-08-09 |  |  | CBAC working fine and all turnstoil also working properly. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138640 | Closed | DEVA DHRUVA | 2026-08-09 | CBACs server down last 2 days. CBACS @Delicensed to Licensed Not Working | 6.2 | CBACs | 1800 | HUBLI DEPOT | To rectify the same and put back into operation | SOD | Marketing | SWZ | 2026-05-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-06-2000012499ACN-2026-06-4000138640 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138640 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138640 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138640 | AUD-2026-06-2000012499ACN-2026-06-4000138640 | 21 | 21 | 27 | 80 | 18 | 18 | 39 | 49
DEVA DHRUVA | 2026-08-09 |  |  | This audit point is erroneously added, not related to Hubli New IRD. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138641 | Closed | DEVA DHRUVA | 2026-08-09 | MRPL to MAPOL pipeline rack bottom PCC not there | 6.3 | PCC below pipeline | 1800 | HUBLI DEPOT | MRPL to MAPOL pipeline rack bottom to be made PCC | SOD | Marketing | SWZ | 2026-12-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-06-2000012499ACN-2026-06-4000138641 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138641 | 2026-09-11 19:30 | 37.9413 | 342 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138641 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138641 | AUD-2026-06-2000012499ACN-2026-06-4000138641 | 21 | 21 | 27 | 80 | 18 | 18 | 70 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | All TTs are being strictly checked by Security and random checks conducted by officers for Fire extinguisher with valid last maintenance date and Extinguisher pressure. TT crew has been trained again regarding use of the same and randomly asked to show application of fire extinguishers. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122636 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Found Okay . However TPT M/s Sura Murmu DCP 9kg found not operative as pressure was NIL | 2.14 | TT crew fire extinguisher usage checked | 1636 | BALASORE DEPOT | Advised planning officer to check for all TTs on random basis and use atleast one TT Fire ext. | SOD | Marketing | ECZ | 2026-04-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122636 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122636 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122636 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122636 | AUD-2026-03-2000011313ACN-2026-03-4000122636 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Coordination between teams and mebers has improved through participation in mock drills regularly. Mock drills are conducted for different scenarios and all points are discussed after the drill. PA system is used by Chief incident controller to give commands and to ensure clear communication. SCBA is worn as per requirement and urgency of situation to ensure no delay in fire fighting. Person closer to incident site is mandatorily equipped with SCBA. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122633 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Location is falls under single contingency . Spillage scenerio created in mock drill on 11.3.26 | 2.2 | Double contingency scenario simulated; observations recorded | 1636 | BALASORE DEPOT | 1. improvement in action taken during spillage scenerio by the team 2. Usage of PA system during drill by leader | SOD | Marketing | ECZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | EMERGENCY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122633 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122633 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122633 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122633 | AUD-2026-03-2000011313ACN-2026-03-4000122633 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Project for Lux level improvement at Balasore IRD was completed and 8 octagonal poles with 150/200W FLP lights installed at critical points to ensure correct lux levels at all places. 400W lights installed at high masts. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122634 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Lux level is low behind TT gantry , secondary roads | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1636 | BALASORE DEPOT | already NPCB taken by location | SOD | Marketing | ECZ | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | ASSET INTEGRITY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122634 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122634 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122634 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122634 | AUD-2026-03-2000011313ACN-2026-03-4000122634 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Improvement in coordination between teams and members has been improved through planeed and surprise mock drills at depot. PA system is utilised during drills whenever required. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122635 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | The same was checked during sudden mock drill announced on 11.3.26 | 2.5 | Emergency response preparedness reviewed | 1636 | BALASORE DEPOT | Response was good from all teams , only some coordination issue and usage of PA system was witnessed | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | EMERGENCY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122635 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122635 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122635 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122635 | AUD-2026-03-2000011313ACN-2026-03-4000122635 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Regular gate meetings are being conducted with TT crew. All transporters have been advised in meetings to minimise deviations. No violations regarding power disconnection/VTS tampering are being generated (other than maintenance work with prior information). | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122638 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Deviation mostly related to night driving , speed voilation during return trip , route deviation , Devise tampering, etc found | 3.3 | VTS deviations reviewed | 1636 | BALASORE DEPOT | These VTS deviations to be discussed in transporter meet, gate meetings | SOD | Marketing | ECZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122638 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122638 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122638 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122638 | AUD-2026-03-2000011313ACN-2026-03-4000122638 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Information was given to all TPT/DCTs to ensure fire screen wherever applicable for the TTs. Currently all TTs have fire screen (for non cabin type TTs) and the same is strictly checked by security at IN Gate. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122644 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Few TTs found operating without fire screen or improper screen | 6.1 | Safety Fittings -TT | 1636 | BALASORE DEPOT | Advised location to immediately inform TPT/DCT to provide the same & give them 1 week time | SOD | Marketing | ECZ | 2026-03-31 | THIRD PARTY ERRORS | 4 | CONTRACTOR SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011313ACN-2026-03-4000122644 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122644 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122644 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122644 | AUD-2026-03-2000011313ACN-2026-03-4000122644 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | Coordination among all the teams hasbeen improved by participation in mock drills. All teams and its members have been clearly conveyed their roles and same is being followed. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122632 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Fire drill records reviewed for drill conducted in last 6 months | 2.1 | Fire drill conducted in last 6 months (surprise) | 1636 | BALASORE DEPOT | Improvement in mock drill discussed | SOD | Marketing | ECZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | EMERGENCY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122632 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122632 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122632 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122632 | AUD-2026-03-2000011313ACN-2026-03-4000122632 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-09 | SWADHA SHARAN NAYAK | 2026-08-09 | We have conducted refresher trainings and competency assessment. We have prepared training matrix for all officers. All officers have been trained for depot operations. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122629 | Closed | SWADHA SHARAN NAYAK | 2026-08-09 | Interaction done and junior officers Swadha & Ansari advised for decisiveness , energetic & enhancing tech. competency | 1.1 | Interaction with all officers (1–1.5 hrs) | 1636 | BALASORE DEPOT | These officers to enehance competencies in all depot operations | SOD | Marketing | ECZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122629 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122629 | 2026-09-26 17:30 | 23.0247 | 342 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122629 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122629 | AUD-2026-03-2000011313ACN-2026-03-4000122629 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
DEVA DHRUVA | 2026-08-10 |  |  | Location has arranged agreement scan copies of all DCT's from Belgaum and Bellary ROs and original agreement copy of TPTs. Also, all TPTs SD are accounted properly. Regular trainings of DCT & Transporters are conducted. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122785 | Closed | DEVA DHRUVA | 2026-08-10 | Interactive session held with 4 officers. NOVEX ITDG Module SOP and ticketing system was discussed in detail. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1800 | HUBLI DEPOT | Advised location to procure agreement copies of all transporters and DCT's from Belgaum and Bellary Ros and confirm that all SD areaccounted properly. Conduct trainings of DCT (Sales area vice ) & Transporters. | SOD | Marketing | SWZ | 2026-04-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011030ACN-2026-03-4000122785 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122785 | 2026-09-11 19:30 | 37.9413 | 343 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122785 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011030ACN-2026-03-4000122785 | AUD-2026-03-2000011030ACN-2026-03-4000122785 | 21 | 21 | 26 | 80 | 18 | 18 | 35 | 49
DEVA DHRUVA | 2026-08-10 |  |  | Three Security/ CWM/Officers has been identified who for handle HVD with HAZ License, who are having experience of HVD. | HUBLI_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-23 18:00 | AUD-2026-06-2000012499 | 2026-05-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138627 | Closed | DEVA DHRUVA | 2026-08-10 | Not Available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1800 | HUBLI DEPOT | LIC to identify and develop few Security/ CWM/Officers to handle HVD with HAZ License | SOD | Marketing | SWZ | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | EMERGENCY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000012499ACN-2026-06-4000138627 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012499ACN-2026-06-4000138627 | 2026-09-11 19:30 | 37.9413 | 343 | >20 | AUD-2026-06-2000012499 - ACN-2026-06-4000138627 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012499ACN-2026-06-4000138627 | AUD-2026-06-2000012499ACN-2026-06-4000138627 | 21 | 21 | 27 | 80 | 18 | 18 | 57 | 49
|  |  |  | Work is in progress for earthpit maintenance jobs. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-06-4000136344 | Open | MD KASHIF | 2026-08-10 | Electrical system: Earthpits 71, 72, 73, found with single clamp, single bolt connection and gap between clamp and strips. | 6.3 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer to ensure double bolts and clamps. Reduce the gap betweem clamp and strips. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136344 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136344 | 2026-09-19 10:00 | 30.3372 | 317 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136344 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012744ACN-2026-06-4000136344 |  | AUD-2026-06-2000012744ACN-2026-06-4000136344 | 21 |  | 27 | 80 | 1 | 1 | 46
|  | KAMLESH SAHU | 2026-08-10 | PTFG gland repalced | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130282 | Completed | KAMLESH SAHU | 2026-08-10 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . | 4.2 | Maintenance activities reviewed | 1528 | RAIPUR IRD-II | Old depot fire engines , mechanical seal to be provided as heavy water leakge found in 1-2 engines | SOD | Marketing | ECZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130282 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130282 | 2026-08-28 18:00 | 52.0038 | 302 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130282 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-05-2000012405ACN-2026-05-4000130282 |  | AUD-2026-05-2000012405ACN-2026-05-4000130282 | 21 |  | 27 | 80 | 3 | 3 | 44
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | New officers has been assigned to experienced officers for better training | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142607 | Closed | BHARTI YOGESH | 2026-08-10 | Interacted with all officers of the Location and enquired about their respective areas of operation & issue faced, if any. Shift officers advised to get familar with day in and out activities irrespective of profile being handled and resolution of minor operational issues locally in shift.Special emphasis given on new officers, guiding them how to learn, update, innovate & conduct themselves. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1183 | NALGARH DEPOT | Advised LIC to formally assign mentors to the new officers for their learning & development. | SOD | Marketing | NFZ | 2026-07-15 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-07-2000015564ACN-2026-07-4000142607 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142607 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142607 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142607 | AUD-2026-07-2000015564ACN-2026-07-4000142607 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | FE service has been carried out and TT FE are being checked randomly | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142611 | Closed | BHARTI YOGESH | 2026-08-10 | Not operated. Had safety talk with TT crew on importance of timely service of fire extingusihers and pros of healthy fire extinguishers. | 2.14 | TT crew fire extinguisher usage checked | 1183 | NALGARH DEPOT | Location to carry out inspection of FE of all TTs associated with depot. | SOD | Marketing | NFZ | 2026-07-30 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142611 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142611 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142611 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142611 | AUD-2026-07-2000015564ACN-2026-07-4000142611 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Common point. Observation included in 1.4 point | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142610 | Closed | BHARTI YOGESH | 2026-08-10 | Location is having 40 CCTVs and out of which 36 are working. Checked records of CCTV being analysed by Security. | 2.6 | CCTV functioning checked | 1183 | NALGARH DEPOT | Repair of camera to be expedited.Follow up with vendor to be maintained | SOD | Marketing | NFZ | 2026-07-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142610 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142610 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142610 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142610 | AUD-2026-07-2000015564ACN-2026-07-4000142610 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Loction is strictly following up with transporters and conversion of DCT TT is under way and after DCT TPT TTwill be converted | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142612 | Closed | BHARTI YOGESH | 2026-08-10 | Not checked during the visit. Precentage of top loading TTs is higher than bottom loading TT | 3.1 | TT fittings & discipline checked | 1183 | NALGARH DEPOT | Location to aggressible work on conversion of top loading TTs to bottom loading TTs | SOD | Marketing | NFZ | 2026-07-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142612 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142612 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142612 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142612 | AUD-2026-07-2000015564ACN-2026-07-4000142612 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Trees under HT cable has been choped off. | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142614 | Closed | BHARTI YOGESH | 2026-08-10 | Housekeeping to be improved. Vegetation found near sample room area & under HT cable passing over depot advised to remove. | 3.15 | Housekeeping & PPE usage checked | 1183 | NALGARH DEPOT | Location to maintain height of all trees in vicinity of HT cable | SOD | Marketing | NFZ | 2026-07-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142614 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142614 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142614 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142614 | AUD-2026-07-2000015564ACN-2026-07-4000142614 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Earthing has been provided to air compressor | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-07-4000142615 | Closed | BHARTI YOGESH | 2026-08-10 | Earth pit condition is checked and found in proper condition. Earthing not provided to air compressor | 3.16 | Earth pits / boundary / vegetation control checked | 1183 | NALGARH DEPOT | Location to provide earthing for air compressor | SOD | Marketing | NFZ | 2026-07-15 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-15 | AUD-2026-07-2000015564ACN-2026-07-4000142615 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142615 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142615 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142615 | AUD-2026-07-2000015564ACN-2026-07-4000142615 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
|  | CHANGMAI RAHUL | 2026-08-10 | We have readied F key road and used for proper tightening of the WCFM mointors and with the hose pipe through monitor the water throw reaching gantry. Additionally we are arranging Electrical centrifugal pump to install from Paradeep Terminal to improve the throw. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136988 | Completed | CHANGMAI RAHUL | 2026-08-10 | NA.Only UG Tank of 180KL is exist.Checked Usage of foam monitor.Throw is insufficient to reach Gantry area. | 2.2 | Double contingency scenario simulated; observations recorded | 1708 | DIMAPUR DEPOT | Advised location to keep ready F rods to operated the foam monitor valve properly.Advised to explore option for shifting any centrifugal electric Pump from other location and can be used to operate monitors during emergency. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136988 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136988 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136988 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136988 |  | AUD-2026-06-2000012955ACN-2026-06-4000136988 | 21 |  | 27 | 80 | 7 | 7 | 44
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Register of pump house has been maintained | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-07-4000142616 | Closed | BHARTI YOGESH | 2026-08-10 | Full field round of the Location done along with LIC. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1183 | NALGARH DEPOT | Location to maintain register of pump operation covering no. of hours operated. | SOD | Marketing | NFZ | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-15 | AUD-2026-07-2000015564ACN-2026-07-4000142616 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142616 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142616 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142616 | AUD-2026-07-2000015564ACN-2026-07-4000142616 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | All glands has been checked and gaps rectified | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142617 | Closed | BHARTI YOGESH | 2026-08-10 | Yes.High Mast tower cables are not properply dressed | 4.2 | Maintenance activities reviewed | 1183 | NALGARH DEPOT | Location to carry out survey of all glands of depot and take corrective action as required. | SOD | Marketing | NFZ | 2026-07-15 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-15 | AUD-2026-07-2000015564ACN-2026-07-4000142617 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142617 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142617 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142617 | AUD-2026-07-2000015564ACN-2026-07-4000142617 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Common point. Observation included in 1.4 point | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142618 | Closed | BHARTI YOGESH | 2026-08-10 | Scrap observed at Location, RFD of the same processed but disposal not done despite finalization of bidder in auction two times. Location is in process of getting the auction done again on the basis of lots to ensure disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1183 | NALGARH DEPOT | Actual disposal to be expedited. | SOD | Marketing | NFZ | 2026-07-30 | INADEQUATE SAFETY CULTURE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142618 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142618 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142618 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142618 | AUD-2026-07-2000015564ACN-2026-07-4000142618 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-10 | BHARTI YOGESH | 2026-08-10 | Grass cutting carried for whole location | LOCATION VISIT-NALAGARH_10-11.06.26 | 2026-06-11 | AUD-2026-07-2000015564 | 2026-06-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142619 | Closed | BHARTI YOGESH | 2026-08-10 | Not checked during the visit. | 6.4 | SAMPLE ROOM | 1183 | NALGARH DEPOT | Location to carryout timely grass cutting. Grass observed in underground tank area | SOD | Marketing | NFZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015564ACN-2026-07-4000142619 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015564ACN-2026-07-4000142619 | 2026-08-27 | 53.7538 | 343 | >20 | AUD-2026-07-2000015564 - ACN-2026-07-4000142619 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015564ACN-2026-07-4000142619 | AUD-2026-07-2000015564ACN-2026-07-4000142619 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 49
|  | CHANGMAI RAHUL | 2026-08-10 | We have readied F key road and used for proper tightening of the WCFM mointors to avoid the minor leakage and with the hose pipe through monitor the water throw reaching gantry. Additionally we are arranging Electrical centrifugal pump to install from Paradeep Terminal to improve the throw. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136994 | Completed | CHANGMAI RAHUL | 2026-08-10 | YES. The foam monitor throw are insufficient to reach Gantry even at 500 GPM with 2 jockey pump. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1708 | DIMAPUR DEPOT | Officer to monitor if any improvement can be done with current Fire fighting system.Minor leakages from other hydrant line to be arrested.Advised to explore option for shifting any centrifugal electric Pump from other location and can be used to operate monitors during emergency. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136994 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136994 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136994 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136994 |  | AUD-2026-06-2000012955ACN-2026-06-4000136994 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-08-10 | Book for eyesight/colour blindness test is procured and available | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136995 | Completed | CHANGMAI RAHUL | 2026-08-10 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1708 | DIMAPUR DEPOT | advised to procure the same urgently | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136995 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136995 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136995 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136995 |  | AUD-2026-06-2000012955ACN-2026-06-4000136995 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-08-10 | Yes. 1.Silcia gel replacement completed at both MS TK-1 and TK-2 2. BCU unit GI Cover to be done 3. T-stainer cleaning as per schedule done 4. Dismantaled BCU power cable removal done 5. Prover tank seal intactness is secured 6. Hydrant line support from ground is ensured with welding activities 7. MCC room door fixing done 8. Modification and valve installation in water tank receipt linefor outside Water tanker receipt provision is completed | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137152 | Completed | CHANGMAI RAHUL | 2026-08-10 | Yes. 1.Silcia gel needs replacement 2. BCU unit GI Cover to be done 3. T-stainer cleaning as per schedule 4. Dismantaled BCU power cable removal 5. Prover tank seal intactness to be secured 6. Hydrant line support from ground to be ensured 7. MCC room door fixingto be done 8. Modification and valve installation in water tank receipt line for outside Water tanker receipt provision | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1708 | DIMAPUR DEPOT | 1.Silcia gel replacement 2. BCU unit GI Cover 3. T-stainer cleaning 4. Dismantaled BCU power cable removal 5. Prover tank seal re-placement 6. Support for Hydrant line to be ensured 7. MCC room door fixing 8. Modification and valve installation in receipt line for outside Water TT receipt | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000137152 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137152 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137152 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137152 |  | AUD-2026-06-2000012955ACN-2026-06-4000137152 | 21 |  | 27 | 80 | 7 | 7 | 44
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-10 | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Training imparted to Security Personnel and rescue team for giving First Aid training to Injured person before moving it to Ambulance. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143372 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Last Fire Drill was conducted on 02-06-2026 16:02 hrs in front of JCIF at Dyke 1 Tank No 102. Scenario was Fire observed in delivery line at secondary valve of tank no 102 having product solvent 3275. On duty M & R personnel observed fire at secondary valve resulting from leakage of product. | 2.1 | Fire drill conducted in last 6 months (surprise) | 3708 | VISAKH NBOT | Following area of improvement observed during the mock fire drill, i.e., first aid treatment to be given to injurued person immediately before moving the person to ambulance to be complied. | SOD | Marketing | SCR | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015047ACN-2026-07-4000143372 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143372 | 2026-09-18 17:30 | 31.0247 | 343 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143372 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143372 | AUD-2026-07-2000015047ACN-2026-07-4000143372 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 49
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-10 | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Training given to TT crew to handle road side emergency situation .Daily gate meeting is being conducted and same is being explained to all TT crew. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143380 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-09 | TT crew roadside emergency procedures checked | 2.15 | TT crew roadside emergency procedures checked | 3708 | VISAKH NBOT | Training to be given to TT crew roadside emergency procedures by all officers/transporters | SOD | Marketing | SCR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143380 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143380 | 2026-09-18 17:30 | 31.0247 | 343 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143380 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143380 | AUD-2026-07-2000015047ACN-2026-07-4000143380 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 49
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-10 | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Training conducted to all stake holders on shortcoming observed during previous mock drill | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143373 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Double contingency scenario not applicable for VNBOT. Single contingency mock drill are conducted conducted | 2.2 | Double contingency scenario simulated; observations recorded | 3708 | VISAKH NBOT | All shortcomings in previous mock drills to be complied | SOD | Marketing | SCR | 2026-07-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | EMERGENCY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015047ACN-2026-07-4000143373 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143373 | 2026-09-18 17:30 | 31.0247 | 343 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143373 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143373 | AUD-2026-07-2000015047ACN-2026-07-4000143373 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 49
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-10 | DIWAKAR KAMLESH KUMAR | 2026-08-09 | Fire engine display of all 3 engine made functional. Electrical rubber gloves and tester made available | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143376 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-09 | 1. Operated two Foam monitors and found ok & checked performance of fire extinguishers & jockey pumps. 2. Checked Emergency kit trollley and found: 1. Electrical rubber gloves testing not valid 2. Eletrical Tester not available | 2.5 | Emergency response preparedness reviewed | 3708 | VISAKH NBOT | 1. Fire engine display of all three fire engines not working to be made functional. 2. Electrical rubber gloves with valid testingto be made available & Eletrical Tester to be made available | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143376 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143376 | 2026-09-18 17:30 | 31.0247 | 343 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143376 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015047ACN-2026-07-4000143376 | AUD-2026-07-2000015047ACN-2026-07-4000143376 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 49
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-10 | DIWAKAR KAMLESH KUMAR | 2026-08-09 | VA alerts are being monitored and are closed on daily basis. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143378 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-09 | VA alerts checked on random basis | 2.7 | VA alerts checked / analysed | 3708 | VISAKH NBOT | VA alerts to be reviewed and closed on daily basis | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143378 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143378 | 2026-09-18 17:30 | 31.0247 | 343 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143378 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143378 | AUD-2026-07-2000015047ACN-2026-07-4000143378 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | a. TT cycle time is improved from 44 min to 42 min. b. Annexure-1 of the VTS circular being maintained and all TTs are covered under VTS. Monthly checks for VTS functionality and EM locking being carried out and proper records maintained. c. TT Gantry Officer is focusing on improving efficiency of the gantry | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.10 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000126978 | Closed | FOUZDAR RISHABH | 2026-08-10 | a. TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlier VC's with all Location TAS officer. To expedite AMC PO placement. b. Transportation - Maintaining Annex-1 of VTS circular and ensuring thgat all TT's are covered for VTS and EM locking check on monthly baisis with record | 1.1000000000000001 | Improvement plans discussed | 1155 | ROORKEE DEPOT | a. The TAS Officer should focus on improving TT exit time and LPM at the location b. Annexure-1 of the VTS circular to be maintained and ensure that all TTs are covered under VTS. Monthly checks for VTS functionality and EM locking should be carried out and proper records maintained. c. The TT Gantry Officer should take necessary steps to improve the LPM at the gantry to enhance operational efficiency. | SOD | Marketing | NUZ | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126978 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126978 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126978 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126978 | AUD-2026-03-2000011028ACN-2026-03-4000126978 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Requirement of ETP for location is not required at location as sufficient capacity OWS are present at location. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000126977 | Closed | FOUZDAR RISHABH | 2026-08-10 | 3 ETP not avialable at location | 1.5 | Pending issues reviewed | 1155 | ROORKEE DEPOT | Budget for ETP at Roorkee to be sought | SOD | Marketing | NUZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126977 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126977 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126977 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126977 | AUD-2026-03-2000011028ACN-2026-03-4000126977 | 21 | 21 | 26 | 80 | 2 | 2 | 44 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Training on points observed given to all members Tyre of MFU repaired | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126979 | Closed | FOUZDAR RISHABH | 2026-06-20 | Reviwe of Mock drill conducted on 29/01/2026 at 1520 hours with scenerio considering Lakage from Manhole of U/G tank no-03 due to over fill. Following observation were observed during the drill a) All equipment unes during the fire drill worked well b) Team coordination was good c) Team performed well as per the directionof CIC | 2.1 | Fire drill conducted in last 6 months (surprise) | 1155 | ROORKEE DEPOT | a) Some members was gathering at a single location instead of spreading to fire fighting equipment as per FOC b) Communications between the team should be continuous and clear c) Tyre of Mobile Foam Unit broke down during the drill | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126979 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126979 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126979 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126979 | AUD-2026-03-2000011028ACN-2026-03-4000126979 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | (a) Security team instructed to ensure proper setting of clock and is being followed in all drills. (b) FOC updated as per observations made during the Fire drill (c),(d) & (e) Training of equipment given to all members of the team on 18th Apr 26 | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126980 | Closed | FOUZDAR RISHABH | 2026-08-10 | The location is a single contingency facility. Off-shift mock drill was conducted on 17/03/2026 and on-shift mock drill on 18/03/2026. During both drills, all firefighting equipment was found to be in good working condition, and personnel including security guards, contract workmen, and officers were generally familiar with the operation of equipment such as Foam Monitor, MEFG, HVLR, and fire extinguishers. However, the following gaps were observed: a) Fire clock was not set by the security guard during the off-shift drill. b) Roles and responsibilities are not clearly defined/updated in the Fire Organization CHart (FOC). c) Foam monitor discharge (throw) was not effectively regulated as per required distance. d) Contract workmen require improved control over foam monitor operation, particularly considering the high discharge capacity (1000 GPM) in a relatively small location. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1155 | ROORKEE DEPOT | a) Ensure strict adherence to emergency response protocols, including timely setting of the fire clock during drills and actual emergencies. b) Review and update the Fire Organization Chart (FOC) to clearly define roles and responsibilities for all personnel. c) Conduct focused training to improve operational control of foam monitors, including proper adjustment of throw distance. d) Impart regular refresher training to contract workmen and security personnel to enhance competency in handling high-capacity firefightingequipment. e) Periodically monitor and evaluate drill performance to ensure continuous improvement in emergency preparedness. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126980 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126980 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126980 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126980 | AUD-2026-03-2000011028ACN-2026-03-4000126980 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | CCTVs have been repaired and are online | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126982 | Closed | FOUZDAR RISHABH | 2026-06-20 | Tot. 40 no of CCTV's are available at the location. 36 nos of CCTV's are working and 04 nos of CCTV's are found to be not working since 16/03/2026. Also 92 days CCTV recording is available. Recording Checked for 18/12/2025 from 1000 am - 1100 am | 2.6 | CCTV functioning checked | 1155 | ROORKEE DEPOT | 100% uptime of CCTV's to be ensured. It is recommended to repair or replace the non-operational cameras at the earliest to ensure complete surveillance coverage. | SOD | Marketing | NUZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126982 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126982 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126982 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126982 | AUD-2026-03-2000011028ACN-2026-03-4000126982 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | CCTVs have been repaired and are online | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126983 | Closed | FOUZDAR RISHABH | 2026-06-20 | A total of 35 CCTVs are integrated with the VA system. As verified on 18/03/2026, 4 nos of CCTV's camera associated with VA system are non operational. Additionally, records for the past three months were checked for VA alerts and no alerts were pending for acknowledgement or closure. | 2.7 | VA alerts checked / analysed | 1155 | ROORKEE DEPOT | Ensure 100% compliance towards closing all VA Alerts in NOVEX, with proper documentation of the root cause for each alert. Also, Itis recommended to repair or replace the non-operational cameras at the earliest to ensure 100% surveillance coverage. | SOD | Marketing | NUZ | 2026-05-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-31 | AUD-2026-03-2000011028ACN-2026-03-4000126983 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126983 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126983 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126983 | AUD-2026-03-2000011028ACN-2026-03-4000126983 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | NCs have been closed by the DCT | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126984 | Closed | FOUZDAR RISHABH | 2026-06-20 | Part B Check was done on DCT UK07 CB7586 of M/s Saket Filling on 18/03/2026. Following Observations were recorded: a) Bottom loading fitting certificate was not available b) Push rod was not provided on Valve Box Cover c) Primary protection was not available on exhaust, However secondary protection was available d) Fire Extinguisher servicing certificate was not available | 3.1 | TT fittings & discipline checked | 1155 | ROORKEE DEPOT | NC to be closed | SOD | Marketing | NUZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011028ACN-2026-03-4000126984 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126984 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126984 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126984 | AUD-2026-03-2000011028ACN-2026-03-4000126984 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | 1. Truck is under observation 2.Dip elimination filenote has been approved | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126985 | Closed | FOUZDAR RISHABH | 2026-06-20 | Post loading dip checks were performed on four TTs during the visit- its findings were shared with the location. Out of the four TTs checked during the visit, Chamber 3 of TT# UK16CA0888 loaded at Bay No. 4 on 18.03.2026 was found having 4mm excess and 10L was manually removed from the chamber. Location is in the process for submitting proposal for 100% dip elimination, in line with the HQO circular. | 3.2 | Post-loading dip checks verified | 1155 | ROORKEE DEPOT | 1. Location to monitor the TT no. UK16CA0888 for any future variations observed and take corrective action like re-calibration, if required. 2. Location to submit the dip elimination file note latest at the earliest, with all relevant annexures duly verified by LIC. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126985 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126985 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126985 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126985 | AUD-2026-03-2000011028ACN-2026-03-4000126985 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Abnormal variations are marked and reasons are noted | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126986 | Closed | FOUZDAR RISHABH | 2026-06-20 | There are only 7 instances of abnormal variations during the period 1st Oct'25 to 18th Mar'26. Reason for abnormal gain/ loss foundentered in SAP for one instance. | 3.9 | Abnormal variations / unused assets reviewed | 1155 | ROORKEE DEPOT | Location to take necessary precautions in future to avoid instances of abnormal variation (gain/ loss). | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126986 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126986 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126986 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126986 | AUD-2026-03-2000011028ACN-2026-03-4000126986 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | analysis of ethanol blending in the day end report is being done. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126987 | Closed | FOUZDAR RISHABH | 2026-06-20 | Dispatches as per MFM totalizer difference and BCU totalizer difference is being compared by the location on daily basis and printouts with signature of TAS officer, Planning Officer as well as LIC. However, location is not recording the analysis of ethanol blending in the day end report. | 3.11 | MFM vs BCU totalizer comparison checked | 1155 | ROORKEE DEPOT | Location to record analysis of ethanol blending in the day end report so that blending percentage can be cross-verified with the physical observations made about ethanol blending in MS. | SOD | Marketing | NUZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126987 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126987 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126987 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126987 | AUD-2026-03-2000011028ACN-2026-03-4000126987 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Excess vegetation at the site has been cleared and housekeeping is being maintained. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126988 | Closed | FOUZDAR RISHABH | 2026-06-20 | Housekeeping - Housekeeping of the location is found to be Good with some areas requireing minor upkeep which were discussed duringfield round with location team. | 3.15 | Housekeeping & PPE usage checked | 1155 | ROORKEE DEPOT | Excess vegetation at the site should be cleared, as discussed during the field round | SOD | Marketing | NUZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126988 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126988 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126988 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126988 | AUD-2026-03-2000011028ACN-2026-03-4000126988 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | CWP and permit are linked with copy attached with the permit. Isolation pemrit during earthpit testing of transformer and other heavy electrical devices are being maintained henceforth | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126989 | Closed | FOUZDAR RISHABH | 2026-08-10 | Earth Pits - Total 114 Nos of Earth pits are there at the location. Earth Pit No 02 & 27 Checked and Found Individual and Grid Reading as mentioned Individual Reading of EP 02 - 1.69 Ω Grid Reading of EP-02 - 0.11 Ω Individual Reading of EP 27 - 1.5 Ω GridReading of EP-27 - 0.14 Ω While revieweing the work permit it is observed that location has not taken Electrical Isolation / energization permit for earthpits connected to Electical equipment. | 3.16 | Earth pits / boundary / vegetation control checked | 1155 | ROORKEE DEPOT | A separate Electrical Isolation/Energization Permit shall be obtained while carrying out half-yearly checks of earth pits connectedto electrical equipment. The CWP and the Electrical Isolation/Energization Permit shall also be properly linked. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126989 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126989 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126989 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126989 | AUD-2026-03-2000011028ACN-2026-03-4000126989 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Repair of concertina coil is done. Parameter integrity checking is done periodically. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126990 | Closed | JAIN PRAKALP | 2026-08-01 | Boundary Wall - The boundary wall was found to be in good condition. The concertina coil installed along the periphery is generallyintact; however, damage was observed at two locations near the transformer yard and the car parking area. Provision of broken glasstopping on the boundary wall is also found intact which is used as an additional security measure to deter unauthorized entry. | 3.16 | Earth pits / boundary / vegetation control checked | 1155 | ROORKEE DEPOT | Repair and restore the damaged sections of the concertina coil on priority to maintain perimeter security integrity. Conduct periodic inspections of all boundary protection measures, including concertina coils and glass topping, to ensure continued effectiveness against unauthorized entry. | SOD | Marketing | NUZ | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126990 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126990 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126990 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126990 | AUD-2026-03-2000011028ACN-2026-03-4000126990 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | MOC are closed in time bound manner | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126991 | Closed | FOUZDAR RISHABH | 2026-06-20 | During FY 2025-26, Total 12 Nos of MoC's were raised and 11 MoC's were approved and closed. Only One MOC is under process for MS tanks defloating.. | 3.17 | MOC status reviewed | 1155 | ROORKEE DEPOT | MOC to be approved and closer of the same in time bound manner | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126991 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126991 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126991 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126991 | AUD-2026-03-2000011028ACN-2026-03-4000126991 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | All support have been made only point contact | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126994 | Closed | FOUZDAR RISHABH | 2026-06-20 | At various points it has been observed that Hydrant line are directly lying on the support structure. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | The pipe support shall have only point contact. | SOD | Marketing | NUZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-31 | AUD-2026-03-2000011028ACN-2026-03-4000126994 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126994 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126994 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126994 | AUD-2026-03-2000011028ACN-2026-03-4000126994 | 21 | 21 | 26 | 80 | 2 | 2 | 48 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Leakage has been arrested, removal and disposal of soil is done | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126995 | Closed | FOUZDAR RISHABH | 2026-06-20 | Leakage observed in Bay-01 across filters and soil soaked with HSD observed. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Attend and rectify the leakage on priority. Remove contaminated soil and dispose of it as per environmental guidelines. Strengthen inspection practices to prevent product loss and environmental hazards. | SOD | Marketing | NUZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011028ACN-2026-03-4000126995 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126995 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126995 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126995 | AUD-2026-03-2000011028ACN-2026-03-4000126995 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Leakage has been arrested | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126997 | Closed | FOUZDAR RISHABH | 2026-06-20 | Leakage was observed in Bay -02 from Swivel Joint of loading arm. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Immediate rectification of the swivel joint leakage is required. Implement routine inspection and maintenance of loading arms to prevent recurrence and ensure safe operations. | SOD | Marketing | NUZ | 2026-05-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-31 | AUD-2026-03-2000011028ACN-2026-03-4000126997 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126997 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126997 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126997 | AUD-2026-03-2000011028ACN-2026-03-4000126997 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | All dates are updated | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126996 | Closed | FOUZDAR RISHABH | 2026-06-20 | Preventive Maintenance (PM) of filters/strainers has been carried out and reports were verified. However, the testing date and nextdue date are not updated at the field level. Last maintenance was carried on 22/02/2026 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Ensure that all filters/strainers are clearly tagged/displayed with the last testing date and next due date at site for effective monitoring and timely maintenance compliance. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126996 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126996 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126996 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126996 | AUD-2026-03-2000011028ACN-2026-03-4000126996 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Termination has been properly addressed | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126998 | Closed | FOUZDAR RISHABH | 2026-06-20 | The OWS motor installed near the TT Gantry is earthed; however, the earthing termination at the motor is not distinctly identifiable. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Ensure proper and clearly identifiable earthing termination at the motor. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126998 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126998 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126998 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126998 | AUD-2026-03-2000011028ACN-2026-03-4000126998 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Jumpers across product pipelines are ensured. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000126999 | Closed | FOUZDAR RISHABH | 2026-06-20 | At many places it has been observed that Jumpers are missing across flanges. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Jumpers to be placed across each flange joints immediately | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126999 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126999 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126999 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126999 | AUD-2026-03-2000011028ACN-2026-03-4000126999 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Double bolting done. Nil repetetion will be ensured. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127350 | Closed | JAIN PRAKALP | 2026-08-01 | Grouting structural footings of Power/Turbo dye shed is done with single bolt. Double-bolt systems is a standard procedure to ensure rigid, secure, and level connections between steel columns and concrete foundations. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Modify the existing grouting arrangement of structural footings in the Power/Turbo Dyke Shed by replacing the single-bolt system with a standard double-bolt configuration. Additionally, conduct a structural review of all similar installations to ensure compliancewith standard engineering practices. | SOD | Marketing | NUZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000127350 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127350 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127350 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127350 | AUD-2026-03-2000011028ACN-2026-03-4000127350 | 21 | 21 | 26 | 80 | 2 | 2 | 48 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Equipment has been blinded | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127351 | Closed | FOUZDAR RISHABH | 2026-06-20 | Open flange ends were observed in Additionally provided Dye pump which is not utilized. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | All open ends to be blinded, if equipment is not in use | SOD | Marketing | NUZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011028ACN-2026-03-4000127351 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127351 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127351 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127351 | AUD-2026-03-2000011028ACN-2026-03-4000127351 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Missing bolts provided | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127352 | Closed | FOUZDAR RISHABH | 2026-06-20 | In product pump house 2 bolts are missing across filter flange of MS motor-3 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Missing bolts to be provided across filter flange | SOD | Marketing | NUZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000127352 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127352 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127352 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127352 | AUD-2026-03-2000011028ACN-2026-03-4000127352 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Serial no of HCDs and Smoke detectors done | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127353 | Closed | FOUZDAR RISHABH | 2026-08-10 | Serial Numbering of all field equipment is to be done along with smoke detectors installed in admin building and control room building | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Serial Numbering to be provided and record to be maintained accordingly | SOD | Marketing | NUZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-08-30 | AUD-2026-03-2000011028ACN-2026-03-4000127353 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127353 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127353 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127353 | AUD-2026-03-2000011028ACN-2026-03-4000127353 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Vegetation cleared from OWS | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127354 | Closed | FOUZDAR RISHABH | 2026-06-20 | Collection chamber of OWS is found to be dry, however vegetation was found inside the chamber. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Vegetation to be removed from OWS chamber | SOD | Marketing | NUZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011028ACN-2026-03-4000127354 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127354 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127354 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127354 | AUD-2026-03-2000011028ACN-2026-03-4000127354 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Cover placed on the drain ASAP | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127355 | Closed | FOUZDAR RISHABH | 2026-06-20 | The walkway near the Tank Farm within the licensed area is in an unsafe condition, with an adjacent open drain posing a risk of personnel falling. The drain is not adequately covered at the entry, creating a potential safety hazard. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Drain cover to be provided immediately | SOD | Marketing | NUZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011028ACN-2026-03-4000127355 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127355 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127355 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127355 | AUD-2026-03-2000011028ACN-2026-03-4000127355 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | As discussed during the audit, lock has been shifted towards the non-hazardous area and breakable seal placed, with record of opening | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127356 | Closed | FOUZDAR RISHABH | 2026-06-20 | Wicked gate provided near TK-11/12 should be kept locked as it defeats the purpose of having demarcation of Licence and delicenced area | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Lock and key arrangement to be made available for wicked gate | SOD | Marketing | NUZ | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-30 | AUD-2026-03-2000011028ACN-2026-03-4000127356 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127356 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127356 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127356 | AUD-2026-03-2000011028ACN-2026-03-4000127356 | 21 | 21 | 26 | 80 | 2 | 2 | 30 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Handrail provided | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127357 | Closed | FOUZDAR RISHABH | 2026-08-10 | Hand rail to be provided for the monkey ladder placed behind Admin Building | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Hand rail to be provided | SOD | Marketing | NUZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000127357 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127357 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127357 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127357 | AUD-2026-03-2000011028ACN-2026-03-4000127357 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 49
MEENA HEMANT KUMAR | 2026-08-10 |  |  | One additional light has been provided | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138490 | Closed | MEENA HEMANT KUMAR | 2026-08-10 | Checked. Lux level was meeting in all areas except ETP. Reading observed is as below: Road near TLF gantry: 65 agnst 20 Back sideof TLF Gantry: 62 agnst 20 Main road: 31 agnst 20 TLF entry and Exit: 61 and 57 agnst 20 TK1 manifold area: 69 agnst 60 TK2 manifold area: 87 agnst 60 TK20: 49 agnst 60 Water tank TK10: 72 agnst 60 PPH: 127 agnst 100 ETP: 32 agnst 60 FWPH: 400 agnst 100 VRU: 122 agnst 100 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1233 | BHARATPUR TERMINAL | Pls ensure required lux level at ETP also | SOD | Marketing | NWF | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-31 | AUD-2026-06-2000013164ACN-2026-06-4000138490 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138490 | 2026-09-16 17:45 | 33.0143 | 343 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138490 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138490 | AUD-2026-06-2000013164ACN-2026-06-4000138490 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 49
MEENA HEMANT KUMAR | 2026-08-10 |  |  | Float type valve is available on daughter tanks | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122706 | Closed | MEENA HEMANT KUMAR | 2026-08-10 | Float system in HVLR foam tanks to be implemented | 6.5 | Handling emergency | 1233 | BHARATPUR TERMINAL | 2 inch valve on foam line leading to daughter tank of HVLR tank, needs to be kept in open condition. Pls ensure float system | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011210ACN-2026-03-4000122706 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122706 | 2026-09-16 17:45 | 33.0143 | 343 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122706 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122706 | AUD-2026-03-2000011210ACN-2026-03-4000122706 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 49
MEENA HEMANT KUMAR | 2026-08-10 |  |  | Tender for rim seal has been floated | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122543 | Closed | MEENA HEMANT KUMAR | 2026-08-10 | 1. RIM seal of TK17 & 18 was checked, TK17 couldn’t be operated from control room and TK18 during discharge one module didn’t discharge. Location has been instructed to resolve the issue immediately. 2. HVLR number 2 & 7 were operated and found operating properly 3. Foam pourer of Largest TK-17 was checked and found ok. 4. Sprinkler of TK-6 was checked and found working ok. 5. Foam trolley, 3 foam monitors, and DCP’s operated during fire drill and worked fine. 6. MEFG of Dyke-3 was checked and found working ok. 7. Point type and open path HCD of TLF pump house checked and found ok | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1233 | BHARATPUR TERMINAL | RIM seal to be attended immediately | SOD | Marketing | NWF | 2026-03-05 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-05 | AUD-2026-03-2000011210ACN-2026-03-4000122543 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122543 | 2026-09-16 17:45 | 33.0143 | 343 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122543 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122543 | AUD-2026-03-2000011210ACN-2026-03-4000122543 | 21 | 21 | 26 | 80 | 2 | 1 | 27 | 49
KOSHLENDRA SINGH YADAV | 2026-08-10 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_27-29.05.26 | 2026-05-29 | AUD-2026-07-2000016451 | 2026-05-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146509 | Closed |  |  | Pending issue related to Budget, proposal , Shifting ot Nalagarh bridging reviewd | 1.3 | Pending issues reviewed | 1180 | SANGRUR DEPOT | XX | SOD | Marketing | NFZ | 2026-06-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 2 | EMERGENCY | S2 | F1 | 2026-06-15 | AUD-2026-07-2000016451ACN-2026-07-4000146509 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016451ACN-2026-07-4000146509 | 2026-07-17 | 94.7538 | 343 | >20 | AUD-2026-07-2000016451 - ACN-2026-07-4000146509 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016451ACN-2026-07-4000146509 | AUD-2026-07-2000016451ACN-2026-07-4000146509 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 49
KOSHLENDRA SINGH YADAV | 2026-08-10 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_27-29.05.26 | 2026-05-29 | AUD-2026-07-2000016451 | 2026-05-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146510 | Closed |  |  | Barrier for Calibration TT movement to be done on emergency route. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1180 | SANGRUR DEPOT | Corrective action to be taken. | SOD | Marketing | NFZ | 2026-06-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-15 | AUD-2026-07-2000016451ACN-2026-07-4000146510 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016451ACN-2026-07-4000146510 | 2026-07-17 | 94.7538 | 343 | >20 | AUD-2026-07-2000016451 - ACN-2026-07-4000146510 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016451ACN-2026-07-4000146510 | AUD-2026-07-2000016451ACN-2026-07-4000146510 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 49
KOSHLENDRA SINGH YADAV | 2026-08-10 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_27-29.05.26 | 2026-05-29 | AUD-2026-07-2000016451 | 2026-05-27 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146512 | Closed |  |  | Scrap observed at Location & found it to be already in the process of disposal. 1) Possibility of shifting Old DGs to Noida/Bhatinda housing to be explored. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1180 | SANGRUR DEPOT | Physical disposal to be expedited | SOD | Marketing | NFZ | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000016451ACN-2026-07-4000146512 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016451ACN-2026-07-4000146512 | 2026-07-17 | 94.7538 | 343 | >20 | AUD-2026-07-2000016451 - ACN-2026-07-4000146512 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000016451ACN-2026-07-4000146512 | AUD-2026-07-2000016451ACN-2026-07-4000146512 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 49
KOSHLENDRA SINGH YADAV | 2026-08-10 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_15-17.07.26 | 2026-07-17 | AUD-2026-08-2000016412 | 2026-07-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147001 | Closed |  |  | Lux level found less at TK05,TK03,TK21 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1180 | SANGRUR DEPOT | Corrective action to be taken. | SOD | Marketing | NFZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-31 | AUD-2026-08-2000016412ACN-2026-08-4000147001 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016412ACN-2026-08-4000147001 | 2026-07-17 | 94.7538 | 343 | >20 | AUD-2026-08-2000016412 - ACN-2026-08-4000147001 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016412ACN-2026-08-4000147001 | AUD-2026-08-2000016412ACN-2026-08-4000147001 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 49
KOSHLENDRA SINGH YADAV | 2026-08-10 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_15-17.07.26 | 2026-07-17 | AUD-2026-08-2000016412 | 2026-07-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147002 | Closed |  |  | Scrap observed at Location & found it to be already in the process of disposal. 1) Possibility of shifting Old DGs to Noida/Bhatinda housing to be explored. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1180 | SANGRUR DEPOT | Physical disposal to be expedited | SOD | Marketing | NFZ | 2026-08-31 | FATIGUE AND STRESS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-08-31 | AUD-2026-08-2000016412ACN-2026-08-4000147002 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016412ACN-2026-08-4000147002 | 2026-07-17 | 94.7538 | 343 | >20 | AUD-2026-08-2000016412 - ACN-2026-08-4000147002 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016412ACN-2026-08-4000147002 | AUD-2026-08-2000016412ACN-2026-08-4000147002 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Valuation shall be taken and RFD will be initiated Point is similar to point - 4.5 and open. Hence, complied. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000126975 | Closed | FOUZDAR RISHABH | 2026-08-10 | 1. e-scrap lying in warehouse | 1.3 | Pending issues reviewed | 1155 | ROORKEE DEPOT | 1. RFD for e-scrap placed in warehouse to be initiated and expedited. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126975 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126975 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126975 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126975 | AUD-2026-03-2000011028ACN-2026-03-4000126975 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Location has approached SIDCUL for land and Proposal has been sent to ECM for Approval. Point is already pending in ESA and MDSA and is repeating point. Hence, point is being closed to being repeating in nature. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000126976 | Closed | FOUZDAR RISHABH | 2026-08-10 | 2. TT Parking not avialable at location | 1.4 | Pending issues reviewed | 1155 | ROORKEE DEPOT | Fresh Tendering for TT parking land to be done and to take up with BPCL for utilising their vacant land | SOD | Marketing | NUZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-03-2000011028ACN-2026-03-4000126976 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126976 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126976 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126976 | AUD-2026-03-2000011028ACN-2026-03-4000126976 | 21 | 21 | 26 | 80 | 2 | 2 | 44 | 49
MANOJ KUMAR | 2026-08-10 |  |  | Pending points are being taken up with utmost seriousness for closure. Pending points are in process of compliance and is being taken with utmost seriousness. Point is already pending in SSA and MDSA and is repeating point. Hence, point is being closed due to it being repeating in nature. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126992 | Closed | FOUZDAR RISHABH | 2026-08-10 | MDSA - Last MDSA/Comprehensive audit was conducted from 29th July to 1st Aug 2025. Total observations were 132, out of which 128 observations were complied and remaining 4 pening points to be complied in time bound manner. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1155 | ROORKEE DEPOT | Compliance report of complied points to be shared with Zonal HSE for review and remaining points to be complied in time bound manner | SOD | Marketing | NUZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-12-31 | AUD-2026-03-2000011028ACN-2026-03-4000126992 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126992 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126992 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126992 | AUD-2026-03-2000011028ACN-2026-03-4000126992 | 21 | 21 | 26 | 80 | 2 | 2 | 70 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-08-10 | Pending points are being taken up with utmost seriousness for closure Pending points are in process of compliance and is being taken with utmost seriousness. Point is already pending in ESA and MDSA and is repeating point. Hence, point is being closed due to itbeing repeating in nature. | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000126993 | Closed | FOUZDAR RISHABH | 2026-08-10 | SSA - Last SSA was conducted from 06th to 09th Sep 2025. Total observation is 64, out of which 62 observations were complied and remaining 2 pending points to be complied in time bound manner. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1155 | ROORKEE DEPOT | Compliance report of complied points to be shared with Zonal HSE for review and remaining points to be complied in time bound manner. | SOD | Marketing | NUZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-12-31 | AUD-2026-03-2000011028ACN-2026-03-4000126993 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126993 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126993 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126993 | AUD-2026-03-2000011028ACN-2026-03-4000126993 | 21 | 21 | 26 | 80 | 2 | 2 | 70 | 49
MANOJ KUMAR | 2026-08-10 | FOUZDAR RISHABH | 2026-06-20 | Monthly Night inspections carried out as per advised and records maintained | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000126981 | Closed | FOUZDAR RISHABH | 2026-06-20 | Surprise visit was done at terminal around 22:35 hours of 17/03/2026 and fould all security guards in alert position. Security shift was headed by Head guard Sh Mahesh Chandra Joshi along with Guards Chandan Singh and Sanjeev Kumar. Although, location officer updated that Night SUrprise inspection is being done but no record pertaining to same was found at the main gate records. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1155 | ROORKEE DEPOT | Location to perform surprise night inspections and ensure that records of officers’ visits are maintained through proper entries inthe Entry Gate register. | SOD | Marketing | NUZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011028ACN-2026-03-4000126981 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000126981 | 2026-09-03 | 46.7538 | 343 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000126981 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000126981 | AUD-2026-03-2000011028ACN-2026-03-4000126981 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-08-08 | EM lock installation for FO trucks is being taken up and the installation and commissioning of the EM Lock system is under progress. KMS box installation completed. EM locks and keys distribution to the customer under progress. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130110 | Closed | SRIJIN S | 2026-08-08 | Non automated location. EM Locks not available for FO trucks. RPO trucks are locked using Srerna locks. | 3.5 | EM Lock SOP compliance verified | 1833 | COCHIN BLACK TERMINAL | Location to explore possibility for EM locks for FO TTs and revert by May 2026 | SOD | Marketing | CZR | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-30 | AUD-2026-05-2000012202ACN-2026-05-4000130110 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130110 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130110 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130110 | AUD-2026-05-2000012202ACN-2026-05-4000130110 | 21 | 21 | 27 | 80 | 2 | 0 | 48 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-08-08 | manual readings and TFMS parameters are being recorded. stabiliztaion of the TFMS system is being carried out on continuous basis and under progress. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130111 | Closed | SRIJIN S | 2026-08-08 | Manual gauging carried out for TK302 and TK-303 and the readings are found matching.However, for tk307, primary radar gauge reading needs be be corrected and density meter readings for H301 and H302 also needs to be corrected. | 3.7 | Inventory physical dip of minimum two tanks taken | 1833 | COCHIN BLACK TERMINAL | To monitor and maintain records of manual and TFMS parameters and take steps for stabiliztaion of the TFMS system | SOD | Marketing | CZR | 2026-06-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-05-2000012202ACN-2026-05-4000130111 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130111 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130111 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130111 | AUD-2026-05-2000012202ACN-2026-05-4000130111 | 21 | 21 | 27 | 80 | 2 | 0 | 44 | 49
TILKAN RAVINDRA KUMAR | 2026-08-10 | Sreelal P P | 2026-08-10 | Location has initiated reapir works in MEB. Budget not required | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125836 | Closed | Sreelal P P | 2026-08-10 | Budget for civil repairs identified for the compound wall needs funds. | 1.5 | HQO / Zonal support required identified | 1845 | IRUMPANAM TERMINAL | Budget requirement to be submitted | SOD | Marketing | CZR | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 8 | ASSET INTEGRITY | S4 | F2 | 2026-04-30 | AUD-2026-03-2000011133ACN-2026-03-4000125836 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125836 | 2026-09-02 16:30 | 47.0663 | 343 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125836 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125836 | AUD-2026-03-2000011133ACN-2026-03-4000125836 | 21 | 21 | 26 | 80 | 1 | -4 | 35 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-07-08 | Details are being shared with zone. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125846 | Closed | SRIJIN S | 2026-04-21 | Interacted with officers. concerns regarding operations and safety issues persisting at the location discussed.Location needs one no E0 officers in place of retiring employee. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1833 | COCHIN BLACK TERMINAL | Manpower details including retiring officer details to be shared with zone | SOD | Marketing | CZR | 2026-03-31 | POOR COMMUNICATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125846 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125846 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125846 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011134ACN-2026-03-4000125846 | AUD-2026-03-2000011134ACN-2026-03-4000125846 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-08-08 | HMV license available with 2 security guards. In case of emergency and none of the TT drivers are available, the security guards may operate the TT to a safe position. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125853 | Closed | SRIJIN S | 2026-08-08 | Not available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1833 | COCHIN BLACK TERMINAL | Security to be trained with HVD/HZA endorsement | SOD | Marketing | CZR | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 6 | EMERGENCY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125853 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125853 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125853 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125853 | AUD-2026-03-2000011134ACN-2026-03-4000125853 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-08-08 | meeting with transporters conducted | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125860 | Closed | SRIJIN S | 2026-08-08 | Location has conducted meeting with factory inspector on 04-12-2025. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1833 | COCHIN BLACK TERMINAL | Location to conduct monthly meetings with transporters | SOD | Marketing | CZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125860 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125860 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125860 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011134ACN-2026-03-4000125860 | AUD-2026-03-2000011134ACN-2026-03-4000125860 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 49
ALBY ABRAHAM ARACKAL | 2026-08-10 | SRIJIN S | 2026-04-21 | All the completed projects were capitalized. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125861 | Closed | SRIJIN S | 2026-04-21 | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | 4.3 | 7 projects to be completed for which works are under progress | 1833 | COCHIN BLACK TERMINAL | All projects to be completed in all aspects including capitalization, cloase out as per time lines | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125861 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125861 | 2026-09-08 16:00 | 41.0872 | 343 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125861 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125861 | AUD-2026-03-2000011134ACN-2026-03-4000125861 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 49
TILKAN RAVINDRA KUMAR | 2026-08-10 | Sreelal P P | 2026-07-30 | Security routinely inspecting the TT movement area for safe movement and wheeel choke compliance | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141182 | Closed | Sreelal P P | 2026-07-30 | Surprise night inspections are carried out once in 2 months. Last surprise check combinedly conducted by LIC and HSSE officer on 06.03.2026. Security were alert. Alertness of security also verified during Senior Management Inspection on 14.03.2026 | 2.4 | Security alertness checked (night-halt / surprise checks) | 1845 | IRUMPANAM TERMINAL | Security alertness checked and found to be satisfactory. Advised to ensure traffic management along approach road | SOD | Marketing | CZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013833ACN-2026-06-4000141182 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141182 | 2026-09-02 16:30 | 47.0663 | 343 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141182 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013833ACN-2026-06-4000141182 | AUD-2026-06-2000013833ACN-2026-06-4000141182 | 21 | 21 | 27 | 80 | 1 | -4 | 44 | 49
TILKAN RAVINDRA KUMAR | 2026-08-10 | Sreelal P P | 2026-08-10 | 1. Scrapyard has been cleared using JCB. Excessive vegetation has been cleared 2. Plastic waste has been removed and soil has beendumped on degradable waste. | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141186 | Closed | Sreelal P P | 2026-08-10 | House keeping is good & observed PPE usage proper in location. | 3.15 | Housekeeping & PPE usage checked | 1845 | IRUMPANAM TERMINAL | 1. Scrap yard to be maintained in a clean, organized, and systematic manner. 2. Accumulated waste, including plastic waste, near High Mast-3 to be cleared and the area maintained clean. | SOD | Marketing | CZR | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141186 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141186 | 2026-09-02 16:30 | 47.0663 | 343 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141186 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141186 | AUD-2026-06-2000013833ACN-2026-06-4000141186 | 21 | 21 | 27 | 80 | 1 | -4 | 52 | 49
TILKAN RAVINDRA KUMAR | 2026-08-10 | Sreelal P P | 2026-08-10 | Dry-cut branches has been removed from the process area. | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141187 | Closed | Sreelal P P | 2026-08-10 | Dry-cut branches to be removed from the process area, and the uprooted tree to be completely cleared from the site. | 3.16 | Earth pits / boundary / vegetation control checked | 1845 | IRUMPANAM TERMINAL | Dry-cut branches to be removed from the process area, and the uprooted tree to be completely cleared from the site. | SOD | Marketing | CZR | 2026-07-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | EMERGENCY | S2 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141187 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141187 | 2026-09-02 16:30 | 47.0663 | 343 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141187 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013833ACN-2026-06-4000141187 | AUD-2026-06-2000013833ACN-2026-06-4000141187 | 21 | 21 | 27 | 80 | 1 | -4 | 48 | 49
TILKAN RAVINDRA KUMAR | 2026-08-10 | Sreelal P P | 2026-08-10 | Location has declared 24 nos of Top loading arms (Technika) as surplus in asset management portal. Location has sent mail to CBOT for upliftment of top loading arm as required | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141193 | Closed | Sreelal P P | 2026-08-10 | Top loading arms removed from Gantry are placed at one place | 4.5 | scrap disposal progress reviwed/scrap free environment checked. | 1845 | IRUMPANAM TERMINAL | Advised to shift two top loading arms to CBOT. Balance are to be declared as surplus and details to be uploaded | SOD | Marketing | CZR | 2026-07-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 6 | ASSET INTEGRITY | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141193 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141193 | 2026-09-02 16:30 | 47.0663 | 343 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141193 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141193 | AUD-2026-06-2000013833ACN-2026-06-4000141193 | 21 | 21 | 27 | 80 | 1 | -4 | 48 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Interection completed with all officers. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129820 | Closed | KUMAR ANIMESH | 2026-08-10 | Interaction done and junior officers Swadha & Ansari advised for decisiveness , energetic & enhancing tech. competency | 1.1 | Interaction with all officers (1–1.5 hrs) | 1636 | BALASORE DEPOT | These officers to further develop competencies in all depot operations, TAS & M&I jobs | SOD | Marketing | ECZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129820 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129820 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129820 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129820 | AUD-2026-05-2000012001ACN-2026-05-4000129820 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | All major KPI were discussed and officers are inline with the target provided , regular monitoring through BCM meeting is being ensured. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129821 | Closed | KUMAR ANIMESH | 2026-08-10 | Yes all major KPIs reviewed | 1.2 | Performance review conducted | 1636 | BALASORE DEPOT | Pending OISD points, stock loss during rake receipt, disposal of slow moving lubes, removal of FO lines & disposal of offspec FO need to be focussed | SOD | Marketing | ECZ | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 9 | PROCESS SAFETY | S3 | F3 | 2026-09-30 | AUD-2026-05-2000012001ACN-2026-05-4000129821 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129821 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129821 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129821 | AUD-2026-05-2000012001ACN-2026-05-4000129821 | 21 | 21 | 27 | 80 | 12 | 12 | 57 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have completed compliance of all OISD points and We are taking all preventive measures for reducing any stock loss. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122630 | Closed | KUMAR ANIMESH | 2026-08-10 | Yes all major KPIs reviewed | 1.2 | Performance review conducted | 1636 | BALASORE DEPOT | stock loss & OISD points compliances to be given focus | SOD | Marketing | ECZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011313ACN-2026-03-4000122630 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122630 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122630 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122630 | AUD-2026-03-2000011313ACN-2026-03-4000122630 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have completed compliance of All audit points related to OISD. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122631 | Closed | KUMAR ANIMESH | 2026-08-10 | OISD action points reviewed | 1.4 | Earlier action points status checked | 1636 | BALASORE DEPOT | All OISD points to be completed by Apr 2026 | SOD | Marketing | ECZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122631 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122631 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122631 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122631 | AUD-2026-03-2000011313ACN-2026-03-4000122631 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | All pending OISD points complied. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129823 | Closed | KUMAR ANIMESH | 2026-08-10 | OISD action points reviewed | 1.4 | Earlier action points status checked | 1636 | BALASORE DEPOT | All OISD PENDING points (2 nos.) to be complied | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129823 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129823 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129823 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129823 | AUD-2026-05-2000012001ACN-2026-05-4000129823 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Same point is being complied in Part code 4.5 | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129824 | Closed | KUMAR ANIMESH | 2026-08-10 | Compliances of pending OISD points, IA points , removal of Lubes from warehouse , scrap disposal of pending scrap items | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1636 | BALASORE DEPOT | Pending scrap items to be disposed in Q1 | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129824 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129824 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129824 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129824 | AUD-2026-05-2000012001ACN-2026-05-4000129824 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
|  | PAMPANABOYINA SWARNA REKHA | 2026-08-10 | PM jobs completed within time and PM orders closed. | AUDIT UPLOAD IN SAP | 2026-06-10 16:45 | AUD-2026-07-2000016564 | 2026-06-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146466 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-08-10 | PM jobs to be completed within time and PM orders to be closed. | 4.2 | Maintenance activities reviewed | 3693 | KAKINADA TML | PM jobs to be completed within time and PM orders to be closed. | SOD | Marketing | SCR | 2026-06-25 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-25 | AUD-2026-07-2000016564ACN-2026-07-4000146466 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016564ACN-2026-07-4000146466 | 2026-09-16 16:00 | 33.0872 | 297 | >20 | AUD-2026-07-2000016564 - ACN-2026-07-4000146466 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016564ACN-2026-07-4000146466 |  | AUD-2026-07-2000016564ACN-2026-07-4000146466 | 21 |  | 27 | 80 | 0 | 0 | 43
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | All HVLR/HCD/RSFPS/ESD are working and it is being checked on regular basis. Service engineer visited and corrective action taken for open Path HCD of tank 6 and working fine. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129829 | Closed | KUMAR ANIMESH | 2026-08-10 | checked and HVLR/HCD/RSFPS/ESD found working , Except for open Path HCD of tank 6 | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1636 | BALASORE DEPOT | Open path HCD of tank 6 and point type HCD to be checked by AMC vendor . Till such time portable HCD detector to be used to check gas level on daily safety check list | SOD | Marketing | ECZ | 2026-05-15 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-15 | AUD-2026-05-2000012001ACN-2026-05-4000129829 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129829 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129829 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129829 | AUD-2026-05-2000012001ACN-2026-05-4000129829 | 21 | 21 | 27 | 80 | 12 | 12 | 37 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Fire extinguisher are being checked on regular basis. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129830 | Closed | KUMAR ANIMESH | 2026-08-10 | Found Okay . | 2.14 | TT crew fire extinguisher usage checked | 1636 | BALASORE DEPOT | Advised planning officer to check for all TTs on random basis and use atleast one TT Fire ext. | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129830 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129830 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129830 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129830 | AUD-2026-05-2000012001ACN-2026-05-4000129830 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have placed order to purchase this item of clour blindness check text book, we will recieve by 18.08.2026, then we will ensure random check of colour blindness of all drivers. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122637 | Closed | KUMAR ANIMESH | 2026-08-10 | Equipment not available in location. | 2.16 | Eyesight / colour-blindness awareness checked | 1636 | BALASORE DEPOT | LIC advised to procure the same immediately and advise security to check randomly | SOD | Marketing | ECZ | 2026-04-30 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122637 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122637 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122637 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122637 | AUD-2026-03-2000011313ACN-2026-03-4000122637 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have placed order for procurement , we will recieve item within 7 days.Then random check for drivers will be ensured for colour blindness. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129831 | Closed | KUMAR ANIMESH | 2026-08-10 | Eye sight chart available . Colour blindness booklet not available | 2.16 | Eyesight / colour-blindness awareness checked | 1636 | BALASORE DEPOT | LIC advised to procure the same immediately and advise security to check randomly | SOD | Marketing | ECZ | 2026-05-30 | FAILURE TO FOLLOW PROCEDURES | 12 | PROCESS SAFETY | S3 | F4 | 2026-05-30 | AUD-2026-05-2000012001ACN-2026-05-4000129831 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129831 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129831 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129831 | AUD-2026-05-2000012001ACN-2026-05-4000129831 | 21 | 21 | 27 | 80 | 12 | 12 | 39 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We are conducting Monthly mock drill on spillage scenario, spillage + fire scenario. We cover all possible positions. This is stenthening the fire fighting handling. We are devloping doing the drill as per ERDM plan. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129826 | Closed | KUMAR ANIMESH | 2026-08-10 | Location is falls under single contingency . Spillage scenerio created at TT Gantry during mock drill conducted on 23.4.26 | 2.2 | Double contingency scenario simulated; observations recorded | 1636 | BALASORE DEPOT | 1. improvement in action taken during spillage scenerio by the team 2. Usage of PA system during drill by leader 3. Actions to be done for spillage scenerio only to be discussed & practiced in mock drills 4. It was advised that SCABA suit to be worn by person near to accident site only to avoid delays in movement | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129826 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129826 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129826 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129826 | AUD-2026-05-2000012001ACN-2026-05-4000129826 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
|  | PAMPANABOYINA SWARNA REKHA | 2026-08-10 | New lights installed.Lux level project work completed | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126440 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-08-10 | Lux level not meeting requirements, For improvement of Lux levels tender floated for additional lights and PO placement by 27.03.2026 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 3693 | KAKINADA TML | To follow up for PO placement by 27/03/2026 | SOD | Marketing | SCR | 2026-04-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126440 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126440 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126440 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126440 |  | AUD-2026-04-2000011081ACN-2026-04-4000126440 | 21 |  | 26 | 80 | 0 | 0 | 35
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Project taken and additional yard lights, tower light , lights in Admin building installed, Additional light have installed in gantary area to improve LUX level. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129827 | Closed | KUMAR ANIMESH | 2026-08-10 | Lux level is low behind TT gantry , secondary roads | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1636 | BALASORE DEPOT | Light poles installed , commissioning pending | SOD | Marketing | ECZ | 2026-05-15 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-15 | AUD-2026-05-2000012001ACN-2026-05-4000129827 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129827 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129827 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129827 | AUD-2026-05-2000012001ACN-2026-05-4000129827 | 21 | 21 | 27 | 80 | 12 | 12 | 37 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Corrective action taken by TAS and Godrej agency , now trunstile is drooping after ESD. It is completed by taking project. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129828 | Closed | KUMAR ANIMESH | 2026-08-10 | Found okay . However during ESD, turnstile not dropping . Same to be taken up with Godrej | 2.8 | Access control systems checked | 1636 | BALASORE DEPOT | To be taken up with Godrej | SOD | Marketing | ECZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S1 | F2 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129828 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129828 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129828 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129828 | AUD-2026-05-2000012001ACN-2026-05-4000129828 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have deposited the payment to W&M, Officer has given appointment to visit the site by 22.08.2026, Calibration of Bay 5 will be completed that day. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129834 | Closed | KUMAR ANIMESH | 2026-08-10 | BC-05 A K factor changes done in Aug 2025 during W&M calibration. Bay no. 5 for full HSD & SKO found to be delivering less & closedfor normal operations. | 3.13 | K-factor changes reviewed (if any) | 1636 | BALASORE DEPOT | Get the Bay 5 HSD/SKO MFM checked by W&M | SOD | Marketing | ECZ | 2026-05-30 | FAILURE TO FOLLOW PROCEDURES | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-30 | AUD-2026-05-2000012001ACN-2026-05-4000129834 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129834 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129834 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129834 | AUD-2026-05-2000012001ACN-2026-05-4000129834 | 21 | 21 | 27 | 80 | 12 | 12 | 39 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Earth pits / boundary / vegetation control was checked and found okay. Earth pit test have been conducted for all and it is valid till November 2026 | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129835 | Closed | KUMAR ANIMESH | 2026-08-10 | Okay . Earth pit testing in progress , dates to be changed | 3.16 | Earth pits / boundary / vegetation control checked | 1636 | BALASORE DEPOT | Ensure that vendor change the dates in time . Suggested that earth pits testing date to be divided in 3 diff. dates to avoid all earth pits due date falls on one day, which is not possible to do | SOD | Marketing | ECZ | 2026-05-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-05-30 | AUD-2026-05-2000012001ACN-2026-05-4000129835 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129835 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129835 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129835 | AUD-2026-05-2000012001ACN-2026-05-4000129835 | 21 | 21 | 27 | 80 | 12 | 12 | 39 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | This OISD and MDSA pending points have been complied , Now nil pending. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122640 | Closed | KUMAR ANIMESH | 2026-08-10 | pending Points : OISD - 7 out of 26 SSA - Same MDSA - 1 out of 38 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1636 | BALASORE DEPOT | Advised to close all points | SOD | Marketing | ECZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122640 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122640 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122640 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122640 | AUD-2026-03-2000011313ACN-2026-03-4000122640 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | 100% OISD Compliance completed, previous MDSA all points complied. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129836 | Closed | KUMAR ANIMESH | 2026-08-10 | pending Points : OISD - 2 out of 26 SSA - Same MDSA - 1 out of 38 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1636 | BALASORE DEPOT | Advised to close all points | SOD | Marketing | ECZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129836 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129836 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129836 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129836 | AUD-2026-05-2000012001ACN-2026-05-4000129836 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | EM Lock SOP was verified and found okay. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129832 | Closed | KUMAR ANIMESH | 2026-08-10 | found okay | 3.5 | EM Lock SOP compliance verified | 1636 | BALASORE DEPOT | advised LIC to check all locks using intelligent key and have record | SOD | Marketing | ECZ | 2026-05-30 | LACK OF TRAINING OR COMPETENCY | 6 | ASSET INTEGRITY | S2 | F3 | 2026-05-30 | AUD-2026-05-2000012001ACN-2026-05-4000129832 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129832 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129832 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129832 | AUD-2026-05-2000012001ACN-2026-05-4000129832 | 21 | 21 | 27 | 80 | 12 | 12 | 39 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | Location is checking all locks using intelligent key and records are being maintained. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122639 | Closed | KUMAR ANIMESH | 2026-08-10 | found okay | 3.5 | EM Lock SOP compliance verified | 1636 | BALASORE DEPOT | advised LIC to check all locks using intelligent key and have record | SOD | Marketing | ECZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011313ACN-2026-03-4000122639 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122639 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122639 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122639 | AUD-2026-03-2000011313ACN-2026-03-4000122639 | 21 | 21 | 26 | 80 | 12 | 12 | 35 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | All losses are being booked and we are writting the same to supplier also for taking corrective action. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129833 | Closed | KUMAR ANIMESH | 2026-08-10 | Location advised to check randomly ethanol TTs in calibration shed and make record of variations supplier wise | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1636 | BALASORE DEPOT | high losses to be taken up with supplier strongly | SOD | Marketing | ECZ | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129833 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129833 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129833 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129833 | AUD-2026-05-2000012001ACN-2026-05-4000129833 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | All project completed , except the major project of Bottom Loading facility , which will be completed by 30.09.2026. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129837 | Closed | KUMAR ANIMESH | 2026-08-10 | All NPCB projects reviewed which are mostly taken for OISD complinaces. Only Major project of Bottom loading is in progress | 4.3 | Project progress reviewed | 1636 | BALASORE DEPOT | Location officers advised to complete all projects by 30.06.2026 | SOD | Marketing | ECZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129837 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129837 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129837 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129837 | AUD-2026-05-2000012001ACN-2026-05-4000129837 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have completed all all the pending projects, however only one major project of Bottom loading facility is going on which will becompleted by 30.09.2026 | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122642 | Closed | KUMAR ANIMESH | 2026-08-10 | All NPCB projects reviewed which are mostly taken for OISD complinaces. Only Major project of Bottom loading is in progress | 4.3 | Project progress reviewed | 1636 | BALASORE DEPOT | Location officers advised to complete all projects by 30.06.2026 | SOD | Marketing | ECZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122642 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122642 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122642 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122642 | AUD-2026-03-2000011313ACN-2026-03-4000122642 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have formed the scrap disposal committee and RFD is being initiated . We will complete the Scrap disposal within 3 Month i.e. ByNovember 2026. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129838 | Closed | KUMAR ANIMESH | 2026-08-10 | Location has done very good job in this KPI and disposed scrap worth Rs.10.57 lakhs in LASY FY | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1636 | BALASORE DEPOT | Some more scrap items of 250 KVA DGSET, Old FVD panels , MCC panels , MS scrap , non-ferous scrap to be disposed in Q1 | SOD | Marketing | ECZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129838 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129838 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129838 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012001ACN-2026-05-4000129838 | AUD-2026-05-2000012001ACN-2026-05-4000129838 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We have made scrap disposal committee, RFD is being floated accordingly. We are ensuring to dispose all scrap of Balasore IRD by November 2026. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122643 | Closed | KUMAR ANIMESH | 2026-08-10 | Location has done very good job in this KPI and disposed scrap worth Rs.10.57 lakhs in this FY | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1636 | BALASORE DEPOT | Some more scrap items of 250 KVA DGSET, Old FVD panels , MCC panels , MS scrap , non-ferous scrap to be disposed | SOD | Marketing | ECZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011313ACN-2026-03-4000122643 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122643 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122643 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011313ACN-2026-03-4000122643 | AUD-2026-03-2000011313ACN-2026-03-4000122643 | 21 | 21 | 26 | 80 | 12 | 12 | 44 | 49
LAKRA JUGAL AJIT | 2026-08-10 | KUMAR ANIMESH | 2026-08-10 | We are on regular basis doing Mock drill on monthly basis in depot premises. we are ensuring to implememt all feedback in Mock drill. In Mock drill we ensure 100% participation of staff & employees. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129825 | Closed | KUMAR ANIMESH | 2026-08-10 | Fire drill records reviewed for drill conducted in last 6 months | 2.1 | Fire drill conducted in last 6 months (surprise) | 1636 | BALASORE DEPOT | Improvement in mock drill discussed | SOD | Marketing | ECZ | 2026-06-30 | INADEQUATE SAFETY CULTURE | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-30 | AUD-2026-05-2000012001ACN-2026-05-4000129825 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129825 | 2026-09-26 17:30 | 23.0247 | 343 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129825 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012001ACN-2026-05-4000129825 | AUD-2026-05-2000012001ACN-2026-05-4000129825 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Location has started closely monitoring the TDG violations. 100% dip checking of TTs and loads after calibration. Surprise TT checks are done by LIC Training sessions were conducted and are being conducted regularly for all officer,NM and contract workmen. Allofficers have started reporting of Near misses, UCs, UAs in SAP | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143154 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Day-to-day operational activities were reviewed. Officers were advised to get more engaged in field for TT dip checking / TT fittings checking. Officers to make rounds of TT parking area, BB-II, Jetty Side and Line Patrolling of MS/HSD/ATF jetty line from BB-II to BB-I. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1644 | KOLKATA-I TERMINAL | Location to control TDG violation, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration. LIC to carry out surprise check of loaded TTs. TTs. All safety fittings of TTs to be checked thoroughly. All the officerswere advised to have hands on training and operational knowledge of all the safety critical equipment. All officers to start reporting of Near misses, UCs, UAs in SAP | SOD | Marketing | EZ | 2026-07-20 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143154 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143154 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143154 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143154 | AUD-2026-07-2000015090ACN-2026-07-4000143154 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Location has worked on the points of the fire drill . Session was taken with all concerned personnels to implement the learnings from the observation and preparation for next drill. Following points were also discussed to avoid reoccurance in the next drill. 1. There was a communication gap w.r.t position of fire and thus fire extinguisher was operated by one of the member of fire combat team. 2. Movement of the members of fire Combat team was observed crossing the rake and not using the overhead stairs 3. Chin Strap of one of the member of fire combat team was missing. PPE usages to be ensured as per SOP only without any loose ends. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143161 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Scenario : Fire Drill in BB-II was conducted wherein rake unloading was going on and a flash fire on dome cover occurred while rakegetting unloaded (simulated). 1. All Equipment worked up to satisfaction and foam generation was also very good. 2. There was a communication gap w.r.t position of fire and thus fire extinguisher was operated by one of the member of fire combat team. 3. Movement of the members of fire Combat team was observed crossing the rake and not using the overhead stairs 4. Chin Strap of one of the member of fire combat team was missing. PPE usages to be ensured as per SOP only without any loose ends. | 2.2 | Double contingency scenario simulated; observations recorded | 1644 | KOLKATA-I TERMINAL | All the observation and recommendation of the drill to be implemented in the next and subsequent drill | SOD | Marketing | EZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015090ACN-2026-07-4000143161 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143161 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143161 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143161 | AUD-2026-07-2000015090ACN-2026-07-4000143161 | 21 | 21 | 27 | 80 | 0 | -7 | 48 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | DSO has started taking regular training sessions on critical safety equipments to all officers, NM and contract workmen to increase the awareness for smooth fuctioning of safety equipments. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143165 | Closed | SAARTHAK SARKAR | 2026-08-10 | DSO to ensure to have hands on training to all the officers. All officer must know the positioning of the different fire fire fighting equipments. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1644 | KOLKATA-I TERMINAL | More hands on training on safety critical equipment to be acquired by all the officers | SOD | Marketing | EZ | 2026-07-20 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143165 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143165 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143165 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143165 | AUD-2026-07-2000015090ACN-2026-07-4000143165 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | TT crew were given proper training to follow the SOP. Location has taken measures to minimize the frequently occuring alerts. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143163 | Closed | SAARTHAK SARKAR | 2026-08-10 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. The VA alerts are repetitive in nature like not keeping 9 KG DCP beside TT while loading. | 2.7 | VA alerts checked / analysed | 1644 | KOLKATA-I TERMINAL | All SOP must be followed with NIL exception. | SOD | Marketing | EZ | 2026-07-20 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143163 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143163 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143163 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143163 | AUD-2026-07-2000015090ACN-2026-07-4000143163 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 |  |  | Godrej in tank farm and gantry are out of order since a long time and vendor has conveyed that the repairing will take time. Hence as per SOP, alternate arrangement has been ensured i.e. a dedicated security personnel has been deployed with attendance register torecord all in and out entries and thus ensuring NIL unauthorised entry. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143164 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Access control system at Tank farm, TTG found to be non functional. (This was also observed during last inspection) It was also noted that the VMS service is not operational. | 2.8 | Access control systems checked | 1644 | KOLKATA-I TERMINAL | Location to closely coordinate with M/s Godrej and ensure 100% functionality of the access control system VMS to be implemented. Nil case of visitors entry without VMS to be ensured | SOD | Marketing | EZ | 2026-07-20 | INSTRUMENTATION OR ALARM FAILURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143164 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143164 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143164 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143164 | AUD-2026-07-2000015090ACN-2026-07-4000143164 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Review has been done by LIC & all are within control. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143171 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1644 | KOLKATA-I TERMINAL | LIC to review the critical alarms periodically and report if any abnormalities found. | SOD | Marketing | EZ | 2026-07-20 | FATIGUE AND STRESS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143171 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143171 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143171 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143171 | AUD-2026-07-2000015090ACN-2026-07-4000143171 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Review has been done by LIC, all within control | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143172 | Closed | SAARTHAK SARKAR | 2026-08-10 | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1644 | KOLKATA-I TERMINAL | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-07-20 | FATIGUE AND STRESS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143172 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143172 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143172 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143172 | AUD-2026-07-2000015090ACN-2026-07-4000143172 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Proper instruction given to Planning and Gantry officer to consult with TAS officer and LIC before declaring any Sick TT in TAS. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143173 | Closed | SAARTHAK SARKAR | 2026-08-10 | Local loading report reviewd and found that local loading being done for own use in DG/ Fire Engine. Local loading being also done for Budge Budge lube and Ramnagar lubes. One TT was made sick in TAS after invoice is generated. Later PRCN was also processed. | 3.14 | Local loading checks (if applicable) | 1644 | KOLKATA-I TERMINAL | Planning Officer to be extra vigilant and must consult the officer hadnling TAS before making any TT as Sick in TAS. Strict control measures to be ensured for all local loading/ Sick TT/ User Access Mtrix, local order entry and other critical TAS parameters. | SOD | Marketing | EZ | 2026-07-20 | COMPLACENCY OR RISK NORMALIZATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143173 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143173 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143173 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143173 | AUD-2026-07-2000015090ACN-2026-07-4000143173 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Proper Housekeeping in TTG is ensured by Gantry officer. All project surplus item removed and shifted to designated place. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143174 | Closed | SAARTHAK SARKAR | 2026-08-10 | Housekeeping & PPE usage checked | 3.15 | Housekeeping & PPE usage checked | 1644 | KOLKATA-I TERMINAL | House keeping in TTG to be improved. Project surplus must be removed before gantry operation. | SOD | Marketing | EZ | 2026-07-20 | INSUFFICIENT SUPERVISION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143174 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143174 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143174 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143174 | AUD-2026-07-2000015090ACN-2026-07-4000143174 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | All damaged earthpit boards are replaced. Emergency board displayed at TT planning room - Stakeholders name / officers name with contact no. has been amended. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143175 | Closed | SAARTHAK SARKAR | 2026-08-10 | Earthpit board to be corrected at few places. Emergency board displayed at TT planning room - Stakeholders name / officers name with contact no. to be reviewed/ amended | 3.16 | Earth pits / boundary / vegetation control checked | 1644 | KOLKATA-I TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-07-20 | FATIGUE AND STRESS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143175 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143175 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143175 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143175 | AUD-2026-07-2000015090ACN-2026-07-4000143175 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Gantry officer has been properly conveyed to personally check all the TTs post load and flag any variation. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143166 | Closed | SAARTHAK SARKAR | 2026-08-10 | Random checking of the dip for TT no. WB19R1278 post loading done and found minimal variation. | 3.2 | Post-loading dip checks verified | 1644 | KOLKATA-I TERMINAL | Gantry officer to encure all TTs are dip checked post loading and any abnormal vairaion is reported to LIC followed by calibration verification of that TT | SOD | Marketing | EZ | 2026-07-20 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143166 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143166 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143166 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143166 | AUD-2026-07-2000015090ACN-2026-07-4000143166 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | 100% Secondary routes have been created in coordination with SOs. Location has been monitoring on daily basis on VTS movements to avoid route deviation/ unauthorised stopages by trucks. Prompt actions are also taken on erring transporters as per ITDG.5 ifapplicable. Regualr feedbacks are shared with zone on action taken on such cases. All records are also maintained. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143167 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Location is taking action on VTS deviation basis mail received from zone and from OCC. Location to take extra attention on route deviation/ unauthorised stopages by trucks. Prompt actions to be taken on erring transporters as per ITDG.5 if applicable. Spotsidentified where multiple TTs are stopping unauthorisedly to be initimated to the police station under which the location is identified. Regualr feedback to be shared with zone on action taken on such cases. | 3.3 | VTS deviations reviewed | 1644 | KOLKATA-I TERMINAL | Location is advised to create the secondary route wherever applicable and action to be taken as per ITDG wherever deemed fit. | SOD | Marketing | EZ | 2026-07-20 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143167 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143167 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143167 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015090ACN-2026-07-4000143167 | AUD-2026-07-2000015090ACN-2026-07-4000143167 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | EBP records are being maintained. 20% of the loaded TTs are getting checked for EBP% & results are within limit. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143168 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Random checking of EBP done from the all level sample of TT WB19R1278 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1644 | KOLKATA-I TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-07-20 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-20 | AUD-2026-07-2000015090ACN-2026-07-4000143168 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143168 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143168 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143168 | AUD-2026-07-2000015090ACN-2026-07-4000143168 | 21 | 21 | 27 | 80 | 0 | -7 | 46 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | All ethanol unloading records are now being maintained properly to ensure nil deviation. | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143169 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Ethanol/Bio Diesel receipt SOPs to be strictly adhered to and concerned Officers to be well conversant of same. Upon review, it is understood that no records are being maintained for monitoring the TT wise dips observed V/s product received in tank and corrective action thereby. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1644 | KOLKATA-I TERMINAL | Necessary records to be maintained for each TTs unloaded for assessing the receipt quantity. Ethanol TT receipt losses to be brought under control immeditely by stringent monitoring and checks for each TT reporting at location. | SOD | Marketing | EZ | 2026-07-10 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-10 | AUD-2026-07-2000015090ACN-2026-07-4000143169 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143169 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143169 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143169 | AUD-2026-07-2000015090ACN-2026-07-4000143169 | 21 | 21 | 27 | 80 | 0 | -7 | 45 | 49
MAJUMDER BIRAJ | 2026-08-10 | SAARTHAK SARKAR | 2026-08-10 | Visit in TTG, TWG, Scrapyard, TTPH, TWPH, Control room, Security room, Admin carried out. Housekeeping & SOP adherence found satisfactory | KOLKATA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-29 20:30 | AUD-2026-07-2000015090 | 2026-06-29 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143177 | Closed | MAJUMDER BIRAJ | 2026-08-10 | Visit in TTG, TWG, Scrapyard, TTPH, TWPH, Control room, Security room, Admin carried out. Housekeeping & SOP adherence found satisfactory | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1644 | KOLKATA-I TERMINAL | Housekeepin in TTG / TT Parking to be improved. | SOD | Marketing | EZ | 2026-07-10 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-10 | AUD-2026-07-2000015090ACN-2026-07-4000143177 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015090ACN-2026-07-4000143177 | 2026-09-18 | 31.7538 | 343 | >20 | AUD-2026-07-2000015090 - ACN-2026-07-4000143177 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015090ACN-2026-07-4000143177 | AUD-2026-07-2000015090ACN-2026-07-4000143177 | 21 | 21 | 27 | 80 | 0 | -7 | 45 | 49
MAZUMDER SAUVIK | 2026-08-10 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-06-4000137701 | Closed | MD KASHIF | 2026-08-10 | Tankfarm fire fighting : Fire wall valve of Tk 201 found to be having integrity. | 6.10 | Quarterly Inspection | 1742 | BOKARO DEPOT | OK. Please maintin the same | SOD | Marketing | PZR | 2026-07-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137701 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137701 | 2026-09-19 10:00 | 30.3372 | 343 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137701 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137701 | AUD-2026-06-2000012744ACN-2026-06-4000137701 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
MAZUMDER SAUVIK | 2026-08-10 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-06-4000137702 | Closed | MD KASHIF | 2026-08-10 | Tankfarm fire fighting: Foam pourers of Tk202 were checked. These were generating foam satisfactorily. | 6.11 | Quarterly Inspection | 1742 | BOKARO DEPOT | OK. Please maintin the same | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137702 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137702 | 2026-09-19 10:00 | 30.3372 | 343 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137702 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137702 | AUD-2026-06-2000012744ACN-2026-06-4000137702 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Location is controlling TDG violations by regularly monitoring VTS of TTs and taking disciplinary actions with the help of concerned authorities. Dip checking of 100% of loaded TTs is carried by officers which by default includes dip checking of first three loadsafter TT calibration. Records maintained. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143414 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Day-to-day operational activities were reviewed. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1650 | HALDIA TERMINAL | Location to control TDG violations, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration | SOD | Marketing | EZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143414 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143414 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143414 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143414 | AUD-2026-07-2000015092ACN-2026-07-4000143414 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Suraj Manna (JEO) is given hands on training for operating all the fire fighting equipment. He is sensitized about positioning of all the safety critical equipment and ESD. Black oil loss is mainly attributable to variations in loading and unloading dip measurements and temperature differences during rake receipt. Loading location VNBOT shares details for black oil rake receipt to facilitate reconciliation and monitoring of quantity variations. JV with HPPL completed, cost shared of INR 491101.30. Transporters and DCTs are taken on board for conversion of their TTs to bottom loading. DCT TTs bottom loading conversion already commenced. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143415 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Individual review of officer carried out with respect to KPI and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1650 | HALDIA TERMINAL | Suraj Manna (JEO) was advised to have hand on exercise for operating all the fire fighting equipment. Further, he should have the knowledge w.r.t positioning of all the safety critical equipment and ESD. LIC to arrest the black oil rake receipt losses by suitablecoordination and actions. As date 08-06-26, loss of 19.7 KL is there in LSHS Premium. All JVs with HPPL should be completed. Transporters and DCTs to be taken on board for conversion of their TTs to bottom loading. | SOD | Marketing | EZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015092ACN-2026-07-4000143415 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143415 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143415 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143415 | AUD-2026-07-2000015092ACN-2026-07-4000143415 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Budget requirement sent to zone with description. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143417 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Location requested for extra budget allocation for Tank /Pipeline/ structure painting. | 1.5 | HQO / Zonal support required identified | 1650 | HALDIA TERMINAL | It is advised to send the budget requirement to zone along with all the supporting documents. | SOD | Marketing | EZ | 2026-06-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143417 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143417 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143417 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143417 | AUD-2026-07-2000015092ACN-2026-07-4000143417 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | 1.Central Contract available for AMC of DBBV (Contract no: 5300018198). AMC of DBBVs carried. 2. Calibration verification for TTs done and records maintained | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143419 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1650 | HALDIA TERMINAL | 1. CAMC PO for DBBV to be processed 2. Calibration verification for TTs to be done and records maintained | SOD | Marketing | EZ | 2026-07-31 | POOR COMMUNICATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143419 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143419 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143419 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143419 | AUD-2026-07-2000015092ACN-2026-07-4000143419 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Hands on training on safety critical equipment acquired by all the officers. Training records kept for reference. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143427 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Junior Executive officers demonstrated the MEFG | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1650 | HALDIA TERMINAL | More hands on training on safety critical equipment to be acquired by all the officers | SOD | Marketing | EZ | 2026-06-30 | POOR COMMUNICATION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143427 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143427 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143427 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143427 | AUD-2026-07-2000015092ACN-2026-07-4000143427 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Two drills conducted in the month of July and all the short comings are addressed. Fire fighting equipment nearest to the incident point is operated for fast action and controlling the incident on time. PPE wore properly by the person wearing SCABA. 1.Clear communication w.r.t leakage scenario given to the SG. 2. Information passed to DSO/ LIC about leakage scenario. 3. ESD operated during the initial phase when incident was addressed. 4. Fire fighting equipments operated on time. 5. LEL level recorded and all clear siren given as LEL was 0. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143421 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Fire in the tank truck delivery valve was simulated when the TT was standing in the Parking and following observations recorded : 1. TT Crew of the nearest TT operated DCP 2. Message was passed to the SG at main gate who in turn informed the DSO / LIC. 3. Nearest WCFM was operated from two sides 4. Double hydrant was not used which was positioned exactly in front of the TT 5. Chin Strap of the Safety Helmet was not tied by the personnel wearing SCABA Off Shift scenario of Leakage from the HS tank manhole was undertaken wherein only one planning officer (JEO) was there and following observations recorded : 1. Clear communication w.r.t leakage scenario to the SG was missing 2. Information to the DSO/ LIC was not communicated 3. Officer entered the tank dyke to access the leakage without ascertaining the LEL level 4. ESD was not operated during the initial phase 5. MEFG was operated after 15-20 minutes 6. LEL level was not recorded at all | 2.2 | Double contingency scenario simulated; observations recorded | 1650 | HALDIA TERMINAL | All the observation and recommendation of the drill to be implemented in the next drill | SOD | Marketing | EZ | 2026-07-31 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143421 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143421 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143421 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143421 | AUD-2026-07-2000015092ACN-2026-07-4000143421 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | Night alertness strengthened. Surprise night inspection done on fortnightly basis. Records maintained. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143423 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Security personnel were interrogated on night time preparedness on emergency and mitigation measures to be taken. The team was found to be well versed on the same. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1650 | HALDIA TERMINAL | Night alertness to be more strengthened. Frequency of Surprise night inspection to be increased. | SOD | Marketing | EZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143423 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143423 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143423 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143423 | AUD-2026-07-2000015092ACN-2026-07-4000143423 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | LIC reviews the critical alarms periodically and report if any abnormalities found. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143433 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1650 | HALDIA TERMINAL | LIC to review the critical alarms periodically and report if any abnormalities found. | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143433 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143433 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143433 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015092ACN-2026-07-4000143433 | AUD-2026-07-2000015092ACN-2026-07-4000143433 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | LIC periodically reviews the K Factor and meter factor in system and in BCU | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143434 | Closed | ISLAM SK WAHIUL | 2026-08-11 | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1650 | HALDIA TERMINAL | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143434 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143434 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143434 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015092ACN-2026-07-4000143434 | AUD-2026-07-2000015092ACN-2026-07-4000143434 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
KUNDU DEBARUN | 2026-08-11 | ISLAM SK WAHIUL | 2026-08-11 | EPs are tested within 6 month frequency in presence of officer. EP resistance is coming below 2 Ohms for individual earthpit and below 1 Ohms for grid. Records maintained. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143437 | Closed | ISLAM SK WAHIUL | 2026-08-11 | Resistivity of EP no. 126 (TK13) checked and found beyond limits (3.4 Ohm without grid). There was delay in EP testing against the prescribed frequency of 6 months. Earth pits of LPS were not tested within due periodicity of 6 months. Vegetation inside the depot was also under control | 3.16 | Earth pits / boundary / vegetation control checked | 1650 | HALDIA TERMINAL | Location to ensure that EPs are tested well within the time period. Further, all Eps to be tested in presence of Officer | SOD | Marketing | EZ | 2026-06-30 | POOR COMMUNICATION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143437 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143437 | 2026-08-20 00:14 | 60.7441 | 344 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143437 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015092ACN-2026-07-4000143437 | AUD-2026-07-2000015092ACN-2026-07-4000143437 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 50
MEENA HEMANT KUMAR | 2026-08-11 |  |  |  | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128574 | Closed |  |  | OISD audit is scheduled on 18th to 20th May 2026. Location was asked to propose budget requirement for critical nature of job | 1.5 | HQO / Zonal support required identified | 1233 | BHARATPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | PROCESS SAFETY | S1 | F3 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128574 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128574 | 2026-09-16 17:45 | 33.0143 | 344 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128574 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010749ACN-2026-04-4000128574 | AUD-2026-04-2000010749ACN-2026-04-4000128574 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 50
MEENA HEMANT KUMAR | 2026-08-11 |  |  | TAS upgradation and spring box assembly have been extended and submersible pump has been closed | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128591 | Closed | MEENA HEMANT KUMAR | 2026-08-11 | Time extension up to 30.06.2026 taken for 3 projects. EDC is 15.06.2026 for all three projects. For 5 projects, it is Teco Completed. Location is requested to take timely action for closure of AR | 4.3 | Project progress reviewed | 1233 | BHARATPUR TERMINAL | All these projects are to be closed by June end. | SOD | Marketing | NWF | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128591 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128591 | 2026-09-16 17:45 | 33.0143 | 344 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128591 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128591 | AUD-2026-04-2000010749ACN-2026-04-4000128591 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 50
MEENA HEMANT KUMAR | 2026-08-11 |  |  | monthly verification is being done | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128598 | Closed | MEENA HEMANT KUMAR | 2026-08-11 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.8 | Additive stock monitoring | 1233 | BHARATPUR TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128598 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128598 | 2026-09-16 17:45 | 33.0143 | 344 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128598 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010749ACN-2026-04-4000128598 | AUD-2026-04-2000010749ACN-2026-04-4000128598 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 50
MEENA HEMANT KUMAR | 2026-08-11 |  |  | weekly call up is being sent | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138487 | Closed | MEENA HEMANT KUMAR | 2026-08-11 | Bay 4 is required to be converted into mixed bay. At present, it can be used to load HSD only. Location is already having MFM for ethanol flow measurement, DCV abd BAE. M/s Technica is supplying loading. This particular bay can be used to load mix product from both loading arms. Mr. rahul has been asigned this task. he needs to send weekly cal up till this job is completed. | 1.4 | Earlier action points status checked | 1233 | BHARATPUR TERMINAL | Pls send weekly call up with effect from 22.06.2026 and complete this job in time bound manner | SOD | Marketing | NWF | 2026-08-31 | FAILURE TO FOLLOW PROCEDURES | 12 | PROCESS SAFETY | S3 | F4 | 2026-08-31 | AUD-2026-06-2000013164ACN-2026-06-4000138487 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138487 | 2026-09-16 17:45 | 33.0143 | 344 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138487 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138487 | AUD-2026-06-2000013164ACN-2026-06-4000138487 | 21 | 21 | 27 | 80 | 2 | 1 | 52 | 50
MEENA HEMANT KUMAR | 2026-08-11 |  |  | PM schedule has been prepared and signed by vendor authorized person | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138489 | Closed | MEENA HEMANT KUMAR | 2026-08-11 | Location should convert all manpower based PO into job based Po in phase wise manner. By that time, location should prepare maintenance schedule of equipment in line with guidelines given by OEM, inline with shedule made by Sr. Mgr. M&I and also in line with OISD244. Preventive Jobs for 4 hrs per day can be assigned to a) Electricians b) Maintenance labors c) Housekeeping labors not engaged on routine nature of jobs (like gardening/toilet cleaning etc). Balance 4 hrs can be assigned to take care of jobs which are either breakdown in nature or some routine jobs. Location to prepare preventive maintenance schedule and ensure to get the job done. | 1.8 | Improvement plans discussed | 1233 | BHARATPUR TERMINAL | Location to prepare preventive Maint schedule by 30th June 2026. Location to get the schedule signed by local contractor. Job needsto be ensured by local contractor inline with finalised schedule. | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-06-2000013164ACN-2026-06-4000138489 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138489 | 2026-09-16 17:45 | 33.0143 | 344 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138489 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013164ACN-2026-06-4000138489 | AUD-2026-06-2000013164ACN-2026-06-4000138489 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 50
BANTHIYA RITESH DEELIP | 2026-08-11 | PANWAR VIPIN SINGH | 2026-08-09 | Currently no assets there unused as of now, Same shall be disposed after TAS revamp project and railway siding job surplus/unused material segregation and | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130675 | Closed | PANWAR VIPIN SINGH | 2026-08-09 | Nil / Unused assets of TAS Revamp is being generated and to be disposed off | 3.9 | Abnormal variations / unused assets reviewed | 1436 | SAGAR DEPOT | Location to ensure timely disposal of unused/expired assets in a time bound manner | SOD | Marketing | CEN | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-05-2000012507ACN-2026-05-4000130675 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130675 | 2026-08-07 19:00 | 72.9622 | 344 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130675 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130675 | AUD-2026-05-2000012507ACN-2026-05-4000130675 | 21 | 21 | 27 | 80 | 4 | 2 | 61 | 50
BANTHIYA RITESH DEELIP | 2026-08-11 | PANWAR VIPIN SINGH | 2026-08-09 | As of Q1, nil scrap available at location and same shall be disposed in before H1 in case of any unused scrap generated due to tas revamp and railway siding project. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130680 | Closed | PANWAR VIPIN SINGH | 2026-08-09 | Nothing pending except surplus old items generated during ongoing project work. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1436 | SAGAR DEPOT | Location is advised to initiate RFD for available scrap | SOD | Marketing | CEN | 2026-07-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-05-2000012507ACN-2026-05-4000130680 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130680 | 2026-08-07 19:00 | 72.9622 | 344 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130680 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130680 | AUD-2026-05-2000012507ACN-2026-05-4000130680 | 21 | 21 | 27 | 80 | 4 | 2 | 48 | 50
KUMBHARE SANJAY PURUSHOTTAM | 2026-08-11 | BHARTI YOGESH | 2026-08-10 | corrective action taken. workflow initiiated | LOCATION VISIT-NALAGARH_05-07.03.26 | 2026-03-07 | AUD-2026-04-2000010748 | 2026-03-05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128569 | Closed | BHARTI YOGESH | 2026-08-10 | Additional TTs induction to be expedited by the Location. | 1.3 | Pending issues reviewed | 1183 | NALGARH DEPOT | File note to be processed immediately with complete details in line with the procedure. | SOD | Marketing | NFZ | 2026-04-15 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-15 | AUD-2026-04-2000010748ACN-2026-04-4000128569 | HP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010748ACN-2026-04-4000128569 | 2026-08-27 | 53.7538 | 344 | >20 | AUD-2026-04-2000010748 - ACN-2026-04-4000128569 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000010748ACN-2026-04-4000128569 | AUD-2026-04-2000010748ACN-2026-04-4000128569 | 21 | 21 | 26 | 80 | 1 | 1 | 33 | 50
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123956 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | Upon review of local loading report, following deviations observed : 1.Many batches of 2Kl found for prover loading / bay calibration. 2. Many TTs are also loaded thru local loading but location failed to show the signed justification/ records for the same | 3.14 | Local loading checks (if applicable) | 1656 | DURGAPUR DEPOT | 1. Location to take the corrective action for early installation of radar gauge. 2. Location to improve the systematic checks and controls for local loading. Location to revert with detailed analysis and signed reasons recorded for all the local loads. Also, forthe provers loaded, Location to revert to zone with each case of prover loading and corresponding dip increase / gain in the UG tank. | SOD | Marketing | EZ | 2026-03-10 | INADEQUATE SAFETY CULTURE | 10 | EMERGENCY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123956 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123956 | 2026-08-07 13:00 | 73.2122 | 190 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123956 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011011ACN-2026-03-4000123956 |  | AUD-2026-03-2000011011ACN-2026-03-4000123956 | 21 |  | 26 | 80 | 0 | 0 | 28
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | MOC made and are closed. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123958 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | 3 no. of approved MOC not closed after the expiry date. | 3.17 | MOC status reviewed | 1656 | DURGAPUR DEPOT | Location to ensure 100% MOC closure post expiry / work completion which ever is earlier. | SOD | Marketing | EZ | 2026-03-09 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-03-09 | AUD-2026-03-2000011011ACN-2026-03-4000123958 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123958 | 2026-08-07 13:00 | 73.2122 | 189 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123958 | 532 | 8294 | 21 | 8294 | 224 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011011ACN-2026-03-4000123958 |  | AUD-2026-03-2000011011ACN-2026-03-4000123958 | 21 |  | 26 | 80 | 0 | 0 | 27
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | Location ensured the EBMS %age is checked and records maintained. Surprise check by LIC is done and records maintained. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122699 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | EBP%age checked for TT no. WB67B7069 and found within limit | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1656 | DURGAPUR DEPOT | Location to ensure to have the EBMS %age checks by officers and maintain records. Surprise check by LIC and maintain records. | SOD | Marketing | EZ | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000122699 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122699 | 2026-08-07 13:00 | 73.2122 | 185 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122699 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011011ACN-2026-03-4000122699 |  | AUD-2026-03-2000011011ACN-2026-03-4000122699 | 21 |  | 26 | 80 | 0 | 0 | 27
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123950 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | Pre and post unloading dip checked for 40 kL TT no. WB11K3239 supplied by M/s Alcograin (Panagarh). Compartment wise variations observed and overall dip shortage of approx. 8 cm observed. The shortage booked by the location is not in alignment with either TT dip shortage or receipt in UG tank which is not acceptable. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1656 | DURGAPUR DEPOT | Location to carry out the TT verification for this TT post unloading and ensure booking of loss. The TT matter should be taken up with the ethanol supplier so as not to send shortage. Planning officer to be extra vigilant and should abide by the TT unloading SOPsstrictly. LIC to carry out the surprise checks for the ethanol TTs to ensure correct receipt of product volume and booking appropriate shortage claims, if any. | SOD | Marketing | EZ | 2026-03-10 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123950 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123950 | 2026-08-07 13:00 | 73.2122 | 190 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123950 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011011ACN-2026-03-4000123950 |  | AUD-2026-03-2000011011ACN-2026-03-4000123950 | 21 |  | 26 | 80 | 0 | 0 | 28
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | SOP adherence is strengthened by Tool Box Talk. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123960 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | Visit completed in and around TTG, Scrapyard, TTPH, Control room, Security room, Admin - Housekeeping found satisfactory. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1656 | DURGAPUR DEPOT | SOP adherence to be strengthened | SOD | Marketing | EZ | 2026-03-09 | INSUFFICIENT SUPERVISION | 5 | EMERGENCY | S1 | F5 | 2026-03-09 | AUD-2026-03-2000011011ACN-2026-03-4000123960 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123960 | 2026-08-07 13:00 | 73.2122 | 189 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123960 | 532 | 8294 | 21 | 8294 | 224 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011011ACN-2026-03-4000123960 |  | AUD-2026-03-2000011011ACN-2026-03-4000123960 | 21 |  | 26 | 80 | 0 | 0 | 27
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | Open projects are closed. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123961 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | Project progress was reviewed and depot ensured to close all the project within timeline. | 4.3 | Project progress reviewed | 1656 | DURGAPUR DEPOT | LIC to ensure closure of all the three open project by Mar'26 | SOD | Marketing | EZ | 2026-03-25 | POOR COMMUNICATION | 5 | EMERGENCY | S1 | F5 | 2026-03-25 | AUD-2026-03-2000011011ACN-2026-03-4000123961 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123961 | 2026-08-07 13:00 | 73.2122 | 205 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123961 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011011ACN-2026-03-4000123961 |  | AUD-2026-03-2000011011ACN-2026-03-4000123961 | 21 |  | 26 | 80 | 0 | 0 | 30
|  | HARAPRASAD GUCHHAIT | 2026-08-11 | VMS is working now. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143192 | Completed | HARAPRASAD GUCHHAIT | 2026-08-11 | Access control system found functional. It was noted that the VMS service is not operational. | 2.8 | Access control systems checked | 1656 | DURGAPUR DEPOT | VMS to be implemented. Nil case of visitors entry without VMS to be ensured | SOD | Marketing | EZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143192 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143192 | 2026-08-07 13:00 | 73.2122 | 302 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143192 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015091ACN-2026-07-4000143192 |  | AUD-2026-07-2000015091ACN-2026-07-4000143192 | 21 |  | 27 | 80 | 0 | 0 | 44
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | No action required as deflector is not required at that place. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-06-4000137703 | Closed | MD KASHIF | 2026-08-10 | Tankfarm fire fighting: Sprinkler system of Tk 201 found proper with no choked nozzles. One nozzle was having lost deflector unit. A replaced portion of the sprinkler ring found to be rusting from joints, as painting not done, post fabrication. | 6.12 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to get the painting done installing deflector unit. Ensue compliance | SOD | Marketing | PZR | 2026-07-15 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137703 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137703 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137703 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137703 | AUD-2026-06-2000012744ACN-2026-06-4000137703 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 |  | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-06-4000137705 | Closed |  |  | Fire alarm system: Hydrocarbon detectors found non functional. | 6.14 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure HCDs are made functional immediately. | SOD | Marketing | PZR | 2026-07-15 | FAILURE TO FOLLOW PROCEDURES | 8 | EMERGENCY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137705 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137705 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137705 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137705 | AUD-2026-06-2000012744ACN-2026-06-4000137705 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 |  | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-06-4000137707 | Closed |  |  | Boundary wall: Creepers found engulfing concertina coil of boundary wall on the backside of bitumen drum yard | 6.16 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to remove creepers on concertina coil of boundary wall on the backside of bitumen drum yard | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137707 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137707 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137707 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137707 | AUD-2026-06-2000012744ACN-2026-06-4000137707 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-06-4000137709 | Closed | MD KASHIF | 2026-08-10 | Stake holder interaction: A meeting was held with around 25 Dealers and DCTs to know their grievances/ expectations. Impact of autoDC on subsequent load, philosophy of OLA, proper locking (pre and post unloading OTP), blocking of TTs due to VTS violation, etc. were discussed. Feedback on their expectations, if any, were asked, to which no response was received. Dealers were also requested tovisit location frequently and witness for themselves location’s TT loading. They were also requested to share information on suspected places of stoppages of TTs with location so that location can take up with Administration. | 6.18 | Quarterly Inspection | 1742 | BOKARO DEPOT | Ensure dealer engagement programms arfe conducted on regualr intervals in depot. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | EMERGENCY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137709 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137709 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137709 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137709 | AUD-2026-06-2000012744ACN-2026-06-4000137709 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-06-4000137712 | Closed | MD KASHIF | 2026-08-10 | Interaction with officers: Officers were interacted with on KPI parameters and various location performance parameters. | 6.21 | Quarterly Inspection | 1742 | BOKARO DEPOT | LIC to review KPIs of officers on regular basis. | SOD | Marketing | PZR | 2026-07-15 | FATIGUE AND STRESS | 8 | ENVIRONMENTAL | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137712 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137712 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137712 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137712 | AUD-2026-06-2000012744ACN-2026-06-4000137712 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | Registers are being reviewed regularly | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-06-4000137713 | Closed | MD KASHIF | 2026-08-10 | Records: Periodic safety checklists were reviewed. Some of these are not being maintained since March 2025. Even the entries are not proper against some of the points. | 6.22 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location officers are requested to review the registers weekly basis for taking corrective action and inform updation on timely manner. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137713 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137713 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137713 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137713 | AUD-2026-06-2000012744ACN-2026-06-4000137713 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-06-4000137714 | Closed | MD KASHIF | 2026-08-10 | Ethanol Blending was found to be 18% from the sample taken from gantry. | 6.23 | Quarterly Inspection | 1742 | BOKARO DEPOT | Blending can improve to 18.5% LIC to ensure the same. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | ENVIRONMENTAL | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137714 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137714 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137714 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137714 | AUD-2026-06-2000012744ACN-2026-06-4000137714 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-06-4000137711 | Closed | MD KASHIF | 2026-08-10 | Stake holder interaction: An interactive session was held with Contract workmen and security, where in stop work, unsafe condition,unsafe act, near miss, etc. were explained. Our expectations were conveyed and their expectations were also sought. They have requested for making provision of toilet in TW siding, which is far off from main working area. | 6.20 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to look into the demands and mtake suitable action. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137711 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137711 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137711 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137711 | AUD-2026-06-2000012744ACN-2026-06-4000137711 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | MD KASHIF | 2026-08-10 | Will be ensured hereafter | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24QUARTERLY INSPECTION | ACN-2026-06-4000137715 | Closed | MD KASHIF | 2026-08-10 | Registers had multiple correction pen being used. To be avoided and instead wrong entries to be strike off. | 6.24 | Quarterly Inspection | 1742 | BOKARO DEPOT | Officers to sensitize the depot staffs to avoid using whiteners and cancel the wrong entries instead. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137715 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137715 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137715 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137715 | AUD-2026-06-2000012744ACN-2026-06-4000137715 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
|  | GAKHAR NAVEEN | 2026-08-11 | Servicing of the Monitor near TK 03 done. Windsock changed | ZONAL VISIT REPORT 17.02.2026 VASHI BOT | 2026-02-17 | AUD-2026-03-2000011166 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123410 | Completed | GAKHAR NAVEEN | 2026-08-11 | Fire Extinguisher, Water cum foam monitors, MEFGs operated by officers and found working satisfactorily , TK tk02, 03 & TK 06 operated | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 3562 | VASHI BO TML | Servicing of the Monitor near TK 03 to be done. Windsock to be changed | SOD | Marketing | WZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-15 | AUD-2026-03-2000011166ACN-2026-03-4000123410 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011166ACN-2026-03-4000123410 | 2026-09-15 | 34.7538 | 195 | >20 | AUD-2026-03-2000011166 - ACN-2026-03-4000123410 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011166ACN-2026-03-4000123410 |  | AUD-2026-03-2000011166ACN-2026-03-4000123410 | 21 |  | 26 | 80 | 9 | 9 | 28
LINGAMPALLI SRIHARSHA | 2026-08-11 |  |  | Dyke valve checked during Safety PLC visit and found to be working condition | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000133469 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Checked HVLRs no. 4 at Tank P5 . Foam Monitor ,MEFG , HCD, were checked at TK D1. All functioning found OK. . Dyke Valve indicator were checked at TK D1 and alarm activation is delayed . | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1915 | RAMAGUNDAM DEPOT | Dyke valve indicator alarm to generate immediately on opening of first thread of the valve, to rectify. | SOD | Marketing | SCR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012788ACN-2026-06-4000133469 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133469 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133469 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133469 | AUD-2026-06-2000012788ACN-2026-06-4000133469 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | Security Naresh has HVD | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000133470 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Location does not have any trained personnel with HVD/HZA Endorsement | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1915 | RAMAGUNDAM DEPOT | Location to get security/ Other staff to get HVD/HZA endorsement for movingTT 50–100m in case of any emergency | SOD | Marketing | SCR | 2026-06-30 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012788ACN-2026-06-4000133470 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133470 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133470 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133470 | AUD-2026-06-2000012788ACN-2026-06-4000133470 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | TT dips are being checked by officers and corrective action taken | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000133471 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Two filled TTs dips checked at TT Gantry . TT no TS 29 T 0322 dips found ok for all the 4 compartments, TT no TG 22-T 2295 excess of 2.0 cms observed in Compartment 3 . | 3.2 | Post-loading dip checks verified | 1915 | RAMAGUNDAM DEPOT | Officers to check TT dips regularly and corrective action to be taken for any deviations | SOD | Marketing | SCR | 2026-05-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-06-2000012788ACN-2026-06-4000133471 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133471 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133471 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133471 | AUD-2026-06-2000012788ACN-2026-06-4000133471 | 21 | 21 | 27 | 80 | 2 | 2 | 39 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | Ethanol blending deviation is being monitored daily and updated to HQO | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000133472 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Blending % checked for two TTs TG 22 T2295 and TG22T1025 Blending % observed 18%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1915 | RAMAGUNDAM DEPOT | Officers to check ethanol blending % periodically and take corrective action for any deviation | SOD | Marketing | SCR | 2026-05-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-06-2000012788ACN-2026-06-4000133472 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133472 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133472 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133472 | AUD-2026-06-2000012788ACN-2026-06-4000133472 | 21 | 21 | 27 | 80 | 2 | 2 | 39 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | Fire engine level tube replaced | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133477 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Fire Engines HSD tanks level tubes found to be opaque | 6.2 |  | 1915 | RAMAGUNDAM DEPOT | Fire Engines HSD tanks level tubes found to be opaque , to be replaced. | SOD | Marketing | SCR | 2026-06-05 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-05 | AUD-2026-06-2000012788ACN-2026-06-4000133477 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133477 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133477 | 532 | 8294 | 21 | 8294 | 136 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133477 | AUD-2026-06-2000012788ACN-2026-06-4000133477 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 |  |  | Fire buckets dry sand replenished | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133478 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Fire buckets found empty near the 100 KW solar plant | 6.3 |  | 1915 | RAMAGUNDAM DEPOT | Fire buckets dry sand to be relenished | SOD | Marketing | SCR | 2026-05-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-06-2000012788ACN-2026-06-4000133478 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133478 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133478 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133478 | AUD-2026-06-2000012788ACN-2026-06-4000133478 | 21 | 21 | 27 | 80 | 2 | 2 | 39 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | Strainer cleaning updated | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133480 | Closed | KESHETTI SAI MANISH | 2026-08-11 | Strainers cleaning due date mentioned as 16/05/2026 | 6.5 |  | 1915 | RAMAGUNDAM DEPOT | Strainers cleaning due date mentioned as 16/05/2026 , to be updated | SOD | Marketing | SCR | 2026-05-31 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-06-2000012788ACN-2026-06-4000133480 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133480 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133480 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133480 | AUD-2026-06-2000012788ACN-2026-06-4000133480 | 21 | 21 | 27 | 80 | 2 | 2 | 39 | 50
LINGAMPALLI SRIHARSHA | 2026-08-11 | KESHETTI SAI MANISH | 2026-08-11 | SOP boards in tank farm area replaced | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133481 | Closed | KESHETTI SAI MANISH | 2026-08-11 | SOP Boards faded in tank farm area | 6.6 |  | 1915 | RAMAGUNDAM DEPOT | SOP Boards faded in tank farm area , to be updated. | SOD | Marketing | SCR | 2026-07-31 | NATURAL DISASTERS OR UNFORESEEN EVENTS | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-06-2000012788ACN-2026-06-4000133481 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133481 | 2026-08-26 18:00 | 54.0038 | 344 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133481 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133481 | AUD-2026-06-2000012788ACN-2026-06-4000133481 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 50
MEHETRE KIRAN K | 2026-08-12 | PRITAM ANIL SURYAWANSHI | 2026-08-12 | All camera's are up now. | ZONAL VISIT REPORT 14.02.2026 MANMAD IRD | 2026-02-14 | AUD-2026-03-2000011117 | 2026-02-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122462 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Yes, VA alerts are checked and anlysed regularly, 13 CCTVs in VA are working & 47 are non-working in VA. | 2.7 | VA alerts checked / analysed | 1397 | HPCL MANMAD IRD | Location to find out root cause for 47 non-working VA & take up with vendor to resolve the issue | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S2 | F3 | 2026-03-31 | AUD-2026-03-2000011117ACN-2026-03-4000122462 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011117ACN-2026-03-4000122462 | 2026-09-08 | 41.7538 | 345 | >20 | AUD-2026-03-2000011117 - ACN-2026-03-4000122462 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011117ACN-2026-03-4000122462 | AUD-2026-03-2000011117ACN-2026-03-4000122462 | 21 | 21 | 26 | 80 | 7 | 7 | 31 | 50
MEHETRE KIRAN K | 2026-08-12 | PRITAM ANIL SURYAWANSHI | 2026-08-12 | sprinkler nozzle's cleaned. | ZONAL VISIT REPORT 14.02.2026 MANMAD IRD | 2026-02-14 | AUD-2026-03-2000011117 | 2026-02-14 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122463 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Fire Extinguisher, Water cum foam monitors, MEFGs operated by officers and found wo king satisfactorily , TK tk03, 04, tk05 & 06 and Tk 15 operated | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1397 | HPCL MANMAD IRD | Few Nozzels at upper ring & lower ring were found chocked in TK 03,04 ,05 & 06 | SOD | Marketing | WZ | 2026-03-07 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-07 | AUD-2026-03-2000011117ACN-2026-03-4000122463 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011117ACN-2026-03-4000122463 | 2026-09-08 | 41.7538 | 345 | >20 | AUD-2026-03-2000011117 - ACN-2026-03-4000122463 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011117ACN-2026-03-4000122463 | AUD-2026-03-2000011117ACN-2026-03-4000122463 | 21 | 21 | 26 | 80 | 7 | 7 | 27 | 50
MEHETRE KIRAN K | 2026-08-12 | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Training imparted to all concerned person. | ZONAL VISIT REPORT 14.02.2026 MANMAD IRD | 2026-02-14 | AUD-2026-03-2000011117 | 2026-02-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122464 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Troley to be placed at a level ground with easily acessible & all specified items in respective compartments | 6.1 | Emergency trolyy condition checked | 1397 | HPCL MANMAD IRD | Avarness & Training of all equipments available in trolley to be given all location team members | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-03-31 | AUD-2026-03-2000011117ACN-2026-03-4000122464 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011117ACN-2026-03-4000122464 | 2026-09-08 | 41.7538 | 345 | >20 | AUD-2026-03-2000011117 - ACN-2026-03-4000122464 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011117ACN-2026-03-4000122464 | AUD-2026-03-2000011117ACN-2026-03-4000122464 | 21 | 21 | 26 | 80 | 7 | 7 | 31 | 50
MEHETRE KIRAN K | 2026-08-12 | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Issue checked by OEM and rectified. | ZONAL VISIT REPORT 14.02.2026 MANMAD IRD | 2026-02-14 | AUD-2026-03-2000011117 | 2026-02-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122465 | Closed | PRITAM ANIL SURYAWANSHI | 2026-08-12 | Lube oil pressure was around 2.5 KG , to be checked up by OEM | 6.4 | Fire engines opearted for 30 minutes | 1397 | HPCL MANMAD IRD | Lube oil pressure to be checked by OEM | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-03-31 | AUD-2026-03-2000011117ACN-2026-03-4000122465 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011117ACN-2026-03-4000122465 | 2026-09-08 | 41.7538 | 345 | >20 | AUD-2026-03-2000011117 - ACN-2026-03-4000122465 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011117ACN-2026-03-4000122465 | AUD-2026-03-2000011117ACN-2026-03-4000122465 | 21 | 21 | 26 | 80 | 7 | 7 | 31 | 50
SATHYAJITH A. | 2026-08-12 | KUMAR MANISH | 2026-08-11 | Issue taken up with M/s AST for resolution. LRC HSB is now synchronizing. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130050 | Closed | KUMAR MANISH | 2026-08-11 | LRC HSB is not synchronizing. Issue taken up with M/s AST for resolution. However, required action is pending from M/s AST. | 1.3 | Pending issues reviewed | 1424 | JABALPUR DEPOT | To be taken up with M/s AST for resolution at the earliest. (To be completed within 1 week) | SOD | Marketing | CEN | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012101ACN-2026-05-4000130050 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130050 | 2026-09-26 17:30 | 23.0247 | 345 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130050 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012101ACN-2026-05-4000130050 | AUD-2026-05-2000012101ACN-2026-05-4000130050 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 50
SATHYAJITH A. | 2026-08-12 | KUMAR MANISH | 2026-08-12 | TT (TT NO: RJ09 GE 5735) has be recalibrated before giving next load. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130052 | Closed | KUMAR MANISH | 2026-08-12 | Yes, verified. 3 mm excess observed in TT No: RJ09 GE 5735 | 3.2 | Post-loading dip checks verified | 1424 | JABALPUR DEPOT | The said TT (TT NO: RJ09 GE 5735) to be recalibrated before giving next load. | SOD | Marketing | CEN | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012101ACN-2026-05-4000130052 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130052 | 2026-09-26 17:30 | 23.0247 | 345 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130052 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012101ACN-2026-05-4000130052 | AUD-2026-05-2000012101ACN-2026-05-4000130052 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 50
SATHYAJITH A. | 2026-08-12 | KUMAR MANISH | 2026-08-12 | Boundary wall adjoining to IOCL plastering has been Complted.i | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130053 | Closed | KUMAR MANISH | 2026-08-12 | Boundary wall adjoining to IOCL is done. Plastering is to be done. Vegetation is under control. | 3.16 | Earth pits / boundary / vegetation control checked | 1424 | JABALPUR DEPOT | To be taken up with IOCL for expediting completion of wall plastering. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-05-2000012101ACN-2026-05-4000130053 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130053 | 2026-09-26 17:30 | 23.0247 | 345 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130053 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012101ACN-2026-05-4000130053 | AUD-2026-05-2000012101ACN-2026-05-4000130053 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 50
SATHYAJITH A. | 2026-08-12 | KUMAR MANISH | 2026-08-12 | Location is regular havining the Mreeting with the OMC and The railways in order to maintain coordial relation with local Railwaysfor ensuring placement of our rakes on priority. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130055 | Closed | KUMAR MANISH | 2026-08-12 | Had interaction with BPCL Depot Incharge at Jabalpur. Also, met ADOM-WCR and Chief Controller of Rlys-WCR, Jabalpur Division duringlocation visit. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1424 | JABALPUR DEPOT | Location is advised to maintain coordial relation with local Railways for ensuring placement of our rakes on priority.. | SOD | Marketing | CEN | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012101ACN-2026-05-4000130055 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130055 | 2026-09-26 17:30 | 23.0247 | 345 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130055 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012101ACN-2026-05-4000130055 | AUD-2026-05-2000012101ACN-2026-05-4000130055 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 50
SATHYAJITH A. | 2026-08-12 | KUMAR MANISH | 2026-08-11 | Location is advised to pursue following 2 projects: 1) Construction of 3 x 180 KL UG Tanks- Proposal has been Submiited to Zone. 2) Construction of 4500 KL A/G HSD Tank- Proposal has been Prosured but it Has been Kept on hold and will be pursue in the futrure.As current required is not there. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130056 | Closed | KUMAR MANISH | 2026-08-11 | Nil | 6.1 | High priority areas requiring immediate action. | 1424 | JABALPUR DEPOT | Location is advised to pursue following 2 projects: 1) Construction of 3 x 180 KL UG Tanks 2) Construction of 4500 KL A/G HSD Tank | SOD | Marketing | CEN | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-31 | AUD-2026-05-2000012101ACN-2026-05-4000130056 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130056 | 2026-09-26 17:30 | 23.0247 | 345 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130056 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012101ACN-2026-05-4000130056 | AUD-2026-05-2000012101ACN-2026-05-4000130056 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Training programme for security Organized for all security guards and practice done in field. Training programme for Contract staff organized and practice done in field. | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123400 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes conducted | 2.1 | Fire drill conducted in last 6 months (surprise) | 1588 | VASHI WHITE OIL TERMINAL | Response time in operation of WFM to be improved | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123400 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123400 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123400 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123400 | AUD-2026-03-2000011165ACN-2026-03-4000123400 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Training Programme organised for Security Guards and Contract staff on Scaba usage and precautions to be taken | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123401 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes conducted | 2.2 | Double contingency scenario simulated; observations recorded | 1588 | VASHI WHITE OIL TERMINAL | It to be ensured that Oxygen level to be checked before wearing the Scaba kit | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123401 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123401 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123401 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123401 | AUD-2026-03-2000011165ACN-2026-03-4000123401 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Regular check with Lux meter being done every month and records being maintained | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123402 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1588 | VASHI WHITE OIL TERMINAL | regularly check should be done with lux meter | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123402 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123402 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123402 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123402 | AUD-2026-03-2000011165ACN-2026-03-4000123402 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Camera alignment checked by Vendor and corrected | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123403 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes | 2.6 | CCTV functioning checked | 1588 | VASHI WHITE OIL TERMINAL | CAMERA ALIGNMENT TO BE DONE | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123403 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123403 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123403 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123403 | AUD-2026-03-2000011165ACN-2026-03-4000123403 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | HVLR malfunctioning corrected. | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123406 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1588 | VASHI WHITE OIL TERMINAL | 3 HVLR MOV MALFUNCTIONING,OEM CONTACTED FOR RECTIFICATION | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123406 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123406 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123406 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123406 | AUD-2026-03-2000011165ACN-2026-03-4000123406 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Training programme conducted | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123408 | Closed | GAKHAR NAVEEN | 2026-08-11 | yes conducted | 2.15 | TT crew roadside emergency procedures checked | 1588 | VASHI WHITE OIL TERMINAL | training programmand refresher course to be organized | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123408 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123408 | 2026-10-14 | 5.7538 | 345 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123408 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123408 | AUD-2026-03-2000011165ACN-2026-03-4000123408 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | rectification done | ZONAL VISIT REPORT 17.02.2026 VASHI BOT | 2026-02-17 | AUD-2026-03-2000011166 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123413 | Closed | GAKHAR NAVEEN | 2026-08-11 | Lub oil pressure was around 5.4 KG, 5.2 Kg and 5.0 kg for FE 1, FE2 and FE3 respectively .Fire Engine No 3 having minute leakage | 6.4 | Fire engines opearted for 30 minutes | 3562 | VASHI BO TML | Leakage in FE No 3 to be arrested | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | OCCUPATIONAL HEALTH | S1 | F3 | 2026-03-31 | AUD-2026-03-2000011166ACN-2026-03-4000123413 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011166ACN-2026-03-4000123413 | 2026-09-15 | 34.7538 | 345 | >20 | AUD-2026-03-2000011166 - ACN-2026-03-4000123413 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011166ACN-2026-03-4000123413 | AUD-2026-03-2000011166ACN-2026-03-4000123413 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 50
NARAYANE KISHORKUMAR SUDAM | 2026-08-12 | GAKHAR NAVEEN | 2026-08-11 | Vegegation cleaning done | ZONAL VISIT REPORT 17.02.2026 VASHI BOT | 2026-02-17 | AUD-2026-03-2000011166 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123411 | Closed | GAKHAR NAVEEN | 2026-08-11 | Taken full field round & found all satisfactory.Green vegetation near scrap yard to be cleaned | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 3562 | VASHI BO TML | Green Vegetaion near scrap yard to be cleaned | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | OCCUPATIONAL HEALTH | S1 | F3 | 2026-03-31 | AUD-2026-03-2000011166ACN-2026-03-4000123411 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011166ACN-2026-03-4000123411 | 2026-09-15 | 34.7538 | 345 | >20 | AUD-2026-03-2000011166 - ACN-2026-03-4000123411 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011166ACN-2026-03-4000123411 | AUD-2026-03-2000011166ACN-2026-03-4000123411 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 50
SUJEET KUMAR | 2026-08-12 | SAXENA UMESH CHANDRA | 2026-08-12 | Accumulated scrap items have been segregated and their valuation has also been completed. The valuation report dated 08.08.2026 is attached for reference. Committee formation is under progress. Thereafter, inspection, preparation of the report and initiation of the RFD process shall be undertaken. The material is expected to be disposed of within two months. Since necessary action has already been initiated towards disposal of the accumulated scrap, the audit observation may kindly be treated as complied with. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000135386 | Closed | SAXENA UMESH CHANDRA | 2026-08-12 | Miscellaneous screp items available at location to be disposed off on priority. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1457 | INDORE DEPOT | RFD to be initiated for disposing of accumulated scrap items. | SOD | Marketing | CEN | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 9 | OCCUPATIONAL HEALTH | S3 | F3 | 2026-09-30 | AUD-2026-06-2000012547ACN-2026-06-4000135386 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135386 | 2026-09-09 19:00 | 39.9622 | 345 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135386 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012547ACN-2026-06-4000135386 | AUD-2026-06-2000012547ACN-2026-06-4000135386 | 21 | 21 | 27 | 80 | 0 | -3 | 57 | 50
[5 empty] | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147388 | Open |  |  | The location shall take up with Renewable department of HQO for exploration of installation of new solar panels at Meerut Depot | 6.3 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016227ACN-2026-08-4000147388 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147388 | 2026-09-25 19:00 | 23.9622 | 364 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147388 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016227ACN-2026-08-4000147388 |  | AUD-2026-08-2000016227ACN-2026-08-4000147388 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147339 | Open |  |  | Earlier action points were discussed with team | 1.4 | Earlier action points status checked | 1128 | MATHURA TERMINAL | To be complied in time bound manner. | SOD | Marketing | NUZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-08-2000016610ACN-2026-08-4000147339 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147339 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147339 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147339 |  | AUD-2026-08-2000016610ACN-2026-08-4000147339 | 21 |  | 27 | 80 | 14 | 13 | 57
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147340 | Open |  |  | Refer Annexure 1 | 1.8 | Improvement plans discussed | 1128 | MATHURA TERMINAL | Detailed action plan to be submitted. | SOD | Marketing | NUZ | 2026-10-31 |  | 4 |  | S1 | F4 | 2026-10-31 | AUD-2026-08-2000016610ACN-2026-08-4000147340 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147340 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147340 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147340 |  | AUD-2026-08-2000016610ACN-2026-08-4000147340 | 21 |  | 27 | 80 | 14 | 13 | 61
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147344 | Open |  |  | Yes | 3.18 | OISD/MDSA/SSA compliance reviewed | 1128 | MATHURA TERMINAL | Pending poitns to be complied in time bound manner. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147344 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147344 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147344 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147344 |  | AUD-2026-08-2000016610ACN-2026-08-4000147344 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147345 | Open |  |  | yes, working | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1128 | MATHURA TERMINAL | All scrap to be disposed off. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147345 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147345 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147345 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147345 |  | AUD-2026-08-2000016610ACN-2026-08-4000147345 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147346 | Open |  |  | Prover unloading is with hoses and is obstructing trucks movement | 6.1 |  | 1128 | MATHURA TERMINAL | permanent arrangement to be made | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147346 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147346 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147346 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147346 |  | AUD-2026-08-2000016610ACN-2026-08-4000147346 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147347 | Open |  |  | many places pedestals are corroded or broken clearance with ground is not meeting | 6.2 | NIL | 1128 | MATHURA TERMINAL | To place new pedestals with the in house scrap if possible so as clearance from ground is maintained. | SOD | Marketing | NUZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-08-2000016610ACN-2026-08-4000147347 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147347 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147347 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147347 |  | AUD-2026-08-2000016610ACN-2026-08-4000147347 | 21 |  | 27 | 80 | 14 | 13 | 57
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147348 | Open |  |  | many places product pipelines also corroded at bottom , may develop leaks too | 6.3 | NIL | 1128 | MATHURA TERMINAL | Immediate steps such as paintaing . Replacing of portion of pipeline to be done to arrest any leaks. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147348 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147348 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147348 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147348 |  | AUD-2026-08-2000016610ACN-2026-08-4000147348 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147349 | Open |  |  | inside terminal many places found cross overs are corroded and not safe to walk on | 6.4 | NIL | 1128 | MATHURA TERMINAL | Hence pls arrange for the new cross overs or paint the cross overs immediately. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147349 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147349 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147349 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147349 |  | AUD-2026-08-2000016610ACN-2026-08-4000147349 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147800 | Open |  |  | As truck after leaving R3 still in geo fence hence trip is not starting . | 6.5 | NIL | 1128 | MATHURA TERMINAL | Need to coordinate with vendor to correct this anamoly. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-08-2000016610ACN-2026-08-4000147800 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147800 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147800 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016610ACN-2026-08-4000147800 |  | AUD-2026-08-2000016610ACN-2026-08-4000147800 | 21 |  | 27 | 80 | 14 | 13 | 83
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Budget allocation request sent | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130267 | Closed | KAMLESH SAHU | 2026-08-09 | MEB budget in some CEs as per SSA jobs & addl. Jobs undertaken by location | 1.5 | HQO / Zonal support required identified | 1528 | RAIPUR IRD-II | FLM send by location for additional budget with justification | SOD | Marketing | ECZ | 2026-06-15 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-06-15 | AUD-2026-05-2000012405ACN-2026-05-4000130267 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130267 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130267 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012405ACN-2026-05-4000130267 | AUD-2026-05-2000012405ACN-2026-05-4000130267 | 21 | 21 | 27 | 80 | 3 | 3 | 41 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Some of the left over jobs has completed before 31 March 26. Some will be initiated after allocation of budget for pending E&P & OISD Observation. Budget proposal sent to HQO | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127184 | Closed | KAMLESH SAHU | 2026-08-10 | To expedite all the pending/leftover jobs by E&P, in view of proposed ESA Audit. | 1.8 | Improvement plans discussed | 1528 | RAIPUR IRD-II | Completion of leftover jobs by E&P | SOD | Marketing | ECZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011236ACN-2026-03-4000127184 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127184 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127184 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127184 | AUD-2026-03-2000011236ACN-2026-03-4000127184 | 21 | 21 | 26 | 80 | 3 | 3 | 44 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Location is completed the pending action required against the pending observations | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127193 | Closed | KAMLESH SAHU | 2026-08-10 | OISD Audit is conducted in Feb' 2026. MDSA/Comprehensive Status - Not yet conducted. Self Safety Audit - 03 sept to 8 Sept' 25 (Total observation - 63, Out of which 57 are closed). PNGRB T4S Audit Status - T4S is scheduled to be conducted in the month of March’ 26. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1528 | RAIPUR IRD-II | Expediting completion of pending audit observations points | SOD | Marketing | ECZ | 2026-06-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S4 | F1 | 2026-06-30 | AUD-2026-03-2000011236ACN-2026-03-4000127193 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127193 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127193 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011236ACN-2026-03-4000127193 | AUD-2026-03-2000011236ACN-2026-03-4000127193 | 21 | 21 | 26 | 80 | 3 | 3 | 44 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Budget allocation request sent | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130281 | Closed | KAMLESH SAHU | 2026-08-10 | Lot of project material is found scattered and also some projectjobs found incomplete. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1528 | RAIPUR IRD-II | All project surplus material to be segregated . Also pending project jobs to be completed and budget for same to be sought from projects or HQO | SOD | Marketing | ECZ | 2026-07-01 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-05-2000012405ACN-2026-05-4000130281 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130281 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130281 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130281 | AUD-2026-05-2000012405ACN-2026-05-4000130281 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Proposal and Budget requestsent to HQO | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130283 | Closed | KAMLESH SAHU | 2026-08-10 | Parking area pending project jobs , pending project activities inside depot to be completed | 4.3 | Project progress reviewed | 1528 | RAIPUR IRD-II | Parking area pending project activities budget details to be provided . | SOD | Marketing | ECZ | 2026-07-31 | THIRD PARTY ERRORS | 3 | PROCESS SAFETY | S3 | F1 | 2026-07-31 | AUD-2026-05-2000012405ACN-2026-05-4000130283 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130283 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130283 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130283 | AUD-2026-05-2000012405ACN-2026-05-4000130283 | 21 | 21 | 27 | 80 | 3 | 3 | 48 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Budget Proposal request sent | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130285 | Closed | KAMLESH SAHU | 2026-08-10 | Visitor room & TT crew waiting area is not available in new depot | 6.1 | Visitor room & TT crew shed | 1528 | RAIPUR IRD-II | same need to be identified and budget request to be given | SOD | Marketing | ECZ | 2026-06-30 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130285 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130285 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130285 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130285 | AUD-2026-05-2000012405ACN-2026-05-4000130285 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Budget allocation request sent | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130286 | Closed | KAMLESH SAHU | 2026-08-10 | Same is shifted but are of insufficient capacity . | 6.2 | Car /scooter parking shed for employees | 1528 | RAIPUR IRD-II | Parking shed required for min. 10 cars and 30 2 wheelers . Budget requirement to be given | SOD | Marketing | ECZ | 2026-06-30 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130286 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130286 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130286 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130286 | AUD-2026-05-2000012405ACN-2026-05-4000130286 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 50
YADAV GIRISH KUMAR | 2026-08-14 | KAMLESH SAHU | 2026-08-10 | Budget allocation request sent | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130288 | Closed | KAMLESH SAHU | 2026-08-10 | No STP provided for office or driver amenity , which is must requirement for any Industry | 6.4 | STP | 1528 | RAIPUR IRD-II | Budget request to be given | SOD | Marketing | ECZ | 2026-06-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130288 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130288 | 2026-08-28 18:00 | 52.0038 | 347 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130288 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012405ACN-2026-05-4000130288 | AUD-2026-05-2000012405ACN-2026-05-4000130288 | 21 | 21 | 27 | 80 | 3 | 3 | 44 | 50
CHANDRAKANTH JOSHI | 2026-08-14 | ROY TAVARES | 2026-08-14 | Trained persons with Hazardous Validity have been identified 1.RAVICHANDRA 2.CHANDRAKANT 3.SHARAN KUMAR 4.VISHWANATH | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138576 | Closed | ROY TAVARES | 2026-08-14 | Not available . | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1797 | GULBARGA NEW IRD | Advised LIC to develop few persons for this HVD/HZA endorsement | SOD | Marketing | SWZ | 2026-07-31 | HARSH WORKING CONDITIONS | 4 | EMERGENCY | S2 | F2 | 2026-07-31 | AUD-2026-06-2000013300ACN-2026-06-4000138576 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138576 | 2026-08-19 18:00 | 61.0038 | 347 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138576 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138576 | AUD-2026-06-2000013300ACN-2026-06-4000138576 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 50
CHANDRAKANTH JOSHI | 2026-08-14 | ROY TAVARES | 2026-08-14 | 1. Dip eliminationa activity has been completed 2. 2 nos af open ARS have been closed | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138567 | Closed | ROY TAVARES | 2026-08-14 | 1.Dip Elimination: Dip elimination is pending. The process is started from 18.05.2026. After data collection completion on 17.06.2026, file note will be initiated and approval will be taken. 2.NPCB Projects due as on 31.03.2026: Bottom Loading: RMU Commissioning is pending and to be completed by 20.06.2026. VHF Sets procurement: Items received, installation completed, capitalization pending. Commissioning bill is to be submitted by vendor. After that capitalization will be done. To be completed by 30.05.2026. | 1.3 | Pending issues reviewed | 1797 | GULBARGA NEW IRD | 1. Location to expedite and achieve dip elimination at the earliest. 2. To expediate the closure of 2 AR's as per target date of 30.06.2026 | SOD | Marketing | SWZ | 2026-08-31 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S4 | F2 | 2026-08-31 | AUD-2026-06-2000013300ACN-2026-06-4000138567 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138567 | 2026-08-19 18:00 | 61.0038 | 347 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138567 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138567 | AUD-2026-06-2000013300ACN-2026-06-4000138567 | 21 | 21 | 27 | 80 | 5 | 5 | 52 | 50
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147004 | Open |  |  | Pending issues and compliances, Projects status, and the status of action points from the last BCM reviewed | 1.3 | Pending issues reviewed | 1953 | RAJAHMUNDRY TERMINAL | Hydrant line project to be completed within approved timeline, TT Branding of 39 out of 92 TT done, TT branding to be increased andcompleted 100% | SOD | Marketing | SCR | 2026-10-31 |  | 6 |  | S3 | F2 | 2026-10-31 | AUD-2026-08-2000016362ACN-2026-08-4000147004 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147004 | 2026-07-22 18:30 | 88.983 | 425 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147004 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147004 |  | AUD-2026-08-2000016362ACN-2026-08-4000147004 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147005 | Open |  |  | Pending points and status of SSA & MDSA | 1.4 | Earlier action points status checked | 1953 | RAJAHMUNDRY TERMINAL | Action to be taken on the pending SSA & MDSA Points. Self Safety audit- 2 points , MDSA- 6 points | SOD | Marketing | SCR | 2026-10-31 |  | 6 |  | S2 | F3 | 2026-10-31 | AUD-2026-08-2000016362ACN-2026-08-4000147005 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147005 | 2026-07-22 18:30 | 88.983 | 425 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147005 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147005 |  | AUD-2026-08-2000016362ACN-2026-08-4000147005 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147006 | Open |  |  | Yes. 3 CCTVs are under outage and as confirmed by location they have been declared non reparable by vendor. camera angle was not aligned for boundary perimeter camera | 2.6 | CCTV functioning checked | 1953 | RAJAHMUNDRY TERMINAL | New camera to be procured, scope of common tender for zone to be explored and done. | SOD | Marketing | SCR | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-08-2000016362ACN-2026-08-4000147006 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147006 | 2026-07-22 18:30 | 88.983 | 425 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147006 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147006 |  | AUD-2026-08-2000016362ACN-2026-08-4000147006 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147007 | Open |  |  | HVLR, HCD, Foam Monitor, MEFG operation checked and found working properly. 2 no DCPs near tank TK3C were checked and both did not operate as the nozzle was found choked. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1953 | RAJAHMUNDRY TERMINAL | DCP Servicing to be done as per given timeline, DCP near Tank TK3C to be checked and made functional. | SOD | Marketing | SCR | 2026-08-07 |  | 5 |  | S1 | F5 | 2026-08-07 | AUD-2026-08-2000016362ACN-2026-08-4000147007 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147007 | 2026-07-22 18:30 | 88.983 | 340 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147007 | 532 | 8294 | 21 | 8294 | 73 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016362ACN-2026-08-4000147007 |  | AUD-2026-08-2000016362ACN-2026-08-4000147007 | 21 |  | 27 | 80 | 1 | 2 | 49
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147008 | Open |  |  | TTs AP39TH0225, AP39TE4799 checked. | 3.1 | TT fittings & discipline checked | 1953 | RAJAHMUNDRY TERMINAL | Surprise TT checking to be carried out for those TT's which are getting shortages | SOD | Marketing | SCR | 2026-08-15 |  | 9 |  | S3 | F3 | 2026-08-15 | AUD-2026-08-2000016362ACN-2026-08-4000147008 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147008 | 2026-07-22 18:30 | 88.983 | 348 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147008 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147008 |  | AUD-2026-08-2000016362ACN-2026-08-4000147008 | 21 |  | 27 | 80 | 1 | 2 | 50
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147009 | Open |  |  | Dips of 2 TT s checked. 1. AP39TE4799 (bay 03, all compartment found ok ), 2. AP39TH0225 (Bay 6 , Comp 2 -3 mm, Comp 3 +3 mm). | 3.2 | Post-loading dip checks verified | 1953 | RAJAHMUNDRY TERMINAL | Location to take corrective action | SOD | Marketing | SCR | 2026-08-07 |  | 6 |  | S2 | F3 | 2026-08-07 | AUD-2026-08-2000016362ACN-2026-08-4000147009 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147009 | 2026-07-22 18:30 | 88.983 | 340 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147009 | 532 | 8294 | 21 | 8294 | 73 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147009 |  | AUD-2026-08-2000016362ACN-2026-08-4000147009 | 21 |  | 27 | 80 | 1 | 2 | 49
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147010 | Open |  |  | 2 OISD, 6 MDSA and 2 SSA pending points to be closed. Pending points to be complied as per timelines | 3.18 | OISD/MDSA/SSA compliance reviewed | 1953 | RAJAHMUNDRY TERMINAL | Action to be taken on the pending MDSA, SSA Points. Location to take up for pending OISD points with HQO. | SOD | Marketing | SCR | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-08-2000016362ACN-2026-08-4000147010 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147010 | 2026-07-22 18:30 | 88.983 | 425 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147010 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147010 |  | AUD-2026-08-2000016362ACN-2026-08-4000147010 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147011 | Open |  |  | Full field round of Gantry, tank farm/pump house//ETP/control room/security/admin was completed | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1953 | RAJAHMUNDRY TERMINAL | TK3A and TK3C painting to be completed. | SOD | Marketing | SCR | 2027-03-31 |  | 8 |  | S4 | F2 | 2027-03-31 | AUD-2026-08-2000016362ACN-2026-08-4000147011 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147011 | 2026-07-22 18:30 | 88.983 | 576 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147011 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147011 |  | AUD-2026-08-2000016362ACN-2026-08-4000147011 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147012 | Open |  |  | Location to initiate RFD for old hydrant line, other scrap at location to be segregated and scrap free environment to be made | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1953 | RAJAHMUNDRY TERMINAL | Location to take corrective action | SOD | Marketing | SCR | 2026-12-31 |  | 6 |  | S3 | F2 | 2026-12-31 | AUD-2026-08-2000016362ACN-2026-08-4000147012 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147012 | 2026-07-22 18:30 | 88.983 | 486 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147012 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016362ACN-2026-08-4000147012 |  | AUD-2026-08-2000016362ACN-2026-08-4000147012 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-08-4000147013 | Open |  |  | Closure of OISD, SSA/ MDSA Points, Scrap Liquidation, CCTV Cameras | 5.1 | High priority areas requiring immediate action. | 1953 | RAJAHMUNDRY TERMINAL | Location to take corrective action | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016362ACN-2026-08-4000147013 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147013 | 2026-07-22 18:30 | 88.983 | 425 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147013 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016362ACN-2026-08-4000147013 |  | AUD-2026-08-2000016362ACN-2026-08-4000147013 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-07-22 18:30 | AUD-2026-08-2000016362 | 2026-07-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147014 | Open |  |  | Lot of dust and dry leaves found at entrance of the admin bldg | 6 | Cleanliness in Admin Building | 1953 | RAJAHMUNDRY TERMINAL | Location to ensure proper housekeping | SOD | Marketing | SCR | 2026-07-23 |  | 5 |  | S1 | F5 | 2026-07-23 | AUD-2026-08-2000016362ACN-2026-08-4000147014 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016362ACN-2026-08-4000147014 | 2026-07-22 18:30 | 88.983 | 325 | >20 | AUD-2026-08-2000016362 - ACN-2026-08-4000147014 | 532 | 8294 | 21 | 8294 | 88 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016362ACN-2026-08-4000147014 |  | AUD-2026-08-2000016362ACN-2026-08-4000147014 | 21 |  | 27 | 80 | 1 | 2 | 47
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147015 | Open |  |  | Pending issues related to Trucks conversion to bottom loading, technical audit points compliance plan. | 1.3 | Pending issues reviewed | 1937 | SURYAPET TERMINAL | 100% TTs to be converted to Bottom Loading by October 2026 | SOD | Marketing | SCR | 2026-10-30 |  | 5 |  | S1 | F5 | 2026-10-30 | AUD-2026-08-2000016363ACN-2026-08-4000147015 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147015 | 2026-08-04 18:45 | 75.9726 | 424 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147015 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147015 |  | AUD-2026-08-2000016363ACN-2026-08-4000147015 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147016 | Open |  |  | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1937 | SURYAPET TERMINAL | Audit compliances to be completed as per given target dates | SOD | Marketing | SCR | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-08-2000016363ACN-2026-08-4000147016 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147016 | 2026-08-04 18:45 | 75.9726 | 486 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147016 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147016 |  | AUD-2026-08-2000016363ACN-2026-08-4000147016 | 21 |  | 27 | 80 | 0 | 0 | 70
|  |  |  | Few emergency trolley items are under procurement process | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147017 | Open | DAMARAKONDA VARSHITHA | 2026-09-08 | Reviewed emergency trolley equipment. Some of the items were found missing and not in the designated compartments. | 2.5 | Emergency response preparedness reviewed | 1937 | SURYAPET TERMINAL | Emergency Trolley items are not as per name plate. Some of the items viz FLP Search Lights are missing . BA refilling due date Aug 2025. To take corrective action for emergency trolley availability with all the required items. | SOD | Marketing | SCR | 2026-08-31 | FATIGUE AND STRESS | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016363ACN-2026-08-4000147017 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147017 | 2026-08-04 18:45 | 75.9726 | 364 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147017 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147017 |  | AUD-2026-08-2000016363ACN-2026-08-4000147017 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147021 | Open |  |  | MS Tank 1C and Ethanol Tank 2B Physical dip checked. TK1C physical dip 333.7.0 cms, water 0.5 cms , Temp 29.0 deg C against TAS dipof 334.2 cms. Water -0.5 cms Temp 29.9 degC, TK 2B Physical dip 698.5 cms , water nil, temp 31.0 deg C and TAS dip is 697.6 cms, water nil , temp - 30.9 deg C | 3.7 | Inventory physical dip of minimum two tanks taken | 1937 | SURYAPET TERMINAL | Location to take up with TAS vendor for corrective action | SOD | Marketing | SCR | 2026-08-20 |  | 5 |  | S1 | F5 | 2026-08-20 | AUD-2026-08-2000016363ACN-2026-08-4000147021 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147021 | 2026-08-04 18:45 | 75.9726 | 353 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147021 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147021 |  | AUD-2026-08-2000016363ACN-2026-08-4000147021 | 21 |  | 27 | 80 | 0 | 0 | 51
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147023 | Open |  |  | Critical alarms checked in CR, HHH, ESD, HCD, Bay reallocation, Cancellation, K-factor of BCU & MFM, and reviewed reasons., Observed erroneous tank leakage alarms to be taken up with Vendor & reasons to be shared. | 3.12 | Critical alarms checked & corrective actions reviewed | 1937 | SURYAPET TERMINAL | Location to take up with TAS vendor for corrective action on erroneous tank leakage alarms | SOD | Marketing | SCR | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016363ACN-2026-08-4000147023 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147023 | 2026-08-04 18:45 | 75.9726 | 364 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147023 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147023 |  | AUD-2026-08-2000016363ACN-2026-08-4000147023 | 21 |  | 27 | 80 | 0 | 0 | 52
|  |  |  | Old TAS assets auction will done in the 2nd week of september (15th), for disposal of TATA SUMO internal PO to be made | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147027 | Open | DAMARAKONDA VARSHITHA | 2026-09-08 | Old TAS related assets disposal to be completed RFD to be initiated for the remaining miscellaneous scrap at the location and the old TATA SUMO vehicle | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1937 | SURYAPET TERMINAL | Old TAS related assets disposal to be completed RFD to be initiated for the remaining miscellaneous scrap at the location and the old TATA SUMO vehicle | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016363ACN-2026-08-4000147027 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147027 | 2026-08-04 18:45 | 75.9726 | 394 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147027 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147027 |  | AUD-2026-08-2000016363ACN-2026-08-4000147027 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-08-4000147028 | Open |  |  | To follow up with VVSPL for MFM bases accounting | 5.1 | MFM based accounting at Pipeline and OMC location | 1937 | SURYAPET TERMINAL | To follow up with VVSPL for MFM basIs accounting | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016363ACN-2026-08-4000147028 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147028 | 2026-08-04 18:45 | 75.9726 | 394 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147028 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147028 |  | AUD-2026-08-2000016363ACN-2026-08-4000147028 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-08-4000147029 | Open |  |  | Hooter functioning to be checked regularly. | 5.2 | Functioning of all Hooters in control room - during regular checking , hooter initially was not working due to software glitch. | 1937 | SURYAPET TERMINAL | Hooter functioning to be checked regularly. | SOD | Marketing | SCR | 2026-08-10 |  | 5 |  | S1 | F5 | 2026-08-10 | AUD-2026-08-2000016363ACN-2026-08-4000147029 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147029 | 2026-08-04 18:45 | 75.9726 | 343 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147029 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147029 |  | AUD-2026-08-2000016363ACN-2026-08-4000147029 | 21 |  | 27 | 80 | 0 | 0 | 49
|  |  |  | Project proposal has been initiated for the modification of road for Ethanol TTs | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147030 | Open | DAMARAKONDA VARSHITHA | 2026-09-08 | The Ethanol TTs reversing to be avoided | 6.1 |  | 1937 | SURYAPET TERMINAL | Road to be modified for turning radius for ethanol TTs | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016363ACN-2026-08-4000147030 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147030 | 2026-08-04 18:45 | 75.9726 | 394 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147030 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016363ACN-2026-08-4000147030 |  | AUD-2026-08-2000016363ACN-2026-08-4000147030 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147034 | Open |  |  | Location Observed Lux Required Lux Status Unloading Pump House 189, 145 P.P.H. / Pump House 101, 112, 120 Unloading Gantry 135, 107, 130 Gantry-1 – Bottom 138/130 Gantry-1 – Top 190, 220 Gantry-2 – Top 149, 125, 125, 123 ROSOV / MOV Area 25, 22, 19 not meeting requirement Tank Farm Road 9, 7 10 not meeting requirement Main Road / Out Gate / In Gate 162, 151 / 198, 148 Truck Entry Gate 20, 35 Lock Shed 148, 136 Main Gate 120, 129 Substation 246, 235 Control Room 225, 206 , not meeting reuirement | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1919 | SECUNDERABAD TERMINAL | Improve Control Room illumination to achieve the required 400 lux. Enhance lighting on the Tank Farm Road to maintain the minimum required 10 lux. Upgrade lighting in the ROSOV/MOV area or Tank Manifold Area to achieve the required 60 lux. | SOD | Marketing | SCR | 2026-10-30 |  | 5 |  | S1 | F5 | 2026-10-30 | AUD-2026-08-2000016364ACN-2026-08-4000147034 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147034 | 2026-08-06 19:00 | 73.9622 | 424 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147034 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147034 |  | AUD-2026-08-2000016364ACN-2026-08-4000147034 | 21 |  | 27 | 80 | 1 | -12 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147040 | Open |  |  | TFMS/SAP reco for April-July 2026 ids 70% | 3.10 | TFMS/SAP reconciliation checked | 1919 | SECUNDERABAD TERMINAL | Location to expedite integration of the new radar gauges with TAS PC. | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147040 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147040 | 2026-08-06 19:00 | 73.9622 | 425 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147040 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147040 |  | AUD-2026-08-2000016364ACN-2026-08-4000147040 | 21 |  | 27 | 80 | 1 | -12 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147041 | Open |  |  | MDSA, TAS, and SSA compliance status was reviewed. The location was advised to ensure 100% compliance with all pending observationswithin the stipulated target dates. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1919 | SECUNDERABAD TERMINAL | Pending audit observations to be complied as per target dates | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016364ACN-2026-08-4000147041 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147041 | 2026-08-06 19:00 | 73.9622 | 394 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147041 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147041 |  | AUD-2026-08-2000016364ACN-2026-08-4000147041 | 21 |  | 27 | 80 | 1 | -12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147043 | Open |  |  | Scrap generated from TK5C dismantling was found available along with IT scrap. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1919 | SECUNDERABAD TERMINAL | RFD to be made and loaction to be scrap free by Q-III | SOD | Marketing | SCR | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-08-2000016364ACN-2026-08-4000147043 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147043 | 2026-08-06 19:00 | 73.9622 | 486 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147043 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147043 |  | AUD-2026-08-2000016364ACN-2026-08-4000147043 | 21 |  | 27 | 80 | 1 | -12 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147904 | Open |  |  | Concertina coil is missing for small section on boundary wall near emergency exit gate. | 6.8 |  | 1919 | SECUNDERABAD TERMINAL | Concertina coil to be provided. | SOD | Marketing | SCR | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147904 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147904 | 2026-08-06 19:00 | 73.9622 | 425 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147904 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016364ACN-2026-08-4000147904 |  | AUD-2026-08-2000016364ACN-2026-08-4000147904 | 21 |  | 27 | 80 | 1 | -12 | 61
M MAHESH BABU | 2026-08-17 | SELVAN J | 2026-08-12 | 1) Main gate HP Logo 2) Fire clock 3) OWS SOP boards are printing was done and replaced. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144102 | Closed | SELVAN J | 2026-08-12 | 1) Main gate HP Logo are faded. 2) Fire clock chart is faded. 3) OWS SOP board faded. | 6.1 | Improving overall look and feel of location | 1973 | CASSIMODE BLACK OIL TERMINAL | To be changed and pasted new. | SOD | Marketing | SZ | 2026-07-31 | INADEQUATE SAFETY CULTURE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015706ACN-2026-07-4000144102 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000144102 | 2026-09-22 17:00 | 27.0455 | 350 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000144102 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000144102 | AUD-2026-07-2000015706ACN-2026-07-4000144102 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 50
SUJEET KUMAR | 2026-08-18 | SAXENA UMESH CHANDRA | 2026-08-15 | The Edge device was received on 29.05.2026. The Video Analytics (VA) solution has been made live at Indore New IRD with effect from15.08.2026. A screenshot of the VA dashboard of Indore New IRD, confirming the go-live of the system, is enclosed for reference. In view of the above compliance and implementation of the VA solution, the audit observation may kindly be considered as closed. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000135378 | Closed | SAXENA UMESH CHANDRA | 2026-08-15 | VA not yet implemented. Under process and targeted to complete by 30.06.2026 | 2.7 | VA alerts checked / analysed | 1457 | INDORE DEPOT | Location to ensure implementation of VA by 30.06.2026 and confirm. | SOD | Marketing | CEN | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012547ACN-2026-06-4000135378 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135378 | 2026-09-09 19:00 | 39.9622 | 351 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135378 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012547ACN-2026-06-4000135378 | AUD-2026-06-2000012547ACN-2026-06-4000135378 | 21 | 21 | 27 | 80 | 0 | -3 | 44 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-18 | DIWAKAR KAMLESH KUMAR | 2026-08-17 | VA alerts are gettig reviwed on daily basis and is closed. VTS is monitored by the respective Officer and same is also getting closed. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143370 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-17 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, CCTV and VA alerts monitoring ,Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 3708 | VISAKH NBOT | Ensure regular field roundsby officers for safety in field activities. CCTV and VTS close monitoring to be done on dauly basis,VA alerts to be reviewed and closed on daily basis | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143370 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143370 | 2026-09-18 17:30 | 31.0247 | 351 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143370 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143370 | AUD-2026-07-2000015047ACN-2026-07-4000143370 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-18 | DIWAKAR KAMLESH KUMAR | 2026-08-17 | Corrective action taken. Stock loss report as of July-26 attached. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143384 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-17 | Abnormal variations / unused assets reviewed | 3.9 | Abnormal variations / unused assets reviewed | 3708 | VISAKH NBOT | A cumulative of 7 KL in LDO & 19 KL in FO380 loss observed against target of ZERO stock loss, to be monitered closely. | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143384 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143384 | 2026-09-18 17:30 | 31.0247 | 351 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143384 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143384 | AUD-2026-07-2000015047ACN-2026-07-4000143384 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-18 | DIWAKAR KAMLESH KUMAR | 2026-08-17 | Scrap has been disposed off Vide doc. No. 9023858831 dt 16-07-26 Invoice Amount : INR 82895. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143392 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-17 | 60% scrap uplifted by vendor from the entire Misc Scrap lot . Remaining to be uplifted | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 3708 | VISAKH NBOT | Balance uplifting of scrap to be expedited | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143392 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143392 | 2026-09-18 17:30 | 31.0247 | 351 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143392 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143392 | AUD-2026-07-2000015047ACN-2026-07-4000143392 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 51
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147878 | Open |  |  | Pending issues of getting the land from MRPL & registering the same, Disposal of Scrap lying for long time, TFMS performance to be improved were discussed and clear time targets arrived. | 1.3 | Pending issues reviewed | 1895 | MANGALORE TERMINAL | Observation made in earlier visit wrt Scrap in May 2026 is still open. | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147878 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147878 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147878 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147878 |  | AUD-2026-08-2000016271ACN-2026-08-4000147878 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147879 | Open |  |  | One ATF tank taken for cleaning and conversion of HSD to ATF tank nearing completion. | 1.8 | Improvement plans discussed | 1895 | MANGALORE TERMINAL | Observation made in earlier visit in May 2026 is still open. | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147879 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147879 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147879 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147879 |  | AUD-2026-08-2000016271ACN-2026-08-4000147879 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147880 | Open |  |  | CCTV functioning checked. Out of 79 cameras, 5 nos cameras are found down. Location has taken up with CCTV vendor. Same to be expedited. | 2.6 | CCTV functioning checked | 1895 | MANGALORE TERMINAL | Observation made in earlier visit in May 2026 is still open. | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147880 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147880 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147880 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147880 |  | AUD-2026-08-2000016271ACN-2026-08-4000147880 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147882 | Open |  |  | TT Nos KA19AE1424, KL18X2142, KL08BU9689 inspected. Variations in dip observed in kasargod bound TT's. | 3.1 | TT dip and EM Lock verified after loading | 1895 | MANGALORE TERMINAL | LIC advised to carry-out calibration of Kasargod bound TT's at Mangalore Terminal itself | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147882 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147882 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147882 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147882 |  | AUD-2026-08-2000016271ACN-2026-08-4000147882 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.21 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147883 | Open |  |  | 32 out of 38 points complied in OISD 24 out of 28 points complied in SSA 17 out of 27 points complied in MDSA 2025-26 | 3.21 | OISD/MDSA/SSA compliance reviewed | 1895 | MANGALORE TERMINAL | Observation made in earlier visit in May 2026 is still open. | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016271ACN-2026-08-4000147883 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147883 | 2026-07-29 17:00 | 82.0455 | 394 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147883 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147883 |  | AUD-2026-08-2000016271ACN-2026-08-4000147883 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147884 | Open |  |  | SIR/PTR No 1895/26-27/4 initated for 3 Nos of Bitumen Tanks is under approval SIR/PTR No 1895/26-27/5 initated for Misc MS Scrap is submitted for Disposal of jetty loading arms, letter of intimation sent to OMC's, RFD will be initiated after due time frame as stated in intimation letter Details of Bitumen gantry are listed in surplus portal | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1895 | MANGALORE TERMINAL | Observation made in earlier visit in May 2026 is still open. | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016271ACN-2026-08-4000147884 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147884 | 2026-07-29 17:00 | 82.0455 | 394 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147884 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147884 |  | AUD-2026-08-2000016271ACN-2026-08-4000147884 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147887 | Open |  |  | All Swing ladders in TT Gantry to be made in line with approved telescopic model (as is available in Bay no 9). | 6.3 | Swing Ladders in TTG | 1895 | MANGALORE TERMINAL | NPCB Proposal for replacement of all Swings in TT Gantry with approved telescopic model shall be submitted | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147887 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147887 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147887 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147887 |  | AUD-2026-08-2000016271ACN-2026-08-4000147887 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147888 | Open |  |  | Sample collection/Disposal record not signed/updated. | 6.4 | TTG Operations | 1895 | MANGALORE TERMINAL | Sample collection/Disposal record to be signed/updated. | SOD | Marketing | SWZ | 2026-08-05 |  | 1 |  | S1 | F1 | 2026-08-05 | AUD-2026-08-2000016271ACN-2026-08-4000147888 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147888 | 2026-07-29 17:00 | 82.0455 | 338 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147888 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147888 |  | AUD-2026-08-2000016271ACN-2026-08-4000147888 | 21 |  | 27 | 80 | 2 | 2 | 49
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147889 | Open |  |  | Marking of Sample Taking Points at TT Gantry not done, provision of spilled product to Drain to OWS/ETP not provided | 6.5 | TTG Operations | 1895 | MANGALORE TERMINAL | Marking of Sample Taking Points at TT Gantry, provision of spilled product to Drain to OWS/ETP | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147889 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147889 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147889 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147889 |  | AUD-2026-08-2000016271ACN-2026-08-4000147889 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147890 | Open |  |  | Sampling points used for purposes other than sampling | 6.6 | TTG Operations | 1895 | MANGALORE TERMINAL | Sampling points to be strictly for sampling purpose only and shall not be used for other purposes. | SOD | Marketing | SWZ | 2026-08-05 |  | 1 |  | S1 | F1 | 2026-08-05 | AUD-2026-08-2000016271ACN-2026-08-4000147890 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147890 | 2026-07-29 17:00 | 82.0455 | 338 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147890 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147890 |  | AUD-2026-08-2000016271ACN-2026-08-4000147890 | 21 |  | 27 | 80 | 2 | 2 | 49
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147891 | Open |  |  | Kasaragod TTs found to have variation in dips | 6.7 | Calibration of Kasargod TT's | 1895 | MANGALORE TERMINAL | Kasaragod TTs found to have variation due to calibration at other locations. Same to be calibrated in Mangalore Terminal for which 1 week time may be given. | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016271ACN-2026-08-4000147891 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147891 | 2026-07-29 17:00 | 82.0455 | 394 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147891 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147891 |  | AUD-2026-08-2000016271ACN-2026-08-4000147891 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147892 | Open |  |  | Replacement of density meters & thermometers etc. in TT Gantry after use of max. 1 year to be reviewed and done | 6.8 | Replacement of Density meter and Thermometers | 1895 | MANGALORE TERMINAL | It is recommended to replace the density meters & thermometers etc. in TT Gantry after use of max. 1 year. | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147892 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147892 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147892 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000147892 |  | AUD-2026-08-2000016271ACN-2026-08-4000147892 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000148001 | Open |  |  | Lapping of gratings found in TT Gantry to be rectified. | 6.17 | TTG Maintenance | 1895 | MANGALORE TERMINAL | Lapping of gratings found in TT Gantry to be rectified. | SOD | Marketing | SWZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000148001 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000148001 | 2026-07-29 17:00 | 82.0455 | 363 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000148001 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016271ACN-2026-08-4000148001 |  | AUD-2026-08-2000016271ACN-2026-08-4000148001 | 21 |  | 27 | 80 | 2 | 2 | 52
KATAKAM SRINIVAS | 2026-08-19 | BAGADE AMAR ARUN | 2026-08-08 | Point repeated at Senior Inspection Audit dtd. 02.06.26 with point no. 6.1 | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122494 | Closed | BAGADE AMAR ARUN | 2026-08-08 | Cooling water line of fire engine is in close loop, thus difficult to ensure its flowability | 6.2 | Fire Engine Shed | 1485 | AKOLA DEPOT | To provide in consultation with OEM | SOD | Marketing | WZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011118ACN-2026-03-4000122494 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122494 | 2026-08-24 | 56.7538 | 352 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122494 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011118ACN-2026-03-4000122494 | AUD-2026-03-2000011118ACN-2026-03-4000122494 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 51
KATAKAM SRINIVAS | 2026-08-19 | BAGADE AMAR ARUN | 2026-08-13 | Repeated point 3.18 of Audit no. AUD-2026-06-2000013155. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122491 | Closed | BAGADE AMAR ARUN | 2026-08-13 | OISD 2022-23 Total points-20 Complied-20 MDSA 2025-26 Total points-33 Complied-14 SSA 2025-26 Total points-32 Complied-28 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1485 | AKOLA DEPOT | Location to comply the points in time bound manner | SOD | Marketing | WZ | 2026-07-31 | COMPLACENCY OR RISK NORMALIZATION | 9 | PROCESS SAFETY | S3 | F3 | 2026-07-31 | AUD-2026-03-2000011118ACN-2026-03-4000122491 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122491 | 2026-08-24 | 56.7538 | 352 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122491 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011118ACN-2026-03-4000122491 | AUD-2026-03-2000011118ACN-2026-03-4000122491 | 21 | 21 | 26 | 80 | 3 | 3 | 48 | 51
SUJEET KUMAR | 2026-08-19 | SAXENA UMESH CHANDRA | 2026-05-25 | FO and LDO tanks have been uplifted and disposed of. Invoice dated 09.08.2026 is enclosed. Hence the audit observation may be considered as closed. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127182 | Closed | SAXENA UMESH CHANDRA | 2026-08-19 | Currently, location has approved RFD for dismantling of FO/LDO tanks. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1457 | INDORE DEPOT | Location to expedite disposal of FO/LDO tank | SOD | Marketing | CEN | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011235ACN-2026-03-4000127182 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127182 | 2026-09-09 19:00 | 39.9622 | 352 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127182 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127182 | AUD-2026-03-2000011235ACN-2026-03-4000127182 | 21 | 21 | 26 | 80 | 0 | -3 | 35 | 51
SALADI SRINIVASU | 2026-08-20 | LOMESH KUMAR PATRE | 2026-07-31 | VTS & CCTV is being monitored, records maintained. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000137060 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1979 | VIJAYAWADA TERMINAL | VTS monitoring , CCTV monitoring to be done by officers on daily basis and records to be maintained | SOD | Marketing | SCR | 2026-06-05 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-05 | AUD-2026-06-2000012864ACN-2026-06-4000137060 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137060 | 2026-08-21 16:00 | 59.0872 | 353 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137060 | 532 | 8294 | 21 | 8294 | 136 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137060 | AUD-2026-06-2000012864ACN-2026-06-4000137060 | 21 | 21 | 27 | 80 | 12 | 12 | 40 | 51
SALADI SRINIVASU | 2026-08-20 | LOMESH KUMAR PATRE | 2026-07-31 | Points raised in Fire drill explained to all FOC members, it is being ensured from next fore drill onwards. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137061 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Fire drill was last conducted on 03.06.2026 in presence of DCIF . Observations given in Fire drill i) Training to be given to in-shift operators in minor maintenance jobs so that they can be handy in handling emergency maintenances in Off Shift hours. Ii) Pump shed to be cooled in case of fire in pump house.iii) Teams shall wear uniforms for easy identification. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1979 | VIJAYAWADA TERMINAL | Fire drill observations to be complied at the earliest | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137061 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137061 | 2026-08-21 16:00 | 59.0872 | 353 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137061 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137061 | AUD-2026-06-2000012864ACN-2026-06-4000137061 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 51
SALADI SRINIVASU | 2026-08-20 | LOMESH KUMAR PATRE | 2026-07-31 | Rectified & is in operable condition | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137065 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Checked HVLR at Tank 1B . RSFPS, MEFG , HCD, were checked at TK 1A. Product Pumphosue HCD checked .All functioning found OK except one unit of RSFPS did not function due to low Nitrogen pressure. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1979 | VIJAYAWADA TERMINAL | RSFPS of TK1A to be rectified . | SOD | Marketing | SCR | 2026-06-05 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-05 | AUD-2026-06-2000012864ACN-2026-06-4000137065 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137065 | 2026-08-21 16:00 | 59.0872 | 353 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137065 | 532 | 8294 | 21 | 8294 | 136 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137065 | AUD-2026-06-2000012864ACN-2026-06-4000137065 | 21 | 21 | 27 | 80 | 12 | 12 | 40 | 51
|  | ANKIT KUMAR | 2026-08-21 | Same will be ensured henceforth. Control room officers and Operation incharge sensitized. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125567 | Completed | AGARWAL VIPUL | 2026-03-18 | There are only 16 instances of abnormal variations during the period 1st Oct'25 to 22nd Feb'26. Reasons for abnormal gain/ loss arefound entered in SAP. | 3.9 | Abnormal variations / unused assets reviewed | 1216 | BAHADURGARH TERMINAL | Location to take necessary precautions in future to avoid instances of abnormal variation (gain/ loss). | SOD | Marketing | NZ | 2026-03-15 |  | 1 |  | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125567 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125567 | 2026-09-05 | 44.7538 | 195 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125567 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125567 |  | AUD-2026-03-2000011128ACN-2026-03-4000125567 | 21 |  | 26 | 80 | 9 | 9 | 28
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Role-specific responsibilities re-communicated to all officers. SOP compliance, field rounds, VTS monitoring, CCTV monitoring, and record maintenance Strengthened. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142294 | Closed | UDIT MISHRA | 2026-08-03 | Role specific / officer specific points were discussed and communicated | 1.6 | Expectations clearly communicated to officers | 1953 | RAJAHMUNDRY TERMINAL | SOPs to be followed for all opertaions , officers to take regular field rounds, VTS monitoring for nil route deviations and nil speed violations, CCTV monitoring on daily basis and records to be maintained | SOD | Marketing | SCR | 2026-06-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000142294 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142294 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142294 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000142294 | AUD-2026-07-2000015529ACN-2026-07-4000142294 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Mock drill observations communicated to all stakeholders during table top exercise before starting of mock drill on 29.07.2026 and all observations were complied. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142295 | Closed | UDIT MISHRA | 2026-08-03 | Double contingency scenario simulated; observations recorded. 1) Assembly area to be made properly 2) Search and rescue process to be strengthend, 3)Ambulance to be kept at the nearest possible location to rescue the injured on immediate basis | 2.2 | Double contingency scenario simulated; observations recorded | 1953 | RAJAHMUNDRY TERMINAL | Mock drill observations to be complied . | SOD | Marketing | SCR | 2026-06-30 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015529ACN-2026-07-4000142295 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142295 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142295 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000142295 | AUD-2026-07-2000015529ACN-2026-07-4000142295 | 21 | 21 | 27 | 80 | 1 | 2 | 44 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Missing emergency trolley items Procured and kept in emergency trolly. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142296 | Closed | UDIT MISHRA | 2026-08-03 | Reviewed emergency trolley equipment , FLP search lights and electrical rubber gloves are not available.Interacted with officers & security personnel about their roles and responsibilities during emergencies | 2.5 | Emergency response preparedness reviewed | 1953 | RAJAHMUNDRY TERMINAL | In Emergency trolley Some of the items viz , Search Lights, Electrical Gloves , are missing To take corrective action for emergencytrolley availability with all the required items. | SOD | Marketing | SCR | 2026-06-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000142296 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142296 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142296 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000142296 | AUD-2026-07-2000015529ACN-2026-07-4000142296 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | K-factor change records updated with vendor MOM communication and supporting documents. Bay kept in observation by vendor, NIL variation observed in the month of july. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143351 | Closed | UDIT MISHRA | 2026-08-03 | Checked,one instance in May 2026 (Precision Value Toggled from 39.999996 to 40) | 3.13 | K-factor changes reviewed (if any) | 1953 | RAJAHMUNDRY TERMINAL | MFM factor change report proper records to maintained, mail communication from vendor to be attached along with report. | SOD | Marketing | SCR | 2026-06-12 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000143351 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143351 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143351 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143351 | AUD-2026-07-2000015529ACN-2026-07-4000143351 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | SHARMA ABHISHEK KUMAR | 2026-07-18 | Local loading report being reviewed and signed. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143352 | Closed | SHARMA ABHISHEK KUMAR | 2026-07-18 | Local loading was reviewed. Local loading carried out for own use for Fire engines, DG sets.Record maintained. | 3.14 | Local loading checks (if applicable) | 1953 | RAJAHMUNDRY TERMINAL | Local loading report to be reviewed and signed by LIC. | SOD | Marketing | SCR | 2026-06-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000143352 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143352 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143352 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143352 | AUD-2026-07-2000015529ACN-2026-07-4000143352 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | SHARMA ABHISHEK KUMAR | 2026-07-18 | Housekeeping done at and near gantry location | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143353 | Closed | SHARMA ABHISHEK KUMAR | 2026-07-18 | Checked, dry leaves and cables waste lying near TT Gantry | 3.15 | Housekeeping & PPE usage checked | 1953 | RAJAHMUNDRY TERMINAL | Housekeeping near TT Gantry to be done regularly | SOD | Marketing | SCR | 2026-06-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000143353 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143353 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143353 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143353 | AUD-2026-07-2000015529ACN-2026-07-4000143353 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Training conducted for security personals on operation of various safety equipment's and handling live fire. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127876 | Closed | UDIT MISHRA | 2026-08-03 | Live fire training of security personnel not done | 6.2 |  | 1953 | RAJAHMUNDRY TERMINAL | Live fire training of security personnel of all guards to be conducted | SOD | Marketing | SCR | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-04-2000011082ACN-2026-04-4000127876 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127876 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127876 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127876 | AUD-2026-04-2000011082ACN-2026-04-4000127876 | 21 | 21 | 26 | 80 | 1 | 2 | 57 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Bay was kept under observation and no further variation observed.Bay no 10 Prover verification and calibration completed on 29.07.2026 | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142298 | Closed | UDIT MISHRA | 2026-08-03 | Two filled TTs dips checked at TT Gantry . TT no AP39UJ2236 dips found ok for compartment 1&2 and 4 mm excess in the 3rd compartment, TT no AP 39UK 5669 dips found ok for all 4 compartments. | 3.2 | Post-loading dip checks verified | 1953 | RAJAHMUNDRY TERMINAL | Corrective action to be taken for any excess variation in post loading dips. | SOD | Marketing | SCR | 2026-06-12 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000142298 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142298 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142298 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000142298 | AUD-2026-07-2000015529ACN-2026-07-4000142298 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | SHARMA ABHISHEK KUMAR | 2026-07-18 | Min. 20% of the trucks are being checked for ethanol content on daily basis. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142299 | Closed | SHARMA ABHISHEK KUMAR | 2026-07-18 | Blending % checked for TT no AP39UM0468 Blending % observed 19.5%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1953 | RAJAHMUNDRY TERMINAL | Officers to check ethanol blending % periodically and take corrective action for any deviation | SOD | Marketing | SCR | 2026-06-12 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-12 | AUD-2026-07-2000015529ACN-2026-07-4000142299 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000142299 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000142299 | 532 | 8294 | 21 | 8294 | 129 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000142299 | AUD-2026-07-2000015529ACN-2026-07-4000142299 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | OEM Emerson informed regarding temperature variation, System was kept under observation and found okay. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143350 | Closed | UDIT MISHRA | 2026-08-03 | Physical dip has been checked for MS tank 1A and HSD Tank 6A. Tank 1A - Physical dip of 418.6 cms against TAS dip of 418.6 cms . Water physical dip observed 0 cms against TAS dip of 0 cms Variation : nil. Tank 6A - Physical dip of 804.7 cms against TAS dip of 804.6 cms . Water physical dip observed 1.6 cms against TAS dip of 1.6 cms Variation : nil. Tank 1A Physical density 740.9 against TAS tank density of 740.4 , Tank 6A Physical density 818.9 against TAS tank density of 818.0. Tank 1A physical temp 35.75 against TAS temp of 35.7 .Tank 6A physical temp 35.0 against TAS temp of 32.3 . | 3.7 | Inventory physical dip of minimum two tanks taken | 1953 | RAJAHMUNDRY TERMINAL | Location to take up with TAS vendor and ensure that variations in tank temperature remain with in tolerance limit . | SOD | Marketing | SCR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015529ACN-2026-07-4000143350 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143350 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143350 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143350 | AUD-2026-07-2000015529ACN-2026-07-4000143350 | 21 | 21 | 27 | 80 | 1 | 2 | 44 | 51
SINGH SOMESH | 2026-08-22 | UDIT MISHRA | 2026-08-03 | Repair of FE2, and starter motor of FE4 & FE5 completed, All engines running in auto, Verified during sequence testing of FE. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143355 | Closed | UDIT MISHRA | 2026-08-03 | Full field round completed covering TT Gantry, tank farm,product pump house, Fire Pump House, control room, ETP security, emergencyexit gate . | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1953 | RAJAHMUNDRY TERMINAL | FE 2 under repair. FE 4 & FE 5 not started in auto due to starter issue. To be rectified urgently. | SOD | Marketing | SCR | 2026-06-15 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-15 | AUD-2026-07-2000015529ACN-2026-07-4000143355 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143355 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143355 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015529ACN-2026-07-4000143355 | AUD-2026-07-2000015529ACN-2026-07-4000143355 | 21 | 21 | 27 | 80 | 1 | 2 | 41 | 51
SINGH SOMESH | 2026-08-22 | SHARMA ABHISHEK KUMAR | 2026-07-18 | PM Jobs being completed and closed in timely basis. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143358 | Closed | SHARMA ABHISHEK KUMAR | 2026-07-18 | PM compliance reviewed , delay in closing of PM orders | 4.4 | Quality of PM compliance reviewed | 1953 | RAJAHMUNDRY TERMINAL | To ensure timely completion of PM Jobs and closing of PM orders | SOD | Marketing | SCR | 2026-06-25 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-25 | AUD-2026-07-2000015529ACN-2026-07-4000143358 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143358 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143358 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143358 | AUD-2026-07-2000015529ACN-2026-07-4000143358 | 21 | 21 | 27 | 80 | 1 | 2 | 43 | 51
SINGH SOMESH | 2026-08-22 | SHARMA ABHISHEK KUMAR | 2026-07-18 | Bags for all visitors eing checked prior to DFMD. Frisking for all visitors is bening done properly. Training to all security personnels has been given related to Frisking and DFMS usage. | AUDIT UPLOAD IN SAP | 2026-06-11 17:30 | AUD-2026-07-2000015529 | 2026-06-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143361 | Closed | SHARMA ABHISHEK KUMAR | 2026-07-18 | Bag checking being done after DFMD by Security. Frisking not being done . | 6.1 |  | 1953 | RAJAHMUNDRY TERMINAL | Security to check the bags prior to DFMD and ensure proper frisking of all visitors | SOD | Marketing | SCR | 2026-06-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015529ACN-2026-07-4000143361 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015529ACN-2026-07-4000143361 | 2026-07-22 18:30 | 88.983 | 355 | >20 | AUD-2026-07-2000015529 - ACN-2026-07-4000143361 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015529ACN-2026-07-4000143361 | AUD-2026-07-2000015529ACN-2026-07-4000143361 | 21 | 21 | 27 | 80 | 1 | 2 | 44 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-22 | DIWAKAR KAMLESH KUMAR | 2026-08-18 | Any deviation in route, night drivings are being monitored at location level by the officials and corrective actions are being taken. Apart from VTS daily gate meeting ois conducted and TT crews are being informed for not taking Night Driving. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143382 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-18 | VTS deviations reviewed on random basis | 3.3 | VTS deviations reviewed | 3708 | VISAKH NBOT | Route deviations and night driving to be minimized | SOD | Marketing | SCR | 2026-07-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-30 | AUD-2026-07-2000015047ACN-2026-07-4000143382 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143382 | 2026-09-18 17:30 | 31.0247 | 355 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143382 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015047ACN-2026-07-4000143382 | AUD-2026-07-2000015047ACN-2026-07-4000143382 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-22 | DIWAKAR KAMLESH KUMAR | 2026-08-22 | 1. Stock loss achievement as of July-26 is as Follows LDO: 0.026 % FO 380 CST: 0.444 % 2. Bay Ressignment has been reduced in July-26. Report attached | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143366 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-22 | Performance review done. 1. LDO & FO380 stock loss not meeting target 2. Bay reassigment and loading time is very high | 1.2 | Performance review conducted | 3708 | VISAKH NBOT | 1. Necessary Action to be taken to achieve LDO & FO380 stock loss 2. Necessary Action to be taken to reduce bay reassigment and loading time | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143366 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143366 | 2026-09-18 17:30 | 31.0247 | 355 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143366 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143366 | AUD-2026-07-2000015047ACN-2026-07-4000143366 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 51
AILAVARAPU VENKATA KRISHNA MURTY | 2026-08-22 | DIWAKAR KAMLESH KUMAR | 2026-08-18 | Following MOC ID has been closed in Arohan MOC ID System Status 3100001295 Closed 3100001617 Closed 3100001618 Closed 3100001803 Closed 3100001821 Closed 3200000609 Closed 3200000680 Closed 3300000142 Closed 3300000204 Closed 3300000334 Closed 3300000390 Closed 3300000394 Closed | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143387 | Closed | DIWAKAR KAMLESH KUMAR | 2026-08-18 | MOC status reviewed. 11 MOC is open | 3.17 | MOC status reviewed, nil pending | 3708 | VISAKH NBOT | All open MOC to be closed within time | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143387 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143387 | 2026-09-18 17:30 | 31.0247 | 355 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143387 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143387 | AUD-2026-07-2000015047ACN-2026-07-4000143387 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 51
|  | GAKHAR NAVEEN | 2026-08-22 | Training imparted to all concerned person | ZONAL VISIT REPORT 17.02.2026 VASHI BOT | 2026-02-17 | AUD-2026-03-2000011166 | 2026-02-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123412 | Completed | GAKHAR NAVEEN | 2026-08-22 | Trolley to be placed at a level ground with easily acessible & all specified items in respective compartments | 6.1 | Emergency trolley condition checked | 3562 | VASHI BO TML | Avarness & Training of all equipments available in trolley to be given all location team members | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | EMERGENCY | S1 | F3 | 2026-03-31 | AUD-2026-03-2000011166ACN-2026-03-4000123412 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011166ACN-2026-03-4000123412 | 2026-09-15 | 34.7538 | 211 | >20 | AUD-2026-03-2000011166 - ACN-2026-03-4000123412 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011166ACN-2026-03-4000123412 |  | AUD-2026-03-2000011166ACN-2026-03-4000123412 | 21 |  | 26 | 80 | 9 | 9 | 31
M MAHESH BABU | 2026-08-22 | SELVAN J | 2026-08-12 | New earth pit boards stickering has been done. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143798 | Closed | SELVAN J | 2026-08-12 | Earth-pit resistance testing done on 17.02.2026 and all values are well with in the limits. | 3.16 | Earth pits / boundary / vegetation control checked | 1973 | CASSIMODE BLACK OIL TERMINAL | Few Earth pit boards Stickering done-due date to be affixed new as faded out. | SOD | Marketing | SZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015706ACN-2026-07-4000143798 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000143798 | 2026-09-22 17:00 | 27.0455 | 355 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000143798 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015706ACN-2026-07-4000143798 | AUD-2026-07-2000015706ACN-2026-07-4000143798 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | Training conducted post that : electician explain the action taken during the assembly review | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146600 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes conducted | 2.1 | Fire drill conducted in last 2 months (surprise) | 3562 | VASHI BO TML | electician to explain the action taken during the assembly review | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146600 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146600 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146600 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146600 | AUD-2026-07-2000016505ACN-2026-07-4000146600 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | All clear siren being given after assembly | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146601 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes conducted | 2.2 | Double contingency scenario simulated; observations recorded | 3562 | VASHI BO TML | All clear sign to be done after manpower count at assembly point only | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146601 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146601 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146601 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146601 | AUD-2026-07-2000016505ACN-2026-07-4000146601 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | Lux levels checked (gantry/roads/admin) during night-halt | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146602 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 3562 | VASHI BO TML | regularly check should be done with lux meter | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146602 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146602 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146602 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146602 | AUD-2026-07-2000016505ACN-2026-07-4000146602 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | CAMERA ALIGNMENT DONE | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146603 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes | 2.6 | CCTV functioning checked | 3562 | VASHI BO TML | CAMERA ALIGNMENT TO BE DONE | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146603 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146603 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146603 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146603 | AUD-2026-07-2000016505ACN-2026-07-4000146603 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | Acesscontrol checking properly | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146604 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes | 2.8 | Access control systems checked | 3562 | VASHI BO TML | Acesscontrol should be checking properly | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146604 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146604 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146604 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146604 | AUD-2026-07-2000016505ACN-2026-07-4000146604 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-22 | regular training conducted of TT crew | VASHO BOT VISTED DTD 19.06.2026 | 2026-06-19 | AUD-2026-07-2000016505 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146606 | Closed | GAKHAR NAVEEN | 2026-08-22 | yes conducted | 2.15 | TT crew roadside emergency procedures checked | 3562 | VASHI BO TML | regular training to be conducted of TT crew | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016505ACN-2026-07-4000146606 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016505ACN-2026-07-4000146606 | 2026-09-15 | 34.7538 | 355 | >20 | AUD-2026-07-2000016505 - ACN-2026-07-4000146606 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016505ACN-2026-07-4000146606 | AUD-2026-07-2000016505ACN-2026-07-4000146606 | 21 | 21 | 27 | 80 | 9 | 9 | 44 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | Explanation being given in drills | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146563 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes conducted | 2.1 | Fire drill conducted in last 6 months (surprise) | 1588 | VASHI WHITE OIL TERMINAL | Fire extinguisher operator to explain the action taken during the assembly review | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146563 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146563 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146563 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146563 | AUD-2026-07-2000016456ACN-2026-07-4000146563 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | being done:All clear sign to be done after manpower count at assembly point only | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146564 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes conducted | 2.2 | Double contingency scenario simulated; observations recorded | 1588 | VASHI WHITE OIL TERMINAL | All clear sign to be done after manpower count at assembly point only | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146564 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146564 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146564 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146564 | AUD-2026-07-2000016456ACN-2026-07-4000146564 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | regular checking and records maintained Lux levels checked (gantry/roads/admin | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146565 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1588 | VASHI WHITE OIL TERMINAL | regularly check should be done with lux meter | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146565 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146565 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146565 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146565 | AUD-2026-07-2000016456ACN-2026-07-4000146565 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | CAMERA ALIGNMENT DONE | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146566 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes | 2.6 | CCTV functioning checked | 1588 | VASHI WHITE OIL TERMINAL | CAMERA ALIGNMENT TO BE DONE | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146566 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146566 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146566 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146566 | AUD-2026-07-2000016456ACN-2026-07-4000146566 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | spare parts procured and HVLR rectified | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146569 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1588 | VASHI WHITE OIL TERMINAL | Spare parts to be procured for HVLR rectification | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146569 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146569 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146569 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146569 | AUD-2026-07-2000016456ACN-2026-07-4000146569 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
NARAYANE KISHORKUMAR SUDAM | 2026-08-22 | GAKHAR NAVEEN | 2026-08-19 | regular training conducted of TT crew | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146571 | Closed | GAKHAR NAVEEN | 2026-08-19 | yes conducted | 2.15 | TT crew roadside emergency procedures checked | 1588 | VASHI WHITE OIL TERMINAL | regular training to be conducted of TT crew | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146571 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146571 | 2026-10-14 | 5.7538 | 355 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146571 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146571 | AUD-2026-07-2000016456ACN-2026-07-4000146571 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 51
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147909 | Open |  |  | Yes. Found satisfactory except at Tank No. 4 Manifold, Foam shed, Control Room and Admin Building. Additional light fixtures to be provided to improve the Lux level. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1436 | SAGAR DEPOT | To ensure and provide adequate lighting to get desired lux level. | SOD | Marketing | CEN | 2026-09-10 |  | 3 |  | S1 | F3 | 2026-09-10 | AUD-2026-08-2000016370ACN-2026-08-4000147909 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147909 | 2026-08-07 19:00 | 72.9622 | 374 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147909 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016370ACN-2026-08-4000147909 |  | AUD-2026-08-2000016370ACN-2026-08-4000147909 | 21 |  | 27 | 80 | 4 | 2 | 54
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147915 | Open |  |  | Not applicable due to Manual Reco. TAS Revamp Project is going on. Targeted to complete by 15.08.2026 | 3.10 | TFMS/SAP reconciliation checked | 1436 | SAGAR DEPOT | Location to follow up with TAS vendor and expedite completion of Project latest by 31.08.2026. | SOD | Marketing | CEN | 2026-08-31 |  | 2 |  | S2 | F1 | 2026-08-31 | AUD-2026-08-2000016370ACN-2026-08-4000147915 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147915 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147915 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016370ACN-2026-08-4000147915 |  | AUD-2026-08-2000016370ACN-2026-08-4000147915 | 21 |  | 27 | 80 | 4 | 2 | 52
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147916 | Open |  |  | Yes reviewed. 2 OISD and 5 MDSA Audit observation points are still open and the compliances of the same are underway. Targeted to complete by H1. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1436 | SAGAR DEPOT | To ensure completion of pending points by 30.09.2026 in all respect. | SOD | Marketing | CEN | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-08-2000016370ACN-2026-08-4000147916 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147916 | 2026-08-07 19:00 | 72.9622 | 394 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147916 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016370ACN-2026-08-4000147916 |  | AUD-2026-08-2000016370ACN-2026-08-4000147916 | 21 |  | 27 | 80 | 4 | 2 | 57
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | a) Part code - 2.6 & 2.7 - Pending as CCTV cameras are still to be reinstated- Pending CCTV have been made functional. b) Part code - 4.1 - Pending points: (i) UG water tank manhole cover found touching ground needs to be raised up- (ii) PMCC room: SLD not updated- SLD has been updated. (iii) Pump house: Inadeqaute height of hand railing for few walkways - complied c) Part code: 6.3 - Cross over in dyke drain should be painted. _painted. d) Part code: 6.14 - UG tank where calibration water is stored, has its manifold at ground level and secured in place by only a few nuts and bolts (this observation was there in Nov 25 inspection report also). All nut bolts have been applied and complied. e) Part code: 6.18 - No SOP was there for STP. STP SOP has been prepared by the OEM AND SHARED TO LOCATION. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000131384 | Closed | KUMAR ATUL | 2026-08-22 | Compliance has been reviewd, however following points under Part code is Pending for previous Zonal Inspection: a) Part code - 2.6& 2.7 - Pending as CCTV cameras are still to be reinstated b) Part code - 4.1 - Pending points: (i) UG water tank manhole coverfound touching ground needs to be raised up (ii) PMCC room: SLD not updated. (iii) Pump house: Inadeqaute height of hand railing for few walkways - Partially complied c) Part code: 6.3 - Cross over in dyke drain should be painted. d) Part code: 6.14 - UG tank where calibration water is stored, has its manifold at ground level and secured in place by only a few nuts and bolts (this observation was there in Nov 25 inspection report also) e) Part code: 6.18 - No SOP was there for STP. | 1.4 | Earlier action points status checked | 1313 | BAITALPUR DEPOT | All pending Part code observations to be closed by 30/06/2026 | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131384 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131384 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131384 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012753ACN-2026-05-4000131384 | AUD-2026-05-2000012753ACN-2026-05-4000131384 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | Faulty cameras TK18 PTZ, TK6 manifold have been repaired and installed. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131385 | Closed | KUMAR ATUL | 2026-08-22 |  | 2.6 | CCTV functioning checked | 1313 | BAITALPUR DEPOT | Location to ensure 100% uptime of all CCTVs. Faulty Camera to be rectified. | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131385 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131385 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131385 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012753ACN-2026-05-4000131385 | AUD-2026-05-2000012753ACN-2026-05-4000131385 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | All visitors are being allowed with valid CBAC pass only. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131386 | Closed | KUMAR ATUL | 2026-08-22 | During the Visit Access control at main gate was checked and found that CBAC Systen was fully functional along with Biomatric operational at Main gate, entry to Licence area and Control room. The PAMS visitor management system is not being used for all the visitors entrering the premises. | 2.8 | Access control systems checked | 1313 | BAITALPUR DEPOT | PAMS system to to be used for Visitor Management at location. | SOD | Marketing | NCR | 2026-05-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S1 | F3 | 2026-05-30 | AUD-2026-05-2000012753ACN-2026-05-4000131386 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131386 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131386 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131386 | AUD-2026-05-2000012753ACN-2026-05-4000131386 | 21 | 21 | 27 | 80 | 1 | 1 | 39 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | NEW TREM CARDS have been printed and issued to all TTs plying at Baitalpur IRD. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131387 | Closed | KUMAR ATUL | 2026-08-22 |  | 2.14 | TT crew fire extinguisher usage checked | 1313 | BAITALPUR DEPOT | Location to ensure that all TT crew carry valid TREM cards at all times. Strict compliance shall be ensured. | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131387 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131387 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131387 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131387 | AUD-2026-05-2000012753ACN-2026-05-4000131387 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | Civil work has been completed for repair work | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131388 | Closed | KUMAR ATUL | 2026-08-22 |  | 3.16 | Earth pits / boundary / vegetation control checked | 1313 | BAITALPUR DEPOT | Civil work to be ensured | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131388 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131388 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131388 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131388 | AUD-2026-05-2000012753ACN-2026-05-4000131388 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | PA system has been made functional by procuring the spared cards. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131390 | Closed | KUMAR ATUL | 2026-08-22 |  | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Restore the Public Announcement System at the earliest and prominently display the communication process in Shed to ensure effective emergency communication and operational preparedness | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131390 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131390 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131390 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131390 | AUD-2026-05-2000012753ACN-2026-05-4000131390 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | Contact list has been revised and displayed at prominent places | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131391 | Closed | KUMAR ATUL | 2026-08-22 | Post DPC, List of First Aid officers & Important contact numbers not updated | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Contact list to be updated immediately | SOD | Marketing | NCR | 2026-05-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S1 | F3 | 2026-05-30 | AUD-2026-05-2000012753ACN-2026-05-4000131391 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131391 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131391 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131391 | AUD-2026-05-2000012753ACN-2026-05-4000131391 | 21 | 21 | 27 | 80 | 1 | 1 | 39 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | First aid box has been replanished in MCC room. however new first aid box has also been ordered for covering the entire premises. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131392 | Closed | KUMAR ATUL | 2026-08-22 | In the MCC room, the First Aid Box requires replenishment with fresh medicines. The list of available medicines should also be displayed/updated for easy reference. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Replenish the First Aid Box in the MCC room or elsewhere with fresh and valid medicines on priority and display an updated list of contents to ensure readiness for emergency use | SOD | Marketing | NCR | 2026-05-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S1 | F3 | 2026-05-30 | AUD-2026-05-2000012753ACN-2026-05-4000131392 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131392 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131392 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131392 | AUD-2026-05-2000012753ACN-2026-05-4000131392 | 21 | 21 | 27 | 80 | 1 | 1 | 39 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | Sir, leakage from oil cup has been arrested by replacng the oil cups. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131393 | Closed | KUMAR ATUL | 2026-08-22 | In TLF pump house, leakage was observed from Oil cup in TLF HSD-03 and TLF MS-01 | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Leakage should be attended immediately to prevent equipment deterioration and ensure safe and reliable operation. | SOD | Marketing | NCR | 2026-07-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-05-2000012753ACN-2026-05-4000131393 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131393 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131393 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131393 | AUD-2026-05-2000012753ACN-2026-05-4000131393 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | MSDS of ethanol MS, HSD has been updated in tank farm area. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131394 | Closed | KUMAR ATUL | 2026-08-22 | Latest MSDS not displayed at the location | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | The existing MSDS should be replaced with the latest updated MSDS and displayed prominently | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S1 | F3 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131394 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131394 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131394 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131394 | AUD-2026-05-2000012753ACN-2026-05-4000131394 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | PM order are being closed fortnightly basis and PM performance is maintained at 100%. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131397 | Closed | KUMAR ATUL | 2026-08-22 | Tot 44 PM orders were scheduled for May'2026. All PM order are in open state in SAP as on 16/05/2026. | 4.4 | Quality of PM compliance reviewed | 1313 | BAITALPUR DEPOT | Location to closed PM orders on fortnightly basis so that pendency on the last day of the month does not become an issue | SOD | Marketing | NCR | 2026-05-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S1 | F4 | 2026-05-30 | AUD-2026-05-2000012753ACN-2026-05-4000131397 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131397 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131397 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131397 | AUD-2026-05-2000012753ACN-2026-05-4000131397 | 21 | 21 | 27 | 80 | 1 | 1 | 39 | 51
VIKAS CHANDRA | 2026-08-23 | KUMAR ATUL | 2026-08-22 | Both CCTV and VHF PO has been finalized and CCTV have been installaed and VHF license in under amendment. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131396 | Closed | KUMAR ATUL | 2026-08-22 | LPR for CCTV procurement and VHF procurement is in progress | 4.3 | Project progress reviewed | 1313 | BAITALPUR DEPOT | Expedite the tendering process for CCTV and VHF procurement to ensure timely finalization and installation. | SOD | Marketing | NCR | 2026-05-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-30 | AUD-2026-05-2000012753ACN-2026-05-4000131396 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131396 | 2026-09-26 17:30 | 23.0247 | 356 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131396 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131396 | AUD-2026-05-2000012753ACN-2026-05-4000131396 | 21 | 21 | 27 | 80 | 1 | 1 | 39 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | Tank 5C repair completed within given timeline. Location completed all NPCB projects in time | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123658 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | Respective roles and responsibilities, performance, and expectations were discussed. A comprehensive review was carried out covering adherence to systems and SOPs, inspection of tank trucks, EM lock integrity, overall terminal preparedness | 1.2 | Performance review conducted | 1919 | SECUNDERABAD TERMINAL | Tank 5C repair to be completed within given timeline.Location to focus on completing all NPCB projects in time | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-03-2000011062ACN-2026-03-4000123658 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123658 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123658 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123658 | AUD-2026-03-2000011062ACN-2026-03-4000123658 | 21 | 21 | 26 | 80 | 1 | -12 | 39 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | Continuous improvement being carried out, Compliance is going on, Marking this complied as a repetitive point in Next Visit. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123660 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | Recent review recommendations were reviewed along with pending audit points of SSA & MDSA | 1.4 | Earlier action points status checked | 1919 | SECUNDERABAD TERMINAL | Compliance of all the MDSA & SSA pending points | SOD | Marketing | SCR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-03-2000011062ACN-2026-03-4000123660 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123660 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123660 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123660 | AUD-2026-03-2000011062ACN-2026-03-4000123660 | 21 | 21 | 26 | 80 | 1 | -12 | 57 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-10 | Emergency trolley being regularly inspected & all equipment placed at their designated compartments. Live fire training to mparted to all contract workmen on 04-06.08.2026. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123663 | Closed | SATYENDRA CHOURASIA | 2026-08-10 | Reviewed emergency trolley equipment. Some of the items were found missing and not in the designated compartments. Interacted with officers & security personnel about their roles and resposibilities during emergencies | 2.5 | Emergency response preparedness reviewed | 1919 | SECUNDERABAD TERMINAL | Emergency trolley to be regularly inspected & all equipment to be placed at their designated compartments. Live fire training to beimparted to all contract workmen. | SOD | Marketing | SCR | 2026-01-27 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-27 | AUD-2026-03-2000011062ACN-2026-03-4000123663 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123663 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123663 | 532 | 8294 | 21 | 8294 | 265 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123663 | AUD-2026-03-2000011062ACN-2026-03-4000123663 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | Continuous improvement being carried out, Compliance is going on, Marking this complied as a repetitive point in Next Visit. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123665 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | MDSA, TAS , SSA compliances are revieved . | 3.18 | OISD/MDSA/SSA compliance reviewed | 1919 | SECUNDERABAD TERMINAL | Advised location to ensure 100 % compliance as per target date. | SOD | Marketing | SCR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-03-2000011062ACN-2026-03-4000123665 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123665 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123665 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123665 | AUD-2026-03-2000011062ACN-2026-03-4000123665 | 21 | 21 | 26 | 80 | 1 | -12 | 57 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | TK5C repair completed and TK3D Comprehensive tank inspections completed. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123669 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | TK 5C repair , Comprehensive tank inspections to be complted | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1919 | SECUNDERABAD TERMINAL | TK 5C repair , Comprehensive tank inspections to be completed as per given target dates | SOD | Marketing | SCR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011062ACN-2026-03-4000123669 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123669 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123669 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123669 | AUD-2026-03-2000011062ACN-2026-03-4000123669 | 21 | 21 | 26 | 80 | 1 | -12 | 44 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | VRU is in working condition, AMC order has been placed for effective monitoring and improvement of recovery rate. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123670 | Closed | SATYENDRA CHOURASIA | 2026-08-05 |  | 6.1 |  | 1919 | SECUNDERABAD TERMINAL | Reasons to be analysed and corrective measures to be taken to improve the recovery rate. | SOD | Marketing | SCR | 2026-02-28 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-28 | AUD-2026-03-2000011062ACN-2026-03-4000123670 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123670 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123670 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123670 | AUD-2026-03-2000011062ACN-2026-03-4000123670 | 21 | 21 | 26 | 80 | 1 | -12 | 26 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 |  | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123671 | Closed |  |  |  | 6.2 |  | 1919 | SECUNDERABAD TERMINAL | Safety Items list displayed | SOD | Marketing | SCR | 2026-01-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-01-31 | AUD-2026-03-2000011062ACN-2026-03-4000123671 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123671 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123671 | 532 | 8294 | 21 | 8294 | 261 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123671 | AUD-2026-03-2000011062ACN-2026-03-4000123671 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | NA | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123672 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | NA | 6.3 | NA | 1919 | SECUNDERABAD TERMINAL | NA | SOD | Marketing | SCR | 2026-01-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-01-31 | AUD-2026-03-2000011062ACN-2026-03-4000123672 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123672 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123672 | 532 | 8294 | 21 | 8294 | 261 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123672 | AUD-2026-03-2000011062ACN-2026-03-4000123672 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | Gland leakage arrested. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123673 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | Gland leaks observed for Fire Engines | 6.4 |  | 1919 | SECUNDERABAD TERMINAL | XX | SOD | Marketing | SCR | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-08-31 | AUD-2026-03-2000011062ACN-2026-03-4000123673 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123673 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123673 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123673 | AUD-2026-03-2000011062ACN-2026-03-4000123673 | 21 | 21 | 26 | 80 | 1 | -12 | 52 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | Water testing reports for fire water tanks being maintained from August month onwards. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123674 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | Water testing reports for fire water tanks not available | 6.5 |  | 1919 | SECUNDERABAD TERMINAL | Water testing reports for fire water tanks to be maintained | SOD | Marketing | SCR | 2026-02-28 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-28 | AUD-2026-03-2000011062ACN-2026-03-4000123674 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123674 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123674 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123674 | AUD-2026-03-2000011062ACN-2026-03-4000123674 | 21 | 21 | 26 | 80 | 1 | -12 | 26 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | Live Fire Training for Security Guard conducted on 04-06.08.2026. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123675 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | Live Fire simulation training is pending for security guards | 6.6 |  | 1919 | SECUNDERABAD TERMINAL | XX | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011062ACN-2026-03-4000123675 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123675 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123675 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123675 | AUD-2026-03-2000011062ACN-2026-03-4000123675 | 21 | 21 | 26 | 80 | 1 | -12 | 44 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | Continuous improvement being carried out, Compliance is going on, Marking this complied as a repetitive point in Next Visit. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129553 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | Recent review recommendations were reviewed along with pending audit points of 4 - SSA & 3- MDSA FY (2024-25) & 5- MDSA FY (2025-26) | 1.4 | Earlier action points status checked | 1919 | SECUNDERABAD TERMINAL | Compliance of all the MDSA FY (2024-25) & FY (2025-26) to be and SSA pending points at the earliest possible | SOD | Marketing | SCR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-05-2000012102ACN-2026-05-4000129553 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129553 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129553 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129553 | AUD-2026-05-2000012102ACN-2026-05-4000129553 | 21 | 21 | 27 | 80 | 1 | -12 | 57 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | Following items are now made available in Emergencey Response Toolkit Trolley: 1. Tester 2. Hand siren not working as handle is not fitted properly 3. Petrloeum product cleaning chemical | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129556 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | Checked Emergencey Response Toolkit Trolley, following items are not available: 1. Tester 2. Hand siren not working as handle is not fitted properly 3. Petrloeum product cleaning chemical | 2.5 | Emergency response preparedness reviewed | 1919 | SECUNDERABAD TERMINAL | Emergency Trolley missing items to be provided | SOD | Marketing | SCR | 2026-05-20 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129556 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129556 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129556 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129556 | AUD-2026-05-2000012102ACN-2026-05-4000129556 | 21 | 21 | 27 | 80 | 1 | -12 | 38 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | All NPCB projects completed within timelines. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129560 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | All NPCB projects to be completed within timelines | 4.3 | Project progress reviewed | 1919 | SECUNDERABAD TERMINAL | All NPCB projects to be completed within timelines | SOD | Marketing | SCR | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-05-2000012102ACN-2026-05-4000129560 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129560 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129560 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129560 | AUD-2026-05-2000012102ACN-2026-05-4000129560 | 21 | 21 | 27 | 80 | 1 | -12 | 52 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | Since 200 KVA is more than 20 years old, it has been planned for disposal as Scrap. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129562 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | 200 KVA DGs action plan to be made. | 6.1 |  | 1919 | SECUNDERABAD TERMINAL | 200 KVA DGs action plan to be made. | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129562 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129562 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129562 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129562 | AUD-2026-05-2000012102ACN-2026-05-4000129562 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-05 | TAS Audit Pending Points status has been reviewed and compliance is in progress. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129572 | Closed | SATYENDRA CHOURASIA | 2026-08-05 | TAS Audit Pending Points status to be checked | 6.11 |  | 1919 | SECUNDERABAD TERMINAL | TAS Audit Pending Points status to be checked | SOD | Marketing | SCR | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-05-2000012102ACN-2026-05-4000129572 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129572 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129572 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012102ACN-2026-05-4000129572 | AUD-2026-05-2000012102ACN-2026-05-4000129572 | 21 | 21 | 27 | 80 | 1 | -12 | 39 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | Near Miss Reporting has been improved as 13 near miss has been reported in aarohan portal in last 10 days. Along with that a separate register started to record all near misses and safety suggestions reported by Contract Workmen and also top 5 suggestions every month will be selected and rewarded. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147049 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | Near Miss Reporting to be improved. | 6.3 |  | 1919 | SECUNDERABAD TERMINAL | Near Miss Reporting to be improved. | SOD | Marketing | SCR | 2026-10-31 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147049 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147049 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147049 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147049 | AUD-2026-08-2000016364ACN-2026-08-4000147049 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 51
NIDAMARTHI NAGA KIRAN | 2026-08-24 | SATYENDRA CHOURASIA | 2026-08-22 | CCTV 92 days coverage disk error message has been checked, CCTV 92 days coverage now available. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147903 | Closed | SATYENDRA CHOURASIA | 2026-08-22 | CCTV 92 days coverage disk error message is appearing | 6.7 |  | 1919 | SECUNDERABAD TERMINAL | Location to take up with vendor for corrective action | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147903 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147903 | 2026-08-06 19:00 | 73.9622 | 357 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147903 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016364ACN-2026-08-4000147903 | AUD-2026-08-2000016364ACN-2026-08-4000147903 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Completd updation of TT crew data | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000148659 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Ensure updation of TT crew data and approval by June end | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Ensure updation of TT crew data and approval by June end | SOD | Marketing | SCR | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-08-2000016174ACN-2026-08-4000148659 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148659 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148659 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016174ACN-2026-08-4000148659 | AUD-2026-08-2000016174ACN-2026-08-4000148659 | 21 | 21 | 27 | 80 | 3 | 2 | 44 | 51
|  | PULI JYOTSNA LATHA | 2026-08-22 | Complied 19/22 points | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000148658 | Open | PULI JYOTSNA LATHA | 2026-08-22 | Complied 16/22 actin points of previous Senior Management Inspection observations. | 1.4 | Earlier action points status checked | 1992 | VISAKH WHITE OIL TERMINAL | Comply the same in time bound manner within target dates | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016174ACN-2026-08-4000148658 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148658 | 2026-09-17 20:00 | 31.9205 | 394 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148658 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016174ACN-2026-08-4000148658 |  | AUD-2026-08-2000016174ACN-2026-08-4000148658 | 21 |  | 27 | 80 | 3 | 2 | 57
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Trip turnaround improvement plan has been implemented and ensuring 2.5 trips per day | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000148660 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Action to be taken for NRD TT in line with ITDG guildelines Chalk out plan for improving CO TT trips per day to 3 | 1.8 | Improvement plans discussed | 1992 | VISAKH WHITE OIL TERMINAL | Action to be taken for NRD TT in line with ITDG guildelines Chalk out plan for improving CO TT trips per day to 3 | SOD | Marketing | SCR | 2026-07-31 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-07-31 | AUD-2026-08-2000016174ACN-2026-08-4000148660 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148660 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148660 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016174ACN-2026-08-4000148660 | AUD-2026-08-2000016174ACN-2026-08-4000148660 | 21 | 21 | 27 | 80 | 3 | 2 | 48 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Faulty light fittings replaced | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000148661 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | LUX level observed: TTP - 25, TTG -120 (Bay 14), 33 (Bay 13), TK103 MOV-165, TK403 MOV - 89, Secondary road Dyke 1&4 - 8.3, PPH - 39/180/17, FWPH - 90/125 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1992 | VISAKH WHITE OIL TERMINAL | 2 lights not working in PPH, 1 light not working TTG Bay 13 | SOD | Marketing | SCR | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-08-2000016174ACN-2026-08-4000148661 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148661 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148661 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148661 | AUD-2026-08-2000016174ACN-2026-08-4000148661 | 21 | 21 | 27 | 80 | 3 | 2 | 44 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Emergency gate Key management system is in place with hooter at 24*7 manned security main gate. | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000148662 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Emergency response preparedness checked RIM Seal, HVLR , MEFG operated by location officers, Emergency Trolley checked. Emergency Gate hooter is coming at Visitor gate, however no local hooter at the gate is available. Also, possibility of TAS integration to be explored. | 2.5 | Emergency response preparedness reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Emergency Trolley items to be made available in slots as per displayed name plate - Medical kit, Electrical tester, SCABA set & Oxygen Cylinder etc. Requirement of local hooter at the emergency gate to be checked. | SOD | Marketing | SCR | 2026-07-15 | POOR COMMUNICATION | 8 | EMERGENCY | S2 | F4 | 2026-07-15 | AUD-2026-08-2000016174ACN-2026-08-4000148662 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148662 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148662 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148662 | AUD-2026-08-2000016174ACN-2026-08-4000148662 | 21 | 21 | 27 | 80 | 3 | 2 | 46 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | all 86 CCTV cameras are online | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000148663 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | All 86 cameras are working, however 2 cameras - Main Gate IN OUT & Licensed Entry Gate view adjustment is required. Trimming of tree branches near boundary is required obstructing complete view of Camera TWG BS Perim Fxd 08 | 2.6 | CCTV functioning checked | 1992 | VISAKH WHITE OIL TERMINAL | Corrective action to be taken for CCTV nos mentioned in observation. | SOD | Marketing | SCR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-08-2000016174ACN-2026-08-4000148663 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148663 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148663 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148663 | AUD-2026-08-2000016174ACN-2026-08-4000148663 | 21 | 21 | 27 | 80 | 3 | 2 | 46 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Bags checking is done before DFMD and hand/HHMD frisking is being carried out. | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-08-4000148665 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Full field round completed (gantry/tank farm/Solar/product pump house/siding/control room/Fire Pump House/security/admin) | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1992 | VISAKH WHITE OIL TERMINAL | Bags checking to be done before DFMD, hand frisking not done | SOD | Marketing | SCR | 2026-06-20 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-20 | AUD-2026-08-2000016174ACN-2026-08-4000148665 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148665 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148665 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148665 | AUD-2026-08-2000016174ACN-2026-08-4000148665 | 21 | 21 | 27 | 80 | 3 | 2 | 42 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Necessary rectification job has been carried out, and resolved | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-08-4000148666 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Fire Engine Sequence checked - S2, 2B, 3C, A, S1 | 4.2 | Maintenance activities reviewed | 1992 | VISAKH WHITE OIL TERMINAL | FE 2B - DP observed 25 bar against 10-11 bar, FE 3C - CWP 0.5 bar against 1-2 bar | SOD | Marketing | SCR | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-31 | AUD-2026-08-2000016174ACN-2026-08-4000148666 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148666 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148666 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148666 | AUD-2026-08-2000016174ACN-2026-08-4000148666 | 21 | 21 | 27 | 80 | 3 | 2 | 48 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Completed and closed in system | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-08-4000148667 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Projects 1) MOV with actuator at Jetty 2) Full Bore Valve to be completed & closed by June 26 | 4.3 | Project progress reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Projects 1) MOV with actuator at Jetty 2) Full Bore Valve to be completed & closed by June 26 | SOD | Marketing | SCR | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-08-2000016174ACN-2026-08-4000148667 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148667 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148667 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148667 | AUD-2026-08-2000016174ACN-2026-08-4000148667 | 21 | 21 | 27 | 80 | 3 | 2 | 44 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Scrap segregation and valuation is in progress | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-08-4000148668 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Scrap to be liquidated | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1992 | VISAKH WHITE OIL TERMINAL | Scrap to be liquidated | SOD | Marketing | SCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016174ACN-2026-08-4000148668 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148668 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148668 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148668 | AUD-2026-08-2000016174ACN-2026-08-4000148668 | 21 | 21 | 27 | 80 | 3 | 2 | 57 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | Advised corrections are implemented in monthly MIS report | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-08-4000148669 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Following corrections to be made in monthly MIS reporting : Average TT filling time, Average TT/Bay in 2 hrs, Online Density Performance of MS/HSD TTs only to be considered | 6.1 |  | 1992 | VISAKH WHITE OIL TERMINAL | Following corrections to be made in monthly MIS reporting : Average TT filling time, Average TT/Bay in 2 hrs, Online Density Performance of MS/HSD TTs only to be considered | SOD | Marketing | SCR | 2026-06-30 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-08-2000016174ACN-2026-08-4000148669 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148669 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148669 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016174ACN-2026-08-4000148669 | AUD-2026-08-2000016174ACN-2026-08-4000148669 | 21 | 21 | 27 | 80 | 3 | 2 | 44 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-07-04 | LEDs replacement done at all HMTs, and observed LUX levels in line with OISD even in secondary roads | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125063 | Closed | PULI JYOTSNA LATHA | 2026-07-04 | Lux levels checked . TT Gantry Bay 15 - 71, Bay 16- 32 , Some lights are not working in TT Gantry, Gantry 1 front side -17, Bay no 7 -56 , Product Pump House 100, TK 201 ROSOV platform -35, Tank 206 ROSOV platform -35. manifold area - 65, Secondary road near behind PH -2.0 , Wagon Gantry - platforAdmin - 320 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1992 | VISAKH WHITE OIL TERMINAL | Lux levels on roads is low and not meeting requirements . Additional lights to be provided to improve lux levels wherever the Lux Levels are not meeting the requirements | SOD | Marketing | SCR | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011314ACN-2026-03-4000125063 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125063 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125063 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125063 | AUD-2026-03-2000011314ACN-2026-03-4000125063 | 21 | 21 | 26 | 80 | 3 | 2 | 44 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-07-04 | Repair work was done | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125073 | Closed | PULI JYOTSNA LATHA | 2026-07-04 | Full field round completed (gantry/tank farm/product pump house/siding/control room/Fire Pump House/security/admin) | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1992 | VISAKH WHITE OIL TERMINAL | In Dyke no 2 the dyke drain cracked due to settlement to be repaired. | SOD | Marketing | SCR | 2026-05-30 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-30 | AUD-2026-03-2000011314ACN-2026-03-4000125073 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125073 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125073 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125073 | AUD-2026-03-2000011314ACN-2026-03-4000125073 | 21 | 21 | 26 | 80 | 3 | 2 | 39 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-24 | Location has coordinated with VR for arranging the LFT for security personnels | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125078 | Closed | PULI JYOTSNA LATHA | 2026-08-24 | Live Fire Training of new security gaurds is pending | 6.2 |  | 1992 | VISAKH WHITE OIL TERMINAL | Live Fire Training of new security gaurds to be given at the earliest | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011314ACN-2026-03-4000125078 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125078 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125078 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125078 | AUD-2026-03-2000011314ACN-2026-03-4000125078 | 21 | 21 | 26 | 80 | 3 | 2 | 44 | 51
BUDAMPATI GOPALA KRISHNA | 2026-08-24 | PULI JYOTSNA LATHA | 2026-08-22 | E diary observations are being updated | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000148657 | Closed | PULI JYOTSNA LATHA | 2026-08-22 | Ensure updation of E diary observations daily 5 nos in portal | 1.3 | Pending issues reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Ensure updation of E diary observations daily 5 nos in portal | SOD | Marketing | SCR | 2026-06-25 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-25 | AUD-2026-08-2000016174ACN-2026-08-4000148657 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148657 | 2026-09-17 20:00 | 31.9205 | 357 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148657 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016174ACN-2026-08-4000148657 | AUD-2026-08-2000016174ACN-2026-08-4000148657 | 21 | 21 | 27 | 80 | 3 | 2 | 43 | 51
ARYA VIPIN KUMAR | 2026-08-25 | ARYA VIPIN KUMAR | 2026-08-01 | Complied.Location has identified Mukesh Kumar (Gunman) as trained driver for heavy vehicle. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122074 | Closed | VERMA RAHUL | 2026-08-01 | Location has not yet identified such person in the location | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1128 | MATHURA TERMINAL | Location to identify such person | SOD | Marketing | NUZ | 2026-03-05 | POOR COMMUNICATION | 1 | EMERGENCY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010909ACN-2026-02-4000122074 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122074 | 2026-09-18 | 31.7538 | 358 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122074 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122074 | AUD-2026-02-2000010909ACN-2026-02-4000122074 | 21 | 21 | 26 | 80 | 14 | 13 | 27 | 52
NIMDEO AMIT VINAYAK | 2026-08-25 |  |  | Refresher training for all the members of FOC has been planned in two phases in 3rd week of March | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125553 | Closed | AGARWAL VIPUL | 2026-03-18 | Mock Drill Dtd: 08/10/2025, with scenerion of Product Leakage from MS pump No-19 was reviewed.Response time was found to be satisfactory as per records. Following short comings were observed: 1. Emergency trolley Reached late at the site 2. All Clear signal was given before head count was completed by security guard | 2.1 | Fire drill conducted in last 6 months (surprise) | 1216 | BAHADURGARH TERMINAL | Proper training shall be imparted to all teams as per the Fire Organization Chart (FOC). Clear understanding of roles and responsibilities should be ensured among all team members. | SOD | Marketing | NZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125553 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125553 | 2026-09-05 | 44.7538 | 358 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125553 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125553 | AUD-2026-03-2000011128ACN-2026-03-4000125553 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 52
NIMDEO AMIT VINAYAK | 2026-08-25 |  |  | a)Refresher training program for officers and Contract Emoloyees on HVLR Operation has been planned on 20.03.2026 b)Foam Thicknessof HVLR 3 found to be satisfactory | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125554 | Closed | AGARWAL VIPUL | 2026-03-18 | Double contingency fire mock drill was conducted on 09/03/2026 at 1235 hours at Bahadurgarh Terminal, considering the scenario of aVapour Cloud Explosion in the VRU shed and a pool fire at TK-12. The sprinklers of surrounding tanks, namely Tank No. 11, Tank No. 13, and Tank No. 27, operated satisfactorily. MEFG of Tank No-12 dyke operated satisfactorily. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1216 | BAHADURGARH TERMINAL | a) Operators of HVLR and Foam Monitor should be provided adequate training to ensure proper operation of the equipment. b) Foam blanket thickness observed during the operation of HVLR-03 was found to be inadequate; the system should be checked and necessary corrective actions taken to ensure effective foam generation. | SOD | Marketing | NZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125554 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125554 | 2026-09-05 | 44.7538 | 358 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125554 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125554 | AUD-2026-03-2000011128ACN-2026-03-4000125554 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 52
NIMDEO AMIT VINAYAK | 2026-08-25 |  |  | Non functional CCTV repaired | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125557 | Closed | NIMDEO AMIT VINAYAK | 2026-08-25 | Tot. 122 no of CCTV's are available at the location and all CCTV's are working except 1 no of CCTV which is not working. Also 92 days CCTV recording is available. | 2.6 | CCTV functioning checked | 1216 | BAHADURGARH TERMINAL | The non-functional CCTV should be repaired at the earliest to ensure 100% surveillance coverage at the location. | SOD | Marketing | NZ | 2026-03-20 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000011128ACN-2026-03-4000125557 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125557 | 2026-09-05 | 44.7538 | 358 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125557 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125557 | AUD-2026-03-2000011128ACN-2026-03-4000125557 | 21 | 21 | 26 | 80 | 9 | 9 | 29 | 52
NIMDEO AMIT VINAYAK | 2026-08-25 |  |  | Necessary ractification made in HVLR 3 on the same day.Checked functionality of remaining HVLRs and found to be satisfactory. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125559 | Closed | AGARWAL VIPUL | 2026-03-18 | HVLR - Total 17 Nos of HVLR is available at the Location. HVLR No. 04 – Checked for its movement in all directions and found satisfactory. HVLR No. 03 was operated by Sh. Dinesh Meena. The throughput capacity of the HVLR is 1000 GPM. The officer was found to bewell acquainted with its operation.However, during the operation, only a water jet was discharged from Nozzle and foam induction did not take place. Upon inspection, the circlip of the foam pick-up line was found to be loose, resulting in failure of foam suction. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1216 | BAHADURGARH TERMINAL | Proper preventive maintenance of all HVLR's shall be ensured to maintain their operational readiness at all times. | SOD | Marketing | NZ | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125559 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125559 | 2026-09-05 | 44.7538 | 358 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125559 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125559 | AUD-2026-03-2000011128ACN-2026-03-4000125559 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 52
NIMDEO AMIT VINAYAK | 2026-08-25 | ANKIT KUMAR | 2026-08-21 | Checking of Functionality and availiability of Foam barrel of all Foam Monitors is carried out. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125561 | Closed | ANKIT KUMAR | 2026-08-21 | Foam Monitor - There are 112 Nos of Foam Monitors installed at the Location. Foam Monitor No: 100 near railway siding workers room was operated by Shri. Kamal and the officer was found to be acquainted with the operation of the Foam Monitors. However, some debrisfound stuck in the Nozzle and foam barrel was found to be empty near the monitor | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1216 | BAHADURGARH TERMINAL | Proper preventive maintenance of all Foam Monitors shall be ensured to maintain their operational readiness at all times. Additionally, 100% availability of foam compound shall be maintained to ensure immediate response capability during emergencies. | SOD | Marketing | NZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125561 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125561 | 2026-09-05 | 44.7538 | 358 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125561 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125561 | AUD-2026-03-2000011128ACN-2026-03-4000125561 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 52
POTHALA VENKATA RAO | 2026-08-25 | M.RAJKUMAR | 2026-08-03 | Location received MDP with BPC as primary source of supply. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142951 | Closed | M.RAJKUMAR | 2026-08-03 | As rake inputs from Dharmapuri are unrealiable in terms of transit time, PLT from BPC Irugur to be kept as primary source of input. | 1.5 | HQO / Zonal support required identified | 1856 | COIMBATORE DEPOT | Zone to take up with S&D to ensure that BPC-Irugur forms part of MDP | SOD | Marketing | SZ | 2027-07-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2027-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142951 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142951 | 2026-08-28 17:00 | 52.0455 | 358 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142951 | 532 | 8294 | 21 | 8294 | -284 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142951 | AUD-2026-07-2000015339ACN-2026-07-4000142951 | 21 | 21 | 27 | 80 | 0 | 1 | 100 | 52
[5 empty] | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150005 | Open |  |  | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1656 | DURGAPUR DEPOT | 1. Pending Scrap disposal to be expedited (Repeat Point) 2. Calibration verification for TTs to be done and records maintained (Repeat Point) | SOD | Marketing | EZ | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000017103ACN-2026-08-4000150005 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150005 | 2026-08-07 13:00 | 73.2122 | 394 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150005 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017103ACN-2026-08-4000150005 |  | AUD-2026-08-2000017103ACN-2026-08-4000150005 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150029 | Open |  |  | Maintenance activity found satisfactory. However, 4 no. of barrels (2 empty) found lying inside the Pump House. 1 no. of Pump marked as not in use as per below details found inside pump house. Pump no. 4, 11 KW, 15 HP, 415 V, 20 Amp and 1475 RMP Unidentified loose end of cable found near pump house, near store house area towards the planning room. Sand lying at TT out gate. 1 no. ofold AC lying beside the lube godown (All above are repeat points) | 4.2 | Maintenance activities reviewed | 1656 | DURGAPUR DEPOT | Location to declare the pump as surplus inventory in the designated portal. Cable dressing to be ensured and cables not required to be removed/ make as per the requirement. | SOD | Marketing | EZ | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150029 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150029 | 2026-08-07 13:00 | 73.2122 | 364 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150029 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017103ACN-2026-08-4000150029 |  | AUD-2026-08-2000017103ACN-2026-08-4000150029 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150030 | Open |  |  | NIL ongoing Project. BG receipt from NHAI to be expedited (This is a repeat point vis-a-vis last quarterly audit). | 4.3 | Project progress reviewed | 1656 | DURGAPUR DEPOT | To be expedited | SOD | Marketing | EZ | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150030 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150030 | 2026-08-07 13:00 | 73.2122 | 364 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150030 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017103ACN-2026-08-4000150030 |  | AUD-2026-08-2000017103ACN-2026-08-4000150030 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150031 | Open |  |  | Location disposed off the scrap in last FY However, Scraps (MS scrap) found lying in the scrap yard. No action taken by location inQ1 (Repeat Point) | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1656 | DURGAPUR DEPOT | Location to complete the scrap disposal and make location scrap free | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-08-2000017103ACN-2026-08-4000150031 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150031 | 2026-08-07 13:00 | 73.2122 | 394 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150031 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017103ACN-2026-08-4000150031 |  | AUD-2026-08-2000017103ACN-2026-08-4000150031 | 21 |  | 27 | 80 | 0 | 0 | 57
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | Both LIC & Mr.Aditya are trained and guiding both JEOs to get knowledge about depot operations. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122845 | Closed | LOGARASU R | 2026-08-26 | Interacted and Motivated all Officers both on 20th morning and on 21st afternoon (1 hour each). Told the young officers to learn from seniors, go through IS codes, SOPs and OISD standards. Get involved in fir=eld activities as there is no substitution to hands onwork & learning. Officers keenly absorbed the tips and advise given during the interaction. | 1.1000000000000001 | Interaction with all officers (1–1.5 hrs) | 1871 | MADURAI DEPOT | Both LIC & Mr.Aditya, Operations Officers should train and guide both JEOs Mr.Raju Putta and Mr.Aravind Kumar in learning the Operational, M&R, Safety , TAs and other related activities quickly to handle the same indenpendently and confidently. | SOD | Marketing | SZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010767ACN-2026-03-4000122845 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122845 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122845 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010767ACN-2026-03-4000122845 | AUD-2026-03-2000010767ACN-2026-03-4000122845 | 21 | 21 | 26 | 80 | 2 | 2 | 33 | 52
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | Takenup with district collecter and neccesary instructions given to tahsildar office and name also changed in land survey and tender also floated and finalayzed. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122846 | Closed | LOGARASU R | 2026-08-26 | change of name in land survey number and Floating/Finalysing of SSP tender for railways. | 1.3 | Pending issues reviewed | 1871 | MADURAI DEPOT | To get approval from government authorities for change of name. | SOD | Marketing | SZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 3 | ASSET INTEGRITY | S3 | F1 | 2026-03-31 | AUD-2026-03-2000010767ACN-2026-03-4000122846 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122846 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122846 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010767ACN-2026-03-4000122846 | AUD-2026-03-2000010767ACN-2026-03-4000122846 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 52
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-06 | Required SAP T-codes are provided for newly joined JEOs | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122847 | Closed | LOGARASU R | 2026-08-06 | SAP Menu Access support for E0 Officers & procurement of land for additional TT parking | 1.5 | HQO / Zonal support required identified | 1871 | MADURAI DEPOT | To provide required SAP menu for new officers. | SOD | Marketing | SZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 3 | ASSET INTEGRITY | S1 | F3 | 2026-03-15 | AUD-2026-03-2000010767ACN-2026-03-4000122847 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122847 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122847 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010767ACN-2026-03-4000122847 | AUD-2026-03-2000010767ACN-2026-03-4000122847 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 52
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149438 | Open |  |  | Yes, Location is advised to cose all open pending points on priority | 1.6 | Expectations clearly communicated to officers | 1435 | GWALIOR DEPOT | All open points of previous visits are related to ongoing TAS Revamp, ACS Maintenance and Railway Siding Sprinklar Work. All these jobs are in progress and are expected to be completed by 30.09.2026, 15.10.2026 & 30.10.2026 respectively. | SOD | Marketing | CEN | 2026-10-30 |  | 3 |  | S1 | F3 | 2026-10-30 | AUD-2026-08-2000017055ACN-2026-08-4000149438 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149438 | 2026-08-22 19:00 | 57.9622 | 424 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149438 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017055ACN-2026-08-4000149438 |  | AUD-2026-08-2000017055ACN-2026-08-4000149438 | 21 |  | 27 | 80 | 2 | 2 | 61
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149441 | Open |  |  | Except at Main Gate 2nd Exit, Access control system is functional at all other locations, i.e. Main Gate 1st Entry & Exit, Main Gate 2nd Entry and Licensed area Entry & Exit. The display touch screen is not working at Main Gate 2nd Exit Access Control. The same is sent for repair. | 2.8 | Access control systems checked | 1435 | GWALIOR DEPOT | Location to follow up and get repaired display touch screen of Main Gate 2nd Exit Access control system on priority and ensure functionality of this CBAC system. | SOD | Marketing | CEN | 2026-10-15 |  | 8 |  | S2 | F4 | 2026-10-15 | AUD-2026-08-2000017055ACN-2026-08-4000149441 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149441 | 2026-08-22 19:00 | 57.9622 | 409 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149441 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017055ACN-2026-08-4000149441 |  | AUD-2026-08-2000017055ACN-2026-08-4000149441 | 21 |  | 27 | 80 | 2 | 2 | 59
|  |  |  | 1) The open path HCD at TLF Pump House to be checked and rectified as it failed to generate an alarm. 2) Permissible Stop command to be integrated under TAS revamping Project | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149442 | Open | YASH SHARMA | 2026-10-16 | 1) HVLR-1 near TK-1 (Dyke-1) was oeprated and throw observed was adequate. Operated Point and Open type HCD at TWD Pump House. Openpath HCD was also operated at TLF Pump House and at Dyke-1 (TK-4) area. Dyke Valve indicator operated for Dyke-1& 2. 2) ESD-10 operated. However, upon activation of ESD-10, TLF Pumps stopped, Tank went to Dormant mode, but TT Gantry DCV remain operational. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1435 | GWALIOR DEPOT | 1) The open path HCD at TLF Pump House to be checked and rectified as it failed to generate an alarm. 2) To check the same by operating other ESD, verify the same and get it rectified on top priority. | SOD | Marketing | CEN | 2026-08-30 |  | 15 |  | S3 | F5 | 2026-08-30 | AUD-2026-08-2000017055ACN-2026-08-4000149442 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149442 | 2026-08-22 19:00 | 57.9622 | 363 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149442 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017055ACN-2026-08-4000149442 |  | AUD-2026-08-2000017055ACN-2026-08-4000149442 | 21 |  | 27 | 80 | 2 | 2 | 52
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149443 | Open |  |  | Yes, operated thru cleaner of TT No: MP07 ZP 7150 | 2.14 | TT crew fire extinguisher usage checked | 1435 | GWALIOR DEPOT | TT crew needs referesher training | SOD | Marketing | CEN | 2026-10-15 |  | 8 |  | S2 | F4 | 2026-10-15 | AUD-2026-08-2000017055ACN-2026-08-4000149443 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149443 | 2026-08-22 19:00 | 57.9622 | 409 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149443 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017055ACN-2026-08-4000149443 |  | AUD-2026-08-2000017055ACN-2026-08-4000149443 | 21 |  | 27 | 80 | 2 | 2 | 59
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149444 | Open |  |  | Yes, verified 2 TT's as only 2 bays are functional due to undergoing TAS Revamp. TT Nos: MP07 ZK 9933 and MP07 ZP 7150. Variation upto 4 mm observed in Bay No. 3. | 3.2 | Post-loading dip checks verified | 1435 | GWALIOR DEPOT | Location is advised to recalibrate the bay thru W&M Dept on top priority. | SOD | Marketing | CEN | 2026-09-25 |  | 8 |  | S2 | F4 | 2026-09-25 | AUD-2026-08-2000017055ACN-2026-08-4000149444 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149444 | 2026-08-22 19:00 | 57.9622 | 389 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149444 | 532 | 8294 | 21 | 8294 | 24 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017055ACN-2026-08-4000149444 |  | AUD-2026-08-2000017055ACN-2026-08-4000149444 | 21 |  | 27 | 80 | 2 | 2 | 56
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149447 | Open |  |  | Reviewed. Ethanol Pump of TK-24 is under maintenance | 4.2 | Maintenance activities reviewed | 1435 | GWALIOR DEPOT | Location to get it repaired and put back into service at the earliest. | SOD | Marketing | CEN | 2026-10-30 |  | 6 |  | S2 | F3 | 2026-10-30 | AUD-2026-08-2000017055ACN-2026-08-4000149447 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149447 | 2026-08-22 19:00 | 57.9622 | 424 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149447 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017055ACN-2026-08-4000149447 |  | AUD-2026-08-2000017055ACN-2026-08-4000149447 | 21 |  | 27 | 80 | 2 | 2 | 61
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | Training for fire fighting equipements, TT inspection given also as per OISD 154 Training also provided. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122848 | Closed | LOGARASU R | 2026-08-26 | To provide Training for New Officer, Additional bay and tankages due to shifing of tirunelveli and procurement of land for additional TT parking. | 1.8 | Improvement plans discussed | 1871 | MADURAI DEPOT | Training to be conducted for New JEO Officers and construction of New Bay and tankages. | SOD | Marketing | SZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-15 | AUD-2026-03-2000010767ACN-2026-03-4000122848 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122848 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122848 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010767ACN-2026-03-4000122848 | AUD-2026-03-2000010767ACN-2026-03-4000122848 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 52
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | New Lights changed for lower side at TW Siding and TT gantry front side and LUX lever found okay as per OISD STD. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122849 | Closed | LOGARASU R | 2026-08-26 | Following locations LUX level found to be on lower side at TW Siding and TT gantry front side. Secondary roads and Admin lux levelsmeeting requirement. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1871 | MADURAI DEPOT | Location to meet Lux level as per OISD STD | SOD | Marketing | SZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000010767ACN-2026-03-4000122849 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122849 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122849 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010767ACN-2026-03-4000122849 | AUD-2026-03-2000010767ACN-2026-03-4000122849 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 52
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | Tender floated and finalysed and Sprinklers, Miscellaneous scraps, prover tanks and aluminium scraps are disposed. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122854 | Closed | LOGARASU R | 2026-08-26 | Auction due date is 24th Feb | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1871 | MADURAI DEPOT | Scrap disposal to be completed. | SOD | Marketing | SZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | ENVIRONMENTAL | S1 | F4 | 2026-03-31 | AUD-2026-03-2000010767ACN-2026-03-4000122854 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122854 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122854 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010767ACN-2026-03-4000122854 | AUD-2026-03-2000010767ACN-2026-03-4000122854 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 52
D SAYEEKUMAR | 2026-08-26 | LOGARASU R | 2026-08-26 | Bay 6 Retractable swing ladder replaced and found working. new lights are fixed lux lever found okay as per OISD std. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-03-4000122855 | Closed | LOGARASU R | 2026-08-26 | Bay 6 Retractable swing ladder and Improvement of Lux | 5.0999999999999996 | High priority areas requiring immediate action. | 1871 | MADURAI DEPOT | Bay 6 Retractable swing ladder to be replaced and Lux level to be improved at locations where it is not meeting. | SOD | Marketing | SZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000010767ACN-2026-03-4000122855 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122855 | 2026-07-03 | 108.7538 | 359 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122855 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010767ACN-2026-03-4000122855 | AUD-2026-03-2000010767ACN-2026-03-4000122855 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | Security deployment at Railway siding is discussed at Mutual Aid meeting. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122481 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Interacted with all officers and dicussed on safety, discipline, and teamwork, motivated them by showing how critical role eachone is playing and asked to maintain zero accidents and operational excellence.As advised by IOC, both HPC and BPC have been requested to review the current security arrangements at the siding. At present, security is being managed by separate OMCs. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1485 | AKOLA DEPOT | Location to review assessment of the adequacy of existing security measures. | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-05-31 | AUD-2026-03-2000011118ACN-2026-03-4000122481 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122481 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122481 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122481 | AUD-2026-03-2000011118ACN-2026-03-4000122481 | 21 | 21 | 26 | 80 | 3 | 3 | 39 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | Extra lights are placed for better lux level at gantry. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122483 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Yes, lux level at all operating areas meets OISD STD 244 and are checked monthly and records maintained | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1485 | AKOLA DEPOT | Location to review for improvement in LUX levels at gantry, near bottom loading couplers to avoid shadows at TT valve box while operating after sunset | SOD | Marketing | WZ | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011118ACN-2026-03-4000122483 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122483 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122483 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122483 | AUD-2026-03-2000011118ACN-2026-03-4000122483 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | The self-closing mechanism of the gauge well cap at TK-15 is fitted. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122489 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Inventory checked for TK-15 i.e. MS tank and variation found within permissible limit range. TAS-607.8 Manual-607.7 The self-closing mechanism of the gauge well cap at TK-15 was found to be loose and not properly fitted, requiring repair and secure refixing. | 3.7 | Inventory physical dip of minimum two tanks taken | 1485 | AKOLA DEPOT | Location to take corrective action | SOD | Marketing | WZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011118ACN-2026-03-4000122489 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122489 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122489 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122489 | AUD-2026-03-2000011118ACN-2026-03-4000122489 | 21 | 21 | 26 | 80 | 3 | 3 | 35 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | Old blurred Layout maps replaced and new layout maps displayed. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146521 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Depot layout displayed at the prominent location appears faded and is not clearly visible. | 6.4 | Layout display | 1485 | AKOLA DEPOT | Replace/refurbish the layout and ensure it is displayed in a clearly visible condition. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146521 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146521 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146521 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146521 | AUD-2026-06-2000013155ACN-2026-07-4000146521 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | 500 KVA DG auto changeover settings are done by AMC service person. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146524 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Changeover of the 500 kVA DG set is being carried out manually. | 6.7 | 500 KVA DG | 1485 | AKOLA DEPOT | To check for automatic changeover facility and ensure reliable operation of the DG system. | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146524 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146524 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146524 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146524 | AUD-2026-06-2000013155ACN-2026-07-4000146524 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 52
KATAKAM SRINIVAS | 2026-08-27 | BAGADE AMAR ARUN | 2026-08-20 | Hexane and SKO dispatched from the location. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146520 | Closed | BAGADE AMAR ARUN | 2026-08-20 | Approx 7.5KL of SKO and 13 KL Hexane lies dowmant in SKO | 6.3 | ATF and Hexane | 1485 | AKOLA DEPOT | To arrange for upliftment of same | SOD | Marketing | WZ | 2026-12-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-06-2000013155ACN-2026-07-4000146520 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146520 | 2026-08-24 | 56.7538 | 360 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146520 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146520 | AUD-2026-06-2000013155ACN-2026-07-4000146520 | 21 | 21 | 27 | 80 | 3 | 3 | 70 | 52
|  | SINGH BHOPENDRA | 2026-08-27 | Training shall be provided to security and contract manpower for emergency response procedures.Ensure that all personnel report to the designated assembly point during an emergency, including personnel present in the MCC or Fire Engine Room. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146672 | Completed | SINGH BHOPENDRA | 2026-08-27 | A surprise fire drill was conducted at the ETP during the visit. The following observations were noted: 1.Coordination among all teams was highly appreciable, and the response was prompt and well-organized. 2.The first responder should clearly communicate the emergency location over the VHF set. 3. Security personnel should ensure that all personnel present at the site are accounted at theassembly point. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1157 | BAREILLY DEPOT | Provide traning to Secuirty and contract satff for handing emergency. | SOD | Marketing | NUZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146672 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146672 | 2026-07-16 | 95.7538 | 363 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146672 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015610ACN-2026-07-4000146672 |  | AUD-2026-07-2000015610ACN-2026-07-4000146672 | 21 |  | 27 | 80 | 3 | 3 | 52
|  | SINGH BHOPENDRA | 2026-08-27 | TERM card checked and available with all TT crew. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 | ACN-2026-07-4000146688 | Completed | SINGH BHOPENDRA | 2026-08-27 | Yes intrcat with TT no. crew UK17CA7386 found satisfactory. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1157 | BAREILLY DEPOT | TT drivers awareness on TREM card and availability of card to be chekced for all trucks | SOD | Marketing | NUZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146688 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146688 | 2026-07-16 | 95.7538 | 363 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146688 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015610ACN-2026-07-4000146688 |  | AUD-2026-07-2000015610ACN-2026-07-4000146688 | 21 |  | 27 | 80 | 3 | 3 | 52
SONAR AMIT KUMAR | 2026-08-27 | SINGH BHOPENDRA | 2026-08-27 | Security is checking the documents of Sitarganj TTs at the TT Ingate. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146674 | Closed | SINGH BHOPENDRA | 2026-08-27 | main gate security documentation checks for Sitarganj are not doing | 2.4 | Security alertness checked (night-halt / surprise checks) | 1157 | BAREILLY DEPOT | Need to check all entering tank trucks documents verification | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146674 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146674 | 2026-07-16 | 95.7538 | 360 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146674 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146674 | AUD-2026-07-2000015610ACN-2026-07-4000146674 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-27 | SINGH BHOPENDRA | 2026-08-27 | Location takeup with OEM and CCTv screen has been working after repair work of work station. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146675 | Closed | SINGH BHOPENDRA | 2026-08-27 | Yes functioning | 2.6 | CCTV functioning checked | 1157 | BAREILLY DEPOT | Control room CCTV screen under maintenance, corrective atction to be taken for repair. | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146675 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146675 | 2026-07-16 | 95.7538 | 360 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146675 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146675 | AUD-2026-07-2000015610ACN-2026-07-4000146675 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-27 | SINGH BHOPENDRA | 2026-08-27 | The location is carrying out daily closure of VA and Novex alerts. However, alerts generated during holidays or off-hours are escalated for necessary action. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146676 | Closed | SINGH BHOPENDRA | 2026-08-27 | VA alerts checked | 2.7 | VA alerts checked / analysed | 1157 | BAREILLY DEPOT | Regular VA alerts of NOVEX to be attended | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146676 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146676 | 2026-07-16 | 95.7538 | 360 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146676 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146676 | AUD-2026-07-2000015610ACN-2026-07-4000146676 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-27 | SINGH BHOPENDRA | 2026-08-27 | Both pumps/motors are connected to the foam tanks. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146677 | Closed | SINGH BHOPENDRA | 2026-08-27 | Mother tank foam avaialble as per the location requirement | 2.9 | Foam inventory verified | 1157 | BAREILLY DEPOT | foam shed second motor is not connected | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146677 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146677 | 2026-07-16 | 95.7538 | 360 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146677 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146677 | AUD-2026-07-2000015610ACN-2026-07-4000146677 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149844 | Open |  |  | 1. Scrap disposal - AMTA from Mugalsarai 2. VTS and EM lock recovery against blacklisted TT (Nanakdhan Singh) 3. Payment against contaminated product. 4. Idle hexan tank utilisation. | 1.3 | Pending issues reviewed | 1308 | SITARGANJ DEPOT | to complete the pending jobs with specific timelines | SOD | Marketing | NUZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-08-2000016859ACN-2026-08-4000149844 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149844 | 2026-08-26 17:00 | 54.0455 | 424 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149844 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000149844 |  | AUD-2026-08-2000016859ACN-2026-08-4000149844 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149845 | Open |  |  | 1. Auto density invoice printing to be resolved. 2. Last audit point - MDSA compliance pending. (Capital in nature, projects in progress.) | 1.4 | Earlier action points status checked | 1308 | SITARGANJ DEPOT | to coordinate with TAS vendor and to complete on permanent basis | SOD | Marketing | NUZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-08-2000016859ACN-2026-08-4000149845 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149845 | 2026-08-26 17:00 | 54.0455 | 424 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149845 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000149845 |  | AUD-2026-08-2000016859ACN-2026-08-4000149845 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149846 | Open |  |  | 1. Local SO asking for Hexan tank utlisation to SKO. 2. Zonal support in reference to mechanical works of UG tank HHH project. | 1.5 | HQO / Zonal support required identified | 1308 | SITARGANJ DEPOT | regular follow up with the DS on the issue to be done , already discussed with GM DS Lucknow , pls take up further and close early | SOD | Marketing | NUZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-08-2000016859ACN-2026-08-4000149846 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149846 | 2026-08-26 17:00 | 54.0455 | 424 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149846 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000149846 |  | AUD-2026-08-2000016859ACN-2026-08-4000149846 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149849 | Open |  |  | Off-shift drill was conducted at location in reference to scenario at TT gantry. Following deficiencies were observed - 1. Manpower as per FOC to be reveiwed. Against requirement of 3, 2 persons are available. 2. Foam generation from monitor was not adequate. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1308 | SITARGANJ DEPOT | 1. Training to security to handle emergency and off shift drills to be imparted. 2. To match FOC and manpower. 3. Foam generationof all the monitors to be checked on priority. | SOD | Marketing | NUZ | 2026-09-07 |  | 4 |  | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000149849 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149849 | 2026-08-26 17:00 | 54.0455 | 371 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149849 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000149849 |  | AUD-2026-08-2000016859ACN-2026-08-4000149849 | 21 |  | 27 | 80 | 0 | 0 | 53
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150200 | Open |  |  | Lux level was checked. Readings of tank farm found as below against requirement of 20. Near VT Pump - 55 Near operating valve - 80 Near dip hatch - 28 Tank farm no. 3 having 2 no. of HSD tanks is not having lighting arrangement. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1308 | SITARGANJ DEPOT | 1. Lighting arrangement to be made in newly commissioned tank farm. 2. High mast lights to be made functional | SOD | Marketing | NUZ | 2026-09-10 |  | 4 |  | S2 | F2 | 2026-09-10 | AUD-2026-08-2000016859ACN-2026-08-4000150200 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150200 | 2026-08-26 17:00 | 54.0455 | 374 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150200 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150200 |  | AUD-2026-08-2000016859ACN-2026-08-4000150200 | 21 |  | 27 | 80 | 0 | 0 | 54
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150205 | Open |  |  | Checked at security room and licence entry area | 2.8 | Access control systems checked | 1308 | SITARGANJ DEPOT | 1. Post fire drill, after ESD reset, the turstile was found down at security main gate entry. Location to take corrective action. 2. The count of manpower inside location as per DFMD and manual register to be reviewed and daily | SOD | Marketing | NUZ | 2026-09-07 |  | 4 |  | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000150205 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150205 | 2026-08-26 17:00 | 54.0455 | 371 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150205 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150205 |  | AUD-2026-08-2000016859ACN-2026-08-4000150205 | 21 |  | 27 | 80 | 0 | 0 | 53
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150212 | Open |  |  | Colour blindness check not carried out by location. | 2.16 | Eyesight / colour-blindness awareness checked | 1308 | SITARGANJ DEPOT | Location to carry out colour blindness check of TT crew. | SOD | Marketing | NUZ | 2026-09-15 |  | 4 |  | S2 | F2 | 2026-09-15 | AUD-2026-08-2000016859ACN-2026-08-4000150212 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150212 | 2026-08-26 17:00 | 54.0455 | 379 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150212 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150212 |  | AUD-2026-08-2000016859ACN-2026-08-4000150212 | 21 |  | 27 | 80 | 0 | 0 | 55
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150213 | Open |  |  | TT UP78HT5304 was checked. The hole where locking rod gets inside the valve box was having larger dia than required as per locking rod. | 3.1 | TT fittings & discipline checked | 1308 | SITARGANJ DEPOT | Location to check all the trucks considering valve box, EM locks and overall fittings. Excel to maintained and tracked. | SOD | Marketing | NUZ | 2026-10-15 |  | 4 |  | S2 | F2 | 2026-10-15 | AUD-2026-08-2000016859ACN-2026-08-4000150213 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150213 | 2026-08-26 17:00 | 54.0455 | 409 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150213 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150213 |  | AUD-2026-08-2000016859ACN-2026-08-4000150213 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150215 | Open |  |  | Yes verified. | 3.5 | EM Lock SOP compliance verified | 1308 | SITARGANJ DEPOT | E- Tag issue to be discussed with Vendor & HQO to finalize. | SOD | Marketing | NUZ | 2026-09-10 |  | 4 |  | S2 | F2 | 2026-09-10 | AUD-2026-08-2000016859ACN-2026-08-4000150215 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150215 | 2026-08-26 17:00 | 54.0455 | 374 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150215 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150215 |  | AUD-2026-08-2000016859ACN-2026-08-4000150215 | 21 |  | 27 | 80 | 0 | 0 | 54
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150216 | Open |  |  | Location is having 180KL tank of hexane which is idle and having dead stock only. Location is communicating with DS SO for utilization. | 3.9 | Abnormal variations / unused assets reviewed | 1308 | SITARGANJ DEPOT | To follow up with DS regularly and to close the issue at the earliest. | SOD | Marketing | NUZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-08-2000016859ACN-2026-08-4000150216 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150216 | 2026-08-26 17:00 | 54.0455 | 424 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150216 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150216 |  | AUD-2026-08-2000016859ACN-2026-08-4000150216 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150217 | Open |  |  | BCU vs MFM data available at location. BCU and MFM readings are not matching. Daily printout not available. | 3.11 | MFM vs BCU totalizer comparison checked | 1308 | SITARGANJ DEPOT | Location to ensure the BCU and MFM readings are matching (same). Also, the BCU MFM totalizer to be printed on daily basis. The sameto be reviewed on daily basis. | SOD | Marketing | NUZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000016859ACN-2026-08-4000150217 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150217 | 2026-08-26 17:00 | 54.0455 | 394 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150217 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150217 |  | AUD-2026-08-2000016859ACN-2026-08-4000150217 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150223 | Open |  |  | OISD not happened at location. MDSA (2025-26) pending points discussed. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1308 | SITARGANJ DEPOT | Location to comply the pending points in time bound manner. Also, the already complied points to be checked and verified. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-08-2000016859ACN-2026-08-4000150223 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150223 | 2026-08-26 17:00 | 54.0455 | 576 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150223 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016859ACN-2026-08-4000150223 |  | AUD-2026-08-2000016859ACN-2026-08-4000150223 | 21 |  | 27 | 80 | 0 | 0 | 83
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-27 | Tank 6 Hooter HCD made working, TLF Pumphouse OPD also working well. New HCD Installation done. | MADURAI IRD VISIT REPORT UPLOAD IN SAP | 2026-02-21 16:25 | AUD-2026-03-2000010767 | 2026-02-20 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122850 | Closed | LOGARASU R | 2026-08-27 | HVLR, HCD and ESD are in working condition. 2 HCD replacement material received, installation is in process. Hooter annunciation atTank 6 and sensitivity of OPD at TLF PH to be checked. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1871 | MADURAI DEPOT | Hooter annunciation at Tank 6 and sensitivity of OPD at TLF PH to be checked. Installation of replacement HCDs to be completed | SOD | Marketing | SZ | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-02-28 | AUD-2026-03-2000010767ACN-2026-03-4000122850 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010767ACN-2026-03-4000122850 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-03-2000010767 - ACN-2026-03-4000122850 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010767ACN-2026-03-4000122850 | AUD-2026-03-2000010767ACN-2026-03-4000122850 | 21 | 21 | 26 | 80 | 2 | 2 | 26 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-27 |  | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138470 | Closed |  |  | (1) Change of name in land survey number (2) Floating/Finalsing of SSP tender for railways to be done (3) Payment of LLF fees to Railways. | 1.3 | Pending issues reviewed | 1871 | MADURAI DEPOT | (1) To get approval from government authorities for change of name in land survey and ensure Sandook open item gets closed. EDC 30.06.2026. (2) Price estimate to be given to DRM Office for for SSP Tender and drainage works. EDC-31.07.2026 (3) Representation given to Madurai DRM to waive off and charge HPCL as per previous agreement. | SOD | Marketing | SZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138470 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138470 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138470 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138470 | AUD-2026-06-2000013157ACN-2026-06-4000138470 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-06 | OPD for TLF pumphouse made working and Installation of HCD also completed. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138474 | Closed | LOGARASU R | 2026-08-06 | HVLR, HCD and ESD are in working condition. 2 HCD replacement material received, installation is in process. Sensitivity of OPD at TLF PH to be checked. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1871 | MADURAI DEPOT | sensitivity of OPD at TLF PH to be checked. Installation of replacement HCDs to be completed | SOD | Marketing | SZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 3 | PROCESS SAFETY | S3 | F1 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138474 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138474 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138474 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138474 | AUD-2026-06-2000013157ACN-2026-06-4000138474 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-06 | Location procured and fixed the lights wherever required and LUX level found meeting as per OISD STD. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138472 | Closed | LOGARASU R | 2026-08-06 | Following locations Luxlevel found to be on lower side at TW Siding and TT gantry front side. Secondary roads and Admin lux levels meeting requirement. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1871 | MADURAI DEPOT | Location to fix few lights at places where Lux levels are not found satisfactory. | SOD | Marketing | SZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 6 | PROCESS SAFETY | S3 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138472 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138472 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138472 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013157ACN-2026-06-4000138472 | AUD-2026-06-2000013157ACN-2026-06-4000138472 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-06 | Location completed on going works during audits are completed. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138476 | Closed | LOGARASU R | 2026-08-06 | Full field round completed. Infrastructure augmentation data communicated to HQO. In regards to additional parking land, it was informed that due to recent elections in TN, the local administration would take it up . Land owners shall provide the data in short time after Govt stabilises. Proposal shall be sent later. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1871 | MADURAI DEPOT | Additional bay and tankages due to shifting of tirunelveli. | SOD | Marketing | SZ | 2026-07-30 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138476 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138476 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138476 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138476 | AUD-2026-06-2000013157ACN-2026-06-4000138476 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-27 | Location completed on going works during audits are completed. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138477 | Closed | LOGARASU R | 2026-08-06 | Work regarding compliances found to be in progress. | 4.2 | Maintenance activities reviewed | 1871 | MADURAI DEPOT | To complete the ongoing works in a time bound manner. | SOD | Marketing | SZ | 2026-07-30 | POOR PERMIT-TO-WORK SYSTEMS | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138477 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138477 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138477 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138477 | AUD-2026-06-2000013157ACN-2026-06-4000138477 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-06 | Location Checking and completing PM Orders for every months. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138479 | Closed | LOGARASU R | 2026-08-06 | 100% PM orders being closed in same month. | 4.4000000000000004 | Quality of PM compliance reviewed | 1871 | MADURAI DEPOT | Location advised to spread the PM orders over entire month and ensure completion of PM orders. | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138479 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138479 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138479 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138479 | AUD-2026-06-2000013157ACN-2026-06-4000138479 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-27 | Bay 6 Retractable swing ladder replaced and found working. new lights are fixed lux lever found okay as per OISD std. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-06-4000138481 | Closed | LOGARASU R | 2026-08-27 | Bay 6 Retractable swing ladder not working properly and Lux level not sufficient | 5.0999999999999996 | High priority areas requiring immediate action. | 1871 | MADURAI DEPOT | Bay 6 Retractable swing ladder to be replaced and Lux level to be improved at locations where it is not meeting especially in the TW unloading area. | SOD | Marketing | SZ | 2026-07-30 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138481 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138481 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138481 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138481 | AUD-2026-06-2000013157ACN-2026-06-4000138481 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
D SAYEEKUMAR | 2026-08-27 | LOGARASU R | 2026-08-27 | Location maintaining COLA, OLA percentages and cycle time. | ZONAL HEAD INSPECTION OF MADURAI NEW IRD | 2026-05-04 | AUD-2026-06-2000013157 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-06-4000138482 | Closed | LOGARASU R | 2026-08-27 | Location maintaining best OLA (98.79%), COLA(98.8%) across SZ locations for FY25-26. Cycle time of 32 min is being maintained. First two hours 5 TTs. | 5.2 | Best practices identified for sharing across zones/locations | 1871 | MADURAI DEPOT | Location was commended on these metrics and advised to keep up the same. | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 2 | ASSET INTEGRITY | S1 | F2 | 2026-07-30 | AUD-2026-06-2000013157ACN-2026-06-4000138482 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013157ACN-2026-06-4000138482 | 2026-07-03 | 108.7538 | 360 | >20 | AUD-2026-06-2000013157 - ACN-2026-06-4000138482 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013157ACN-2026-06-4000138482 | AUD-2026-06-2000013157ACN-2026-06-4000138482 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 52
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150231 | Open |  |  | Day-to-day operational activities were reviewed. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1650 | HALDIA TERMINAL | Location to control TDG violation, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration. Location to take extra attention on route deviation/ unauthorised stoppages by trucks loaded. ATF TTs travel monitoring to continue in coordination with ASF Dumdum officer. Prompt actions to be taken on erring transporters as per ITDG.5 if applicable. Spots identified where multiple TTs are stopping unauthorisedly to be intimated to the police station under which the location is identified. Regular feedback to be shared with zone on action taken on such cases. Barrels lying in the abandoned old PH to be arranged/ removed. Misc. Engineering item lying in and around the abandoned old PH and old MCC panel room to be removed/ arranged. Oldabandoned earth pit for the old PH to be dismantled/ non in use board to be displayed. Foam drum (near the MS tank) caps should be properly fastened to avoid ingress of rain water. | SOD | Marketing | EZ | 2026-09-30 | POOR COMMUNICATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150231 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150231 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150231 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150231 |  | AUD-2026-08-2000016860ACN-2026-08-4000150231 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150233 | Open |  |  | 1. MS Line modification PO job to be expedited. The project is getting in ordinally delayed. 2. M&I Tank Audit points to be complied 3. 3 no. of open MDSA Points of F 24-25 to be complied and closed 4. 46 no. of open MDSA Points of F 25-26 to be complied and closed 5. 5 no. of HLSA open points to be complied and closed 6. 5 no. of open SSA points to be complied and closed 7. Regular E M Lock checking by LIC Master key and records to be maintained 8. Adequate E M Locks & Key inventory at location to be maintained 9. EBMS 20% blending check at TT Gantry to be ensured and records to be maintained (immediate) 10. Strict adherence to the sampling frequency and modalities as per HQO circular to be ensured (immediate). | 1.3 | Pending issues reviewed | 1650 | HALDIA TERMINAL | Expeditious action / compliance to be taken | SOD | Marketing | EZ | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150233 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150233 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150233 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150233 |  | AUD-2026-08-2000016860ACN-2026-08-4000150233 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150235 | Open |  |  | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1650 | HALDIA TERMINAL | 1. Location to upload the 100%TT dip checking data in SAP. 2. Location to ensure the recovery w.r.t VTS equipment charges 3. Location to monitor and take action line with ITDS for the deviations (route/ speed/ night halting etc). 4. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 5. Manual allocation of TT in IMS to be minimised and records with justification to be maintained for all such cases. 6. EM lock handling and Monitoring : Part load must not be executed without prior approval of zonal O&D head, Post decantation OTP to be ensured, programming key usages to be ensured for all TT within a period of max. 1 month. 7. All RTGPs to be reviewed periodically and closed 8. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL cases of scope change in any AR to be done without prior approval. | SOD | Marketing | EZ | 2026-09-15 |  | 10 |  | S2 | F5 | 2026-09-15 | AUD-2026-08-2000016860ACN-2026-08-4000150235 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150235 | 2026-08-20 00:14 | 60.7441 | 379 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150235 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150235 |  | AUD-2026-08-2000016860ACN-2026-08-4000150235 | 21 |  | 27 | 80 | 5 | 5 | 55
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150240 | Open |  |  | Location has total of 68 CCTV Camera and 5 of them were non functional on the date of visit | 2.6 | CCTV functioning checked | 1650 | HALDIA TERMINAL | Random video recording of the CCTV at main gate area were checked and it was advised to make the non functional CCTV to be made functional at the earliest in close coordination with vendor. | SOD | Marketing | EZ | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150240 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150240 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150240 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150240 |  | AUD-2026-08-2000016860ACN-2026-08-4000150240 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150242 | Open |  |  | Checked the functionality of HVLR for MS tank and found functioning satisfactory. 1. One of the foam Pourer of Black Oil tank was non functional at all for TK-15. All Foam pourers to be checked for the smooth functionality, including black oil tanks. 2. WCFM no. 40 found as non functional due to slippage of butterfly valve. 3. Foam line was found leaky near TK-14 (outside tank dyke) (Immediate) | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1650 | HALDIA TERMINAL | To be rectified and ensure NIL recurrence | SOD | Marketing | EZ | 2026-09-10 |  | 5 |  | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150242 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150242 | 2026-08-20 00:14 | 60.7441 | 374 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150242 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150242 |  | AUD-2026-08-2000016860ACN-2026-08-4000150242 | 21 |  | 27 | 80 | 5 | 5 | 54
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150244 | Open |  |  | Monkey ladder in TT no. WB33D8985 found not in alignment with the approved PESO drawing. (Repeat Point, earlier inspection point not closed) | 3.1 | TT fittings & discipline checked | 1650 | HALDIA TERMINAL | Corrective action to be taken. | SOD | Marketing | EZ | 2026-09-10 |  | 5 |  | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150244 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150244 | 2026-08-20 00:14 | 60.7441 | 374 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150244 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150244 |  | AUD-2026-08-2000016860ACN-2026-08-4000150244 | 21 |  | 27 | 80 | 5 | 5 | 54
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150246 | Open |  |  | Review of VTS deviation done on regular basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC. Location to take extra attention on route deviation/ unauthorised stoppages by TTs. Prompt actions to be taken on erring transporters as per ITDG.5 if applicable. Spots identified where multiple TTs are stopping unauthorisedly to be intimated tothe police station under which the location is identified. Regular feedback to be shared with zone on action taken on such cases. | 3.3 | VTS deviations reviewed | 1650 | HALDIA TERMINAL | Location is advised to create the secondary route wherever applicable and action to be taken as per ITDG wherever deemed fit. | SOD | Marketing | EZ | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150246 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150246 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150246 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150246 |  | AUD-2026-08-2000016860ACN-2026-08-4000150246 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150248 | Open |  |  | 100 % Reco done through Manual dips due to WDM issue and dip not getting posted. | 3.8 | Auto vs Manual reconciliation checked | 1650 | HALDIA TERMINAL | Location to closely coordinate with Vendor M/s AST for early installation and functioning of the dip posting. | SOD | Marketing | EZ | 2026-12-31 |  | 4 |  | S1 | F4 | 2026-12-31 | AUD-2026-08-2000016860ACN-2026-08-4000150248 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150248 | 2026-08-20 00:14 | 60.7441 | 486 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150248 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150248 |  | AUD-2026-08-2000016860ACN-2026-08-4000150248 | 21 |  | 27 | 80 | 5 | 5 | 70
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150249 | Open |  |  | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1650 | HALDIA TERMINAL | Black oil, Ethanol and SKO losses to be brought under control | SOD | Marketing | EZ | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150249 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150249 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150249 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150249 |  | AUD-2026-08-2000016860ACN-2026-08-4000150249 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150250 | Open |  |  | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1650 | HALDIA TERMINAL | LIC to review the critical alarms periodically and report if any abnormalities found. Stringent control w.r.t user credentials/password integrity & access to be ensured [BCU, MFM, TAS User Matrix etc.] | SOD | Marketing | EZ | 2026-09-10 |  | 10 |  | S2 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150250 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150250 | 2026-08-20 00:14 | 60.7441 | 374 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150250 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150250 |  | AUD-2026-08-2000016860ACN-2026-08-4000150250 | 21 |  | 27 | 80 | 5 | 5 | 54
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150251 | Open |  |  | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1650 | HALDIA TERMINAL | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-09-10 |  | 10 |  | S2 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150251 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150251 | 2026-08-20 00:14 | 60.7441 | 374 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150251 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150251 |  | AUD-2026-08-2000016860ACN-2026-08-4000150251 | 21 |  | 27 | 80 | 5 | 5 | 54
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150252 | Open |  |  | Local loading record maintained at location: Observations : 1. TT no. is not being mentioned while making the order in BCU for local loading for all the local loads of LSHS premium (July'26 report) 2. One no. of local loading of 0 Ltr. appearing on 29.07.26. Location to review as why this is appearing in the report if loading has not happened. | 3.14 | Local loading checks (if applicable) | 1650 | HALDIA TERMINAL | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-09-10 |  | 10 |  | S2 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150252 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150252 | 2026-08-20 00:14 | 60.7441 | 374 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150252 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150252 |  | AUD-2026-08-2000016860ACN-2026-08-4000150252 | 21 |  | 27 | 80 | 5 | 5 | 54
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150253 | Open |  |  | OISD - NIL pending Point SSA - 5 Pending point (Repeat Point) MDSA - 6 pending point Comprehensive Audit - 46 points | 3.18 | OISD/MDSA/SSA compliance reviewed | 1650 | HALDIA TERMINAL | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150253 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150253 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150253 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150253 |  | AUD-2026-08-2000016860ACN-2026-08-4000150253 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150254 | Open |  |  | MS unloading line project civil work was ongoing. HSD and SKO tank repair work was in progress. Reviewed both the projects and advised for timely closure. | 4.2 | Maintenance activities reviewed | 1650 | HALDIA TERMINAL | Quantitive and qualitative damage assessment (dent/ pin hole etc) to be done for each tank by competent third party before carry out the repairs (Repeat Point) | SOD | Marketing | EZ | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150254 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150254 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150254 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016860ACN-2026-08-4000150254 |  | AUD-2026-08-2000016860ACN-2026-08-4000150254 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150256 | Open |  |  | Location disposed off the scrap in last FY However, few Scraps (MS scrap/Pipe pieces / Cables etc) found lying in the scrap yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1650 | HALDIA TERMINAL | Location to complete the scrap disposal and make location scrap free (Repeat Point) | SOD | Marketing | EZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150256 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150256 | 2026-08-20 00:14 | 60.7441 | 394 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150256 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150256 |  | AUD-2026-08-2000016860ACN-2026-08-4000150256 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000150257 | Open |  |  | 1. Wear and tear found w.r.t Insulation rubber on the swing ladder at TTG, TT locking shed, TT security checking platform 2. It isadvised to use non sparking tool only, in the licenced area. 3. Road carpeting material mixed with bitumen was found lying outsideMS tank dyke TK-17 4. 1 unutilized UG tank identified. Necessary review to be undertaken for its reuse/scrapping (Repeat Point) 5. Haldia TOP is having only single local network connectivity. LIC to take up with IS and get the primary and secondary network thruIS Team. | 6.1 | Additional Observations | 1650 | HALDIA TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-09-15 |  | 5 |  | S1 | F5 | 2026-09-15 | AUD-2026-08-2000016860ACN-2026-08-4000150257 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150257 | 2026-08-20 00:14 | 60.7441 | 379 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150257 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016860ACN-2026-08-4000150257 |  | AUD-2026-08-2000016860ACN-2026-08-4000150257 | 21 |  | 27 | 80 | 5 | 5 | 55
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | TERM card checked and available with all TT crew. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146678 | Closed | SINGH BHOPENDRA | 2026-08-27 | Dicussed at TT gantry with drivers. | 2.15 | TT crew roadside emergency procedures checked | 1157 | BAREILLY DEPOT | TT drivers awareness on TREM card and availability of card to be chekced for all trucks | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146678 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146678 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146678 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146678 | AUD-2026-07-2000015610ACN-2026-07-4000146678 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | LIC has started maintaining the countersigned MFM vs. BCU totalizer report | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146685 | Closed | SINGH BHOPENDRA | 2026-08-27 | Checked | 3.11 | MFM vs BCU totalizer comparison checked | 1157 | BAREILLY DEPOT | daily countersign of LIC to be implemented | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146685 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146685 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146685 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146685 | AUD-2026-07-2000015610ACN-2026-07-4000146685 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | LIC has started maintaining the countersigned Critical alarms of TAS | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146686 | Closed | SINGH BHOPENDRA | 2026-08-27 | Checked | 3.12 | Critical alarms checked & corrective actions reviewed | 1157 | BAREILLY DEPOT | daily countersign of LIC to be implemented | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146686 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146686 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146686 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146686 | AUD-2026-07-2000015610ACN-2026-07-4000146686 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | MOC has been reviewed and closed for the completed work. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146687 | Closed | SINGH BHOPENDRA | 2026-08-27 | Reviewed | 3.17 | MOC status reviewed | 1157 | BAREILLY DEPOT | completed activites to be closed | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146687 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146687 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146687 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146687 | AUD-2026-07-2000015610ACN-2026-07-4000146687 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | RCA for the Bay No. 8 issue has been completed in coordination with the OEM. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146681 | Closed | SINGH BHOPENDRA | 2026-08-27 | blending percentage checked & found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1157 | BAREILLY DEPOT | Bay no. 8 is offline due to etahnol percentage variation | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146681 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146681 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146681 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146681 | AUD-2026-07-2000015610ACN-2026-07-4000146681 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | LIC has started maintaining the countersigned EM locks register. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146682 | Closed | SINGH BHOPENDRA | 2026-08-27 | Yes verified. | 3.5 | EM Lock SOP compliance verified | 1157 | BAREILLY DEPOT | EM locks register countersign by LIC is to be imlemented | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146682 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146682 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146682 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146682 | AUD-2026-07-2000015610ACN-2026-07-4000146682 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | ethanol reco as per the dips cross veriifed at day end. | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146683 | Closed | SINGH BHOPENDRA | 2026-08-27 | Yes verified. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1157 | BAREILLY DEPOT | ethanol reco as per the dips to be cross veriifed at day end. | SOD | Marketing | NUZ | 2026-08-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146683 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146683 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146683 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146683 | AUD-2026-07-2000015610ACN-2026-07-4000146683 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
SONAR AMIT KUMAR | 2026-08-31 | SINGH BHOPENDRA | 2026-08-27 | LIC has started maintaining the countersigned on daily reports | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146684 | Closed | SINGH BHOPENDRA | 2026-08-27 | Yes | 3.8 | Auto vs Manual reconciliation checked | 1157 | BAREILLY DEPOT | daily countersign of LIC to be implemented | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146684 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146684 | 2026-07-16 | 95.7538 | 364 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146684 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146684 | AUD-2026-07-2000015610ACN-2026-07-4000146684 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 52
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150270 | Open |  |  | 1. Observation related to Scrap disposal is pending 2. Observation related to CBAC system is still pending | 1.4 | Earlier action points status checked | 1305 | KANPUR TERMINAL | All earlier pending observeations to be complied | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150270 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150270 | 2026-08-26 17:00 | 54.0455 | 394 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150270 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150270 |  | AUD-2026-08-2000017157ACN-2026-08-4000150270 | 21 |  | 27 | 80 | 4 | 4 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150272 | Open |  |  | The lux level was last checked on 24.08.2026 and was found to be in compliance with the prescribed requirements. However, it was observed that, in an effort to conserve electrical energy, lighting in various pump houses and other facilities had been switched off.This resulted in inadequate visibility and difficulty in identifying the facilities from the ground level, particularly during low-light conditions. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1305 | KANPUR TERMINAL | Adequate lighting should be ensured in and around all critical facilities during night shift. | SOD | Marketing | NCR | 2026-09-15 |  | 4 |  | S2 | F2 | 2026-09-15 | AUD-2026-08-2000017157ACN-2026-08-4000150272 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150272 | 2026-08-26 17:00 | 54.0455 | 379 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150272 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150272 |  | AUD-2026-08-2000017157ACN-2026-08-4000150272 | 21 |  | 27 | 80 | 4 | 4 | 55
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150273 | Open |  |  |  | 2.6 | CCTV functioning checked | 1305 | KANPUR TERMINAL | The non-functional CCTV cameras to be restored at the earliest. | SOD | Marketing | NCR | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150273 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150273 | 2026-08-26 17:00 | 54.0455 | 394 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150273 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017157ACN-2026-08-4000150273 |  | AUD-2026-08-2000017157ACN-2026-08-4000150273 | 21 |  | 27 | 80 | 4 | 4 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150276 | Open |  |  | OISD - The last OISD audit was conducted during Nov'22. All 29 observations complied. T4S - The last T4S audit was conducted during April’26. A total of 33 observations were raised. 07 observations complied. MDSA/Comprehensive Audit - The last Comprehensive audit was conducted during Sep'25. A total of 104 observations were raised, 96 observations complied. SSA - Last SSA was conducted during Sep'25. A total of 52 observations were raised, 48 complied HSLA - Last HSLA conducted during May'26. A total of 04 observations were raised, all complied | 3.18 | OISD/MDSA/SSA/T4S compliance reviewed | 1305 | KANPUR TERMINAL | All Audit observations to be complied within time line. | SOD | Marketing | NCR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-08-2000017157ACN-2026-08-4000150276 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150276 | 2026-08-26 17:00 | 54.0455 | 425 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150276 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150276 |  | AUD-2026-08-2000017157ACN-2026-08-4000150276 | 21 |  | 27 | 80 | 4 | 4 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150277 | Open |  |  | Lights along the boundary wall of Future expansion area was non operational. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1305 | KANPUR TERMINAL | To be made functional and put in to use. | SOD | Marketing | NCR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-08-2000017157ACN-2026-08-4000150277 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150277 | 2026-08-26 17:00 | 54.0455 | 425 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150277 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150277 |  | AUD-2026-08-2000017157ACN-2026-08-4000150277 | 21 |  | 27 | 80 | 4 | 4 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150279 | Open |  |  | Suitable platform/crossover arrangements were not found across the sprinkler lines at Bay Nos. 25 and 47 during random inspection of the tank wagon gantry area. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1305 | KANPUR TERMINAL | Crossovers/platforms to be ensured across all the sprinkler line network to ensure safe and unobstructed movement in Tank wagon gantry area. | SOD | Marketing | NCR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-08-2000017157ACN-2026-08-4000150279 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150279 | 2026-08-26 17:00 | 54.0455 | 425 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150279 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150279 |  | AUD-2026-08-2000017157ACN-2026-08-4000150279 | 21 |  | 27 | 80 | 4 | 4 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150281 | Open |  |  | Various scrap items were observed lying in the Scrap Yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1305 | KANPUR TERMINAL | RFDs to be initiated for the disposal of scrap materials lying in the Scrap Yard and ensure timely disposal. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150281 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150281 | 2026-08-26 17:00 | 54.0455 | 394 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150281 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017157ACN-2026-08-4000150281 |  | AUD-2026-08-2000017157ACN-2026-08-4000150281 | 21 |  | 27 | 80 | 4 | 4 | 57
|  | RANA PULKIT | 2026-08-31 | Faulty lights repaired, lux level maintained as per OISD | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146550 | Completed | RANA PULKIT | 2026-08-31 | Lux Levels checked, found in line with OISD 244 except at Tk-5 Manifold and road in the area between 102A and 102B | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1509 | SHOLAPUR TERMINAL | Faulty lights to be repaired/replaced in observed area and rest all to be ensured Lux levels are as per OISD 244 | SOD | Marketing | WZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146550 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146550 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146550 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146550 |  | AUD-2026-07-2000016455ACN-2026-07-4000146550 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | currently foam quantity is meeting requirement, location will porcure as per demand. | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146551 | Completed | RANA PULKIT | 2026-08-31 | Requirement-18.9 KL(AFFF), 4.45KL(AR-AFFF) Total Qty as on date -19.5KL(AFFF), 4.7 KL(AR-AFFF) | 2.9 | Foam inventory verified | 1509 | SHOLAPUR TERMINAL | Since available Foam qty is just meeting the requirement, advised to keep monitoring stock and maintain as per OISD requirement | SOD | Marketing | WZ | 2026-08-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146551 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146551 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146551 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146551 |  | AUD-2026-07-2000016455ACN-2026-07-4000146551 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | all break glass type ESD has been replaced with Push-pull button type ESD. | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146552 | Completed | RANA PULKIT | 2026-08-31 | Location has 7 HVLR, 10 point type HCD, 7 open path HCD, 18+1 ESDs all are functioning properly | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1509 | SHOLAPUR TERMINAL | As advised by location, breakglass ESD buttons are being replaced to push type, same to be ensured in current quarter | SOD | Marketing | WZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146552 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146552 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146552 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146552 |  | AUD-2026-07-2000016455ACN-2026-07-4000146552 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | Points being complied as per schedule | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146554 | Completed | RANA PULKIT | 2026-08-31 | OISD 2022-23 Total points-21 Complied-21 MDSA 2025-26 Total points-70 Complied-44 SSA 2025-26 Total points-43 Complied-43 | 3.10 | TFMS/SAP reconciliation checked | 1509 | SHOLAPUR TERMINAL | Pending points to be complied as per scheduled timelines and action plan | SOD | Marketing | WZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146554 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146554 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146554 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146554 |  | AUD-2026-07-2000016455ACN-2026-07-4000146554 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | Points being complied as per schedule | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146555 | Completed | RANA PULKIT | 2026-08-31 | OISD 2022-23 Total points-21 Complied-21 MDSA 2025-26 Total points-70 Complied-40 SSA 2025-26 Total points-43 Complied-33 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1509 | SHOLAPUR TERMINAL | Pending points to be complied as per scheduled timelines and action plan | SOD | Marketing | WZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146555 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146555 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146555 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146555 |  | AUD-2026-07-2000016455ACN-2026-07-4000146555 | 21 |  | 27 | 80 | 0 | 0 | 52
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149660 | Open |  |  | 1. Integrity of boundary wall/fencing - Perimeter lighting (no dark zones) 2. Integrity of boundary wall/fencing - Watch towers needs Painting | 1.4 | Earlier action points status checked | 1292 | LUCKNOW DEPOT | All pending observation needs to be closed within time line | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-08-2000017257ACN-2026-08-4000149660 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149660 | 2026-09-03 | 46.7538 | 425 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149660 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149660 |  | AUD-2026-08-2000017257ACN-2026-08-4000149660 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149663 | Open |  |  | A total of 75 CCTVs are integrated with the VA system, out of which 02 CCTVs are currently non-functional. MOC has been raised videMOC no: 3100002112 as verified on 21/05/2026. Nil VA alerts were pending as on date. | 2.7 | VA alerts checked / analysed | 1292 | LUCKNOW DEPOT | Faulty Camera (integrated with VA system) to be rectified. | SOD | Marketing | NCR | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149663 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149663 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149663 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017257ACN-2026-08-4000149663 |  | AUD-2026-08-2000017257ACN-2026-08-4000149663 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149665 | Open |  |  | OISD - The last OISD audit was conducted during Nov'22. All 29 observations complied. T4S - The last T4S audit was conducted during April’26. A total of 32 observations were raised, 16 observations complied. MDSA/Comprehensive Audit - The last Comprehensive audit was conducted during Sep'25. A total of 104 observations were raised, 96 observations complied. SSA - Last SSA was conducted during Sep'25. A total of 52 observations were raised, 48 complied HLSA - Last HLSA was conducted in March'26. A total of observationswere raised 04, 02 complied Sr. Management Audit - 1. Audit Conducted in March'26. A total of 33 observations were raised, 27 complied 2. Last conducted in June'26. A total of 21 observations were raised, 10 complied | 3.18 | OISD/MDSA/SSA/T4S compliance reviewed | 1292 | LUCKNOW DEPOT | All pending audit observations to be complied within time line | SOD | Marketing | NCR | 2026-12-10 |  | 1 |  | S1 | F1 | 2026-12-10 | AUD-2026-08-2000017257ACN-2026-08-4000149665 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149665 | 2026-09-03 | 46.7538 | 465 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149665 | 532 | 8294 | 21 | 8294 | -51 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149665 |  | AUD-2026-08-2000017257ACN-2026-08-4000149665 | 21 |  | 27 | 80 | 0 | 0 | 67
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149666 | Open |  |  | The structure of the Calibration Shed requires painting and necessary upkeep to maintain its condition. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Necessary painting of the Calibration Shed structure to be carried out at the earliest. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149666 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149666 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149666 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149666 |  | AUD-2026-08-2000017257ACN-2026-08-4000149666 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149667 | Open |  |  | The height of the point-type HCD installed near the VRU shed is more and should be reduced to facilitate easy accessibility. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Reduce the installation height of the point-type HCD located near the VRU shed. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149667 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149667 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149667 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149667 |  | AUD-2026-08-2000017257ACN-2026-08-4000149667 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149670 | Open |  |  | Structural painting in the tank farm area is observed to be deteriorated at various locations and should be undertaken to prevent corrosion and maintain asset integrity. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Structural painting in the tank farm area to be carried out on priority to arrest corrosion and to improve asset condition. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149670 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149670 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149670 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149670 |  | AUD-2026-08-2000017257ACN-2026-08-4000149670 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149671 | Open |  |  | The painting of the Railway Siding hydrant line is found to be faded/deteriorated at various places. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Repaint the Railway Siding hydrant line wherever faded. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149671 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149671 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149671 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149671 |  | AUD-2026-08-2000017257ACN-2026-08-4000149671 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149673 | Open |  |  | Various scrap items were observed lying in the Scrap Yard. Necessary RFDs to be initiated and ensure timely disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1292 | LUCKNOW DEPOT | Necessary RFDs to be initiated and ensure timely disposal of scrap materials. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149673 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149673 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149673 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149673 |  | AUD-2026-08-2000017257ACN-2026-08-4000149673 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-08-31 | Both projects closed in SAP | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146557 | Completed | RANA PULKIT | 2026-08-31 | 2 projects are in progress at location. | 4.3 | Project progress reviewed | 1509 | SHOLAPUR TERMINAL | To be completed and capitalized before 30.06.2026 | SOD | Marketing | WZ | 2026-08-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146557 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146557 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146557 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146557 |  | AUD-2026-07-2000016455ACN-2026-07-4000146557 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | PM jobs completed | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146558 | Completed | RANA PULKIT | 2026-08-31 | Following is the PM performance of location for last 3 month Mar 26-100% Apr 26-100% May 26-80% | 4.4 | Quality of PM compliance reviewed | 1509 | SHOLAPUR TERMINAL | PM jobs for May'26 to be completed before 31.05.2026 | SOD | Marketing | WZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146558 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146558 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146558 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146558 |  | AUD-2026-07-2000016455ACN-2026-07-4000146558 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-08-31 | TK-1 JB shifted above dyke height. | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146560 | Completed | RANA PULKIT | 2026-08-31 | TK-1 JB found to be below dyke height, to be shifted outside or above dyke height | 6.1 | Tank Farm | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-08-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146560 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146560 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146560 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146560 |  | AUD-2026-07-2000016455ACN-2026-07-4000146560 | 21 |  | 27 | 80 | 0 | 0 | 52
TAPAS RANJAN PANDA | 2026-08-31 | BHUYAN PRARTHANA | 2026-08-31 | All 47 cameras are now in fully working condition. CCTV is duly monitored at security cabin, control room (by DSO) & LIC aand observations are duly recorded. Point is fully complied. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139169 | Closed | TAPAS RANJAN PANDA | 2026-08-31 | Except one (at DG Room,down from 10/6/26,sent for repairing),All CCTV are in working condition. | 2.6 | CCTV functioning checked | 1677 | GUWAHATI DEPOT | Advised to take up with Vendor for early ratification and put to service immediately.CCTV monitoring at Securty Cabin to be checkedon daily basis with observations to be monitored. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139169 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139169 | 2026-09-01 | 48.7538 | 364 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139169 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139169 | AUD-2026-06-2000013067ACN-2026-06-4000139169 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 52
|  | RANA PULKIT | 2026-08-31 | STP made operational | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146561 | Completed | RANA PULKIT | 2026-08-31 | STP to be made operational | 6.2 | STP | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-08-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146561 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146561 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146561 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146561 |  | AUD-2026-07-2000016455ACN-2026-07-4000146561 | 21 |  | 27 | 80 | 0 | 0 | 52
TAPAS RANJAN PANDA | 2026-08-31 | BHUYAN PRARTHANA | 2026-08-31 | All balance jobs have been completed pertaining to HCD. Location is now having fully compliant 5 no. of open path & 5 no. of point type HCD integrated into TAS. Housekeeping is given due importance in process area. Hence, complied. | SENIOR MANAGEMENT INSPECTION_GUWAHATI_ | 2026-06-18 | AUD-2026-06-2000013067 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000139180 | Closed | TAPAS RANJAN PANDA | 2026-08-31 | Battery room acid resistant paint available.heat detector installation in progress.Control room spare items to be kept properly. | 6.2 | Battery room of control room | 1677 | GUWAHATI DEPOT | Heat detector installation to be completed immediately. Regular housekeeping to be done. | SOD | Marketing | GZR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013067ACN-2026-06-4000139180 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013067ACN-2026-06-4000139180 | 2026-09-01 | 48.7538 | 364 | >20 | AUD-2026-06-2000013067 - ACN-2026-06-4000139180 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013067ACN-2026-06-4000139180 | AUD-2026-06-2000013067ACN-2026-06-4000139180 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Training have been to security guards on Safety briefing, Frisking and CCTV monitoring. HSE officer is reviewing the CCTV monitoring register daily and also taking actions on CCTV findings and reviewing the unsafe acts, unsafe conditions and near misses. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-08-4000146717 | Closed | JHA RAJAN KUMAR | 2026-08-31 | 1. No safety briefing provided by Security 2. Frisking is not done properly. Metal detector did not detect wrist watch. 3. Gate registers are being regularly reviewed 4. Security is carrying out monitoring of CCTV camera and recording their observation, which is being checked periodically by location officers also. However, action not being taken on observations. Observation of vegetation on concertina coil,in May 26, July 26 still not complied, in addition to other cases of reporting of vegetation on boundary wall, blocking view of cameras, etc 5. Improper review of CCTV register. 6. Contract workman in/out regioster found OK | 6.1 | Quarterly Inspection | 1723 | PATNA DEPOT | 1. Security to be trained for providing safety briefing 2. Security to be trained for carrying out frisking properly 3. No actionneeded 4. Actions to be taken on findings of CCTV camera monitoring. Clearing the view of CCTV blocking view of Gantry Bay 3&4 5.Safety Officer to review CCTV register properly for timely and corrective action. 6. To be maintained. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146717 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146717 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146717 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146717 | AUD-2026-08-2000016222ACN-2026-08-4000146717 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Updated in the admin building and Security cabin. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-08-4000146718 | Closed | JHA RAJAN KUMAR | 2026-08-31 | Contact details not updated | 6.2 | Quarterly Inspection | 1723 | PATNA DEPOT | Conatct details to be updated for LIC, M&I, Region Head. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146718 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146718 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146718 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146718 | AUD-2026-08-2000016222ACN-2026-08-4000146718 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Permits updated and actions being taken on CCTV monitoring observations. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-08-4000146728 | Closed | JHA RAJAN KUMAR | 2026-08-31 | 1. No action is being taken on CCTV monitoring observation 2. Nos of Work permits are either not closed, or not updated during period of vailidity of the permits. Even JSAs and Tool box safety talk records are blank for many permits. Extent of noncompliance to work permit requirement found to be receiver specific, implying lack of awareness of receiving officer and no monitorng of permits | 6.12 | Quarterly Inspection | 1723 | PATNA DEPOT | 1. HSE officer to get involved and LIC also to monitor. 2. HSE officer and LIC to check permits and associated documents, before issuance and during and after workexecution | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146728 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146728 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146728 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146728 | AUD-2026-08-2000016222ACN-2026-08-4000146728 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Noted for action. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-08-4000146737 | Closed | JHA RAJAN KUMAR | 2026-08-31 | Found ok. officer is present during caliberation of TT | 6.21 | Quarterly Inspection | 1723 | PATNA DEPOT | To be maintained. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146737 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146737 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146737 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146737 | AUD-2026-08-2000016222ACN-2026-08-4000146737 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Noted for action. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-08-4000146739 | Closed | JHA RAJAN KUMAR | 2026-08-31 | Random CCTV footage for 22/6/25 and 9/6/26 was viewed and found ok | 6.23 | Quarterly Inspection | 1723 | PATNA DEPOT | To be maintained. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146739 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146739 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146739 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146739 | AUD-2026-08-2000016222ACN-2026-08-4000146739 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MONISH KUMAR | 2026-08-31 | JHA RAJAN KUMAR | 2026-08-31 | Noted for action. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | ZONAL AUDIT | ACN-2026-08-4000146740 | Closed | JHA RAJAN KUMAR | 2026-08-31 | Order No. 130000623078 and 130000622470 was reviewed | 6.24 | Quarterly Inspection | 1723 | PATNA DEPOT | Found OK | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146740 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146740 | 2026-08-03 | 77.7538 | 364 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146740 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146740 | AUD-2026-08-2000016222ACN-2026-08-4000146740 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 52
MAZUMDER SAUVIK | 2026-08-31 | MD KASHIF | 2026-08-10 | Found meeting the requirements.No action required. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125702 | Closed | MD KASHIF | 2026-08-10 | Yes all major KPIs reviewed | 1.2 | Performance review conducted | 1742 | BOKARO DEPOT | Ethanol tank & MFM project , stock loss & MDSA points compliances to be given focus | SOD | Marketing | PZR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125702 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125702 | 2026-09-19 10:00 | 30.3372 | 364 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125702 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125702 | AUD-2026-03-2000010870ACN-2026-03-4000125702 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 52
MAZUMDER SAUVIK | 2026-08-31 | MD KASHIF | 2026-08-10 | Found meeting the requirements.No action required. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125705 | Closed | MD KASHIF | 2026-08-10 | Fire drill records reviewed for drill conducted in last 6 months | 2.1 | Fire drill conducted in last 6 months (surprise) | 1742 | BOKARO DEPOT | Improvement in mock drill discussed | SOD | Marketing | PZR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125705 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125705 | 2026-09-19 10:00 | 30.3372 | 364 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125705 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010870ACN-2026-03-4000125705 | AUD-2026-03-2000010870ACN-2026-03-4000125705 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 52
MAZUMDER SAUVIK | 2026-08-31 | MD KASHIF | 2026-08-10 | Found meeting the requirements.No action required. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125708 | Closed | MD KASHIF | 2026-08-10 | The same was checked during sudden mock drill announced on 29.1.26 | 2.5 | Emergency response preparedness reviewed | 1742 | BOKARO DEPOT | Response was good from all teams , only some coordination issue and usage of PA system was witnessed | SOD | Marketing | PZR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125708 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125708 | 2026-09-19 10:00 | 30.3372 | 364 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125708 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125708 | AUD-2026-03-2000010870ACN-2026-03-4000125708 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 52
MAZUMDER SAUVIK | 2026-08-31 | MD KASHIF | 2026-08-10 | Foam received and meets the min. foam requirements | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-03-4000125711 | Closed | MD KASHIF | 2026-08-10 | Foam Inventory is just meeting the OISD -117 requirement. Additional foams to be purchased from centralized PO | 2.9 | Foam inventory verified | 1742 | BOKARO DEPOT | Location confirm that additional foam order placed on vendor and expected to arrive in March | SOD | Marketing | PZR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010870ACN-2026-03-4000125711 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125711 | 2026-09-19 10:00 | 30.3372 | 364 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125711 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125711 | AUD-2026-03-2000010870ACN-2026-03-4000125711 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 52
MAZUMDER SAUVIK | 2026-08-31 | MD KASHIF | 2026-08-10 | Scrap disposal of 225 KL tank completed | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125722 | Closed | MD KASHIF | 2026-08-10 | 1 no. 225 KL double wall MS horz. Tank which is shifted from other locations and some other misc. scrap required disposal | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1742 | BOKARO DEPOT | Location advised to expdite disposal | SOD | Marketing | PZR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125722 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125722 | 2026-09-19 10:00 | 30.3372 | 364 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125722 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125722 | AUD-2026-03-2000010870ACN-2026-03-4000125722 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 52
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150403 | Open |  |  | 6 pending point of total 19 points of inspection in | 1.4 | Earlier action points status checked | 1797 | GULBARGA NEW IRD | Pending observations to be complied at the earliest | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150403 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150403 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150403 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150403 |  | AUD-2026-08-2000016952ACN-2026-08-4000150403 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150406 | Open |  |  | Lux level to be improved at Tank Farm Area | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1797 | GULBARGA NEW IRD | Lux level to be improved at Tank Farm Area | SOD | Marketing | SWZ | 2026-09-30 |  | 8 |  | S4 | F2 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150406 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150406 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150406 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016952ACN-2026-08-4000150406 |  | AUD-2026-08-2000016952ACN-2026-08-4000150406 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150409 | Open |  |  | 3 High Volume Long Range (HVLR) monitors are working . Emergency Shutdown (ESD) buttons were found 100% functional. HCD of TW pump house was not working | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1797 | GULBARGA NEW IRD | The non-working HCD in TW pump house is to be corrected at earliest. Audio visual alram to be checked | SOD | Marketing | SWZ | 2026-09-30 |  | 8 |  | S4 | F2 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150409 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150409 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150409 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016952ACN-2026-08-4000150409 |  | AUD-2026-08-2000016952ACN-2026-08-4000150409 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150412 | Open |  |  | Following TTS were checked with intelligent key TT no: KA39A3862,KA46A0846,KA32D7101 and found ok | 3.5 | EM Lock SOP compliance verified | 1797 | GULBARGA NEW IRD | LIC to check more TTs using intelligent key and records to be maintained | SOD | Marketing | SWZ | 2026-09-01 |  | 4 |  | S2 | F2 | 2026-09-01 | AUD-2026-08-2000016952ACN-2026-08-4000150412 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150412 | 2026-08-19 18:00 | 61.0038 | 365 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150412 | 532 | 8294 | 21 | 8294 | 48 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150412 |  | AUD-2026-08-2000016952ACN-2026-08-4000150412 | 21 |  | 27 | 80 | 5 | 5 | 53
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150415 | Open |  |  | All OISD points are complied. Pending MDSA/SSA points to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1797 | GULBARGA NEW IRD | Location to expediate the closure of Pending MDSA/SSA points.MDSA pending observations: 7 and SSA pending points: 5 | SOD | Marketing | SWZ | 2026-09-30 |  | 8 |  | S4 | F2 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150415 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150415 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150415 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016952ACN-2026-08-4000150415 |  | AUD-2026-08-2000016952ACN-2026-08-4000150415 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150416 | Open |  |  | All operational areas were inspected and observed to be satisfactory 1. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1797 | GULBARGA NEW IRD | Platform Infront of unloading bay to be demolished and made level with surrounding area. (Old mother foam tank area) | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150416 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150416 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150416 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150416 |  | AUD-2026-08-2000016952ACN-2026-08-4000150416 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150417 | Open |  |  | 4 TAS related projects to be completed as per timelines | 4.3 | Project progress reviewed | 1797 | GULBARGA NEW IRD | 1. TAS novex integration 2. UG Tanks overfill protection 3.Replacement of secondary radar of AG tanks 4.UG tanks TFMS equipment replacement | SOD | Marketing | SWZ | 2027-03-31 |  | 6 |  | S3 | F2 | 2027-03-31 | AUD-2026-08-2000016952ACN-2026-08-4000150417 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150417 | 2026-08-19 18:00 | 61.0038 | 576 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150417 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016952ACN-2026-08-4000150417 |  | AUD-2026-08-2000016952ACN-2026-08-4000150417 | 21 |  | 27 | 80 | 5 | 5 | 83
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150418 | Open |  |  | Auctioning by MSTC of Scrap Lots in progress | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1797 | GULBARGA NEW IRD | Location to be ready for physical disposal once Disposal Order released by MSTC | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-08-2000016952ACN-2026-08-4000150418 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150418 | 2026-08-19 18:00 | 61.0038 | 425 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150418 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150418 |  | AUD-2026-08-2000016952ACN-2026-08-4000150418 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000150419 | Open |  |  | Some TTS were found without branding TT no:KA32AA6239,KA22AA7883. | 6.1 | TT Branding | 1797 | GULBARGA NEW IRD | Branding of 100% TTs to be ensured | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150419 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150419 | 2026-08-19 18:00 | 61.0038 | 394 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150419 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150419 |  | AUD-2026-08-2000016952ACN-2026-08-4000150419 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000150420 | Open |  |  | Fire proximity suit and SCABA were kept in Cupboard in employee rest room | 6.1 | PPE | 1797 | GULBARGA NEW IRD | Fire proximity suit and SCABA any other safety equipment to be kept outside in easily accessible location | SOD | Marketing | SWZ | 2026-09-15 |  | 1 |  | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016952ACN-2026-08-4000150420 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150420 | 2026-08-19 18:00 | 61.0038 | 379 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150420 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150420 |  | AUD-2026-08-2000016952ACN-2026-08-4000150420 | 21 |  | 27 | 80 | 5 | 5 | 55
[5 empty] | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000150421 | Open |  |  | Fire Emergency Trolley was having one SCABA . 2 SCABA sets to be provided , 1 water gel blanket requires replacement same to be replaced | 6.1 | Safety | 1797 | GULBARGA NEW IRD | All Safety Equipments in Trolley including medicine to be provided as per OISD requirement and to be verified on monthly basis | SOD | Marketing | SWZ | 2026-09-15 |  | 2 |  | S2 | F1 | 2026-09-15 | AUD-2026-08-2000016952ACN-2026-08-4000150421 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150421 | 2026-08-19 18:00 | 61.0038 | 379 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150421 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016952ACN-2026-08-4000150421 |  | AUD-2026-08-2000016952ACN-2026-08-4000150421 | 21 |  | 27 | 80 | 5 | 5 | 55
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | Details shared with Zone regarding training of Officers. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147905 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | Yes, Done | 1.1 | Interaction with all officers (1–1.5 hrs) | 1436 | SAGAR DEPOT | Officer requested for SAP training. Taken up with HQO for arranging training to Officers. | SOD | Marketing | CEN | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-08-30 | AUD-2026-08-2000016370ACN-2026-08-4000147905 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147905 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147905 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147905 | AUD-2026-08-2000016370ACN-2026-08-4000147905 | 21 | 21 | 27 | 80 | 4 | 2 | 52 | 52
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | Budget request sent to HQO for 29.5 lacs budget , same approved and budget appropriated in sap after budget allotment. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147907 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | Yes, Points identified and attended immediately. | 1.5 | HQO / Zonal support required identified | 1436 | SAGAR DEPOT | Location requested budget for closed loop system was facilitated and given to them. | SOD | Marketing | CEN | 2026-08-20 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-20 | AUD-2026-08-2000016370ACN-2026-08-4000147907 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147907 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147907 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147907 | AUD-2026-08-2000016370ACN-2026-08-4000147907 | 21 | 21 | 27 | 80 | 4 | 2 | 51 | 52
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | "OEM visit scheduled on 14.08.26, MOV valve replaced and level switch resetting done by OEM Engineer ( M/S Idex ). Testing done after valve repalcement , now HVLR functioning properly ( valve Open/ Close operating remotely from panel ). HVLR training also provided to all CW and Security Staff for handling emergency. Hence point complied. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147910 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | HVLR No. 4 checked for TK-17, wherein problem of MOV is encountered. To be attended on priority. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1436 | SAGAR DEPOT | To coordinate with OEM for rectification of MOV for smooth operation of HVLR. | SOD | Marketing | CEN | 2026-08-17 | POOR EQUIPMENT MAINTENANCE | 10 | PROCESS SAFETY | S2 | F5 | 2026-08-17 | AUD-2026-08-2000016370ACN-2026-08-4000147910 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147910 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147910 | 532 | 8294 | 21 | 8294 | 63 | 70 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016370ACN-2026-08-4000147910 | AUD-2026-08-2000016370ACN-2026-08-4000147910 | 21 | 21 | 27 | 80 | 4 | 2 | 50 | 52
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | "DCP powder replaced for all DCP of TLF Gantry and Tank farm area. ( Monoammonium Phosphate repalced with Sodium bi carbonate powder due to high chances of cake formation of mono ammonium phosphate with reaction with moisture / atm O2 ). DCP also tested for performance. Hence complied. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147911 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | Yes, Problem encountered in DCP Powder, that needs to be replaced | 2.14 | TT crew fire extinguisher usage checked | 1436 | SAGAR DEPOT | To get the DCP Powder checked in all Fire Extinguishers to avoid such issues. | SOD | Marketing | CEN | 2026-08-20 | POOR EQUIPMENT MAINTENANCE | 10 | PROCESS SAFETY | S2 | F5 | 2026-08-20 | AUD-2026-08-2000016370ACN-2026-08-4000147911 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147911 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147911 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016370ACN-2026-08-4000147911 | AUD-2026-08-2000016370ACN-2026-08-4000147911 | 21 | 21 | 27 | 80 | 4 | 2 | 51 | 52
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | Locks replaced and defective lock sent to Sterna lab. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147913 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | EM locking system checked for TT Nos. MP40 ZE 8955, MP13 H 2139 and MP33 H 2413. Issue encountered with Top lock of TT No. MP33 H 2413. | 3.5 | EM Lock SOP compliance verified | 1436 | SAGAR DEPOT | Lock to be replaced with new one and defective lock to be sent to Sterna for further investigation. | SOD | Marketing | CEN | 2026-08-20 | THIRD PARTY ERRORS | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-20 | AUD-2026-08-2000016370ACN-2026-08-4000147913 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147913 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147913 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016370ACN-2026-08-4000147913 | AUD-2026-08-2000016370ACN-2026-08-4000147913 | 21 | 21 | 27 | 80 | 4 | 2 | 51 | 52
BANTHIYA RITESH DEELIP | 2026-08-31 | PANWAR VIPIN SINGH | 2026-08-29 | Bottom loading spare received at location from OEM. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147917 | Closed | PANWAR VIPIN SINGH | 2026-08-29 | Nil. Bottom loading arms spares awaited. Location to follow up and get the spares on priority | 4.2 | Maintenance activities reviewed | 1436 | SAGAR DEPOT | Location to provide timeline for getting Bottom loading arms spares | SOD | Marketing | CEN | 2026-08-30 | POOR EQUIPMENT MAINTENANCE | 6 | PROCESS SAFETY | S2 | F3 | 2026-08-30 | AUD-2026-08-2000016370ACN-2026-08-4000147917 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147917 | 2026-08-07 19:00 | 72.9622 | 364 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147917 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016370ACN-2026-08-4000147917 | AUD-2026-08-2000016370ACN-2026-08-4000147917 | 21 | 21 | 27 | 80 | 4 | 2 | 52 | 52
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149295 | Open |  |  | Location is a single-contingency location. A mock drill was conducted on 24/06/2026 in the presence of the Zonal Team with scenerioof leakage from TSV installed at HSD tank Tk-02. The overall response time was found to be satisfactory; however, the following shortcomings were observed during the drill: 1. ESD to be operated from the nearast point during emergency 2. C/W was not acquented with the operation of portable MEFG | 2.2 | Double contingency scenario simulated; observations recorded | 1319 | MUGHALSARAI DEPOT | 1. Location to prepare Standee for team identification 2. Continuous training to be provided to workmen w.r.t. usage of safety equipmemt | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000149295 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000149295 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000149295 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000149295 |  | AUD-2026-07-2000015715ACN-2026-08-4000149295 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149297 | Open |  |  | Tot. 60 no of CCTV's are available at the location out of which only 58 CCTV's are working. For Remaining 2 no of CCTV sent to the AMC vendor for repair vide Gate Pass Nos. 11319-R-017143 and 11319-R-017898 dated 12.06.2026. 92 days CCTV recording was available &regular basis reviews were made and records maintained. | 2.6 | CCTV functioning checked | 1319 | MUGHALSARAI DEPOT | Location to expedite the 100% CCTV surveillance at the premises | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000149297 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000149297 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000149297 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000149297 |  | AUD-2026-07-2000015715ACN-2026-08-4000149297 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149298 | Open |  |  | A total of 47 CCTVs are integrated with the VA system, out of which 01 CCTVs are currently non-functional was sent to AMC vendor for repair vide gate Pass No: 11319-R-017898 dt 12.06.2026. | 2.7 | VA alerts checked / analysed | 1319 | MUGHALSARAI DEPOT | Location to expedite the 100% VA surveillance at the premises through CCTV | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000149298 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000149298 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000149298 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000149298 |  | AUD-2026-07-2000015715ACN-2026-08-4000149298 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149299 | Open |  |  | Total 21 nos of MOC initiated and 16 are pproved and closed. However 5 no of MOC is approved but not closed due to on going projectwork. | 3.17 | MOC status reviewed | 1319 | MUGHALSARAI DEPOT | Location is advised to closed remaining 5 MOCs post completion of Job | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000149299 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000149299 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000149299 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000149299 |  | AUD-2026-07-2000015715ACN-2026-08-4000149299 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150500 | Open |  |  | OISD - The last OISD audit was conducted during July'25. A total of 26 observations were raised, 25 are complied. T4S - The last T4S audit was conducted during May'26. A total of 20 observations were raised, 5 observations complied. MDSA/Comprehensive Audit - The last Comprehensive audit was conducted during March'26. A total of 58 observations were raised, 22 observations complied. SSA - Last SSA was conducted during Sep'25. A total of 35 observations were raised, 33 complied | 3.18 | OISD/MDSA/SSA/T4S compliance reviewed | 1319 | MUGHALSARAI DEPOT | Location is advsied to Comply with the audit observation in time bound manner and update compliance status in SAP | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150500 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150500 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150500 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000150500 |  | AUD-2026-07-2000015715ACN-2026-08-4000150500 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150501 | Open |  |  | Air Conditioner of Control room is not affective. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Periodic maintenance and repair of Air conditioning system is to be ensured by the location | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150501 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150501 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150501 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000150501 |  | AUD-2026-07-2000015715ACN-2026-08-4000150501 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150506 | Open |  |  | Tell Tale clock not operational since 2019. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | The Tell-Tale Clock to be made operational on priority to ensure continuous monitoring and recording of security patrols. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150506 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150506 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150506 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015715ACN-2026-08-4000150506 |  | AUD-2026-07-2000015715ACN-2026-08-4000150506 | 21 |  | 27 | 80 | 1 | 2 | 57
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-08-22 | Closed, Duplicate recommendation, same is mentioned in part code 3.18 | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141719 | Closed | GEETE DEVASHISH | 2026-08-22 | Yes, Location is advised to expedite closure of all 19 open MDSA Audit observation points in a time bound manner. | 1.6 | Expectations clearly communicated to officers | 1435 | GWALIOR DEPOT | Location to expedite closure of all 19 open MDSA Audit observation points in a time bound manner. | SOD | Marketing | CEN | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-06-2000015012ACN-2026-06-4000141719 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141719 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141719 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141719 | AUD-2026-06-2000015012ACN-2026-06-4000141719 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 53
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-08-22 | Closed, Refresher training given to TT Crew on 08/08/2026 & 14/08/2026, pre and post evaluation done and training observed satisfactory | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141722 | Closed | GEETE DEVASHISH | 2026-08-22 | Yes, operated thru one cleaner of TT No: MP33 H1905 | 2.14 | TT crew fire extinguisher usage checked | 1435 | GWALIOR DEPOT | TT crew needs referesher training | SOD | Marketing | CEN | 2026-07-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-07-30 | AUD-2026-06-2000015012ACN-2026-06-4000141722 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141722 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141722 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000015012ACN-2026-06-4000141722 | AUD-2026-06-2000015012ACN-2026-06-4000141722 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 53
PURANAM PRAKASH | 2026-09-01 |  |  | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143123 | Closed | G SADASIVAN | 2026-07-06 | Few TTs checked for post fill Dips. In KA46A0832/Puradamma Tpt- Comp2-10L, Comp3-20L excess observed. Removed the excess. | 3.2 | Post-loading dip checks verified | 1777 | Hassan Terminal | Asked LIC & TAS officer to get the bay thoroughly checked for MFM accuracy and get it recalibrated if required. If TT is faulty, get the TT recalibrated | SOD | Marketing | SWZ | 2026-07-15 | INADEQUATE SAFETY CULTURE | 9 | CONTRACTOR SAFETY | S3 | F3 | 2026-07-15 | AUD-2026-07-2000014942ACN-2026-07-4000143123 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143123 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143123 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143123 | AUD-2026-07-2000014942ACN-2026-07-4000143123 | 21 | 21 | 27 | 80 | 1 | 2 | 46 | 53
PURANAM PRAKASH | 2026-09-01 |  |  | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143127 | Closed | PURANAM PRAKASH | 2026-09-01 | Water level variation is observed which needs to be rectified | 3.7 | Inventory physical dip of minimum two tanks taken | 1777 | Hassan Terminal | To be rectified | SOD | Marketing | SWZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 8 | ASSET INTEGRITY | S4 | F2 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143127 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143127 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143127 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143127 | AUD-2026-07-2000014942ACN-2026-07-4000143127 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 53
PURANAM PRAKASH | 2026-09-01 |  |  | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143130 | Closed | G SADASIVAN | 2026-07-06 | Local loading observed for the quarterly prover verification . Records are being maintained | 3.14 | Local loading checks (if applicable) | 1777 | Hassan Terminal | Batch control Log Book: Missing MRPL Batch No/Test Report No/Date & Sign. Record to be complete in all aspects. | SOD | Marketing | SWZ | 2026-07-15 | INSUFFICIENT SUPERVISION | 9 | ASSET INTEGRITY | S3 | F3 | 2026-07-15 | AUD-2026-07-2000014942ACN-2026-07-4000143130 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143130 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143130 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143130 | AUD-2026-07-2000014942ACN-2026-07-4000143130 | 21 | 21 | 27 | 80 | 1 | 2 | 46 | 53
PURANAM PRAKASH | 2026-09-01 |  |  | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143134 | Closed | G SADASIVAN | 2026-07-06 | Reviewed progress of 2 current projects related to Bottom Loading and VHF sets procurement | 4.3 | Project progress reviewed | 1777 | Hassan Terminal | To complete the ongoing projects within the agreed timelines | SOD | Marketing | SWZ | 2026-07-31 | INADEQUATE SAFETY CULTURE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-31 | AUD-2026-07-2000014942ACN-2026-07-4000143134 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143134 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143134 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000014942ACN-2026-07-4000143134 | AUD-2026-07-2000014942ACN-2026-07-4000143134 | 21 | 21 | 27 | 80 | 1 | 2 | 48 | 53
PURANAM PRAKASH | 2026-09-01 |  |  | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 5.3 POST-VISIT-REPORTING | ACN-2026-07-4000143138 | Closed | G SADASIVAN | 2026-07-06 | Sno Electrician's Validity expired on 31.03.2026 | 5.5 | Electrician License Validity | 1777 | Hassan Terminal | Validity of Licenses to be checked, updated and to be ensured | SOD | Marketing | SWZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 9 | ASSET INTEGRITY | S3 | F3 | 2026-08-31 | AUD-2026-07-2000014942ACN-2026-07-4000143138 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143138 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143138 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143138 | AUD-2026-07-2000014942ACN-2026-07-4000143138 | 21 | 21 | 27 | 80 | 1 | 2 | 52 | 53
|  | G SADASIVAN | 2026-09-01 | MFM Calibration completed | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 5.3 POST-VISIT-REPORTING | ACN-2026-07-4000143137 | Completed | G SADASIVAN | 2026-09-01 | Check MFM calibration is overdue | 5.4 | PLT Receipt Check MFM Calibration | 1777 | Hassan Terminal | To be done immediately | SOD | Marketing | SWZ | 2026-08-15 |  | 16 |  | S4 | F4 | 2026-08-15 | AUD-2026-07-2000014942ACN-2026-07-4000143137 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143137 | 2026-09-22 17:00 | 27.0455 | 348 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143137 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | HIGH | AUD-2026-07-2000014942ACN-2026-07-4000143137 |  | AUD-2026-07-2000014942ACN-2026-07-4000143137 | 21 |  | 27 | 80 | 1 | 2 | 50
|  | SELVAN J | 2026-09-01 | The culverts are mentioned in the surplus/Idle assest Portal 5nos to use other locations. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144104 | Completed | SELVAN J | 2026-09-01 | New RCC culverts were fabricated as protection for TNEB cables at the OUT gate. The same are lying idle since TNEB is not giving permission to lay culverts. | 6.3 | RCC Culverts | 1973 | CASSIMODE BLACK OIL TERMINAL | it is recommended to put these culverts on Surplus/Idle asset portal and shift to location where required. | SOD | Marketing | SZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015706ACN-2026-07-4000144104 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000144104 | 2026-09-22 17:00 | 27.0455 | 333 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000144104 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015706ACN-2026-07-4000144104 |  | AUD-2026-07-2000015706ACN-2026-07-4000144104 | 21 |  | 27 | 80 | 0 | 0 | 48
|  | SELVAN J | 2026-09-01 | OWS pit maintained clean. Cleaned date, Due date sticker was pasted to maintained on a frequent basis. | CASSIMODE_Q1_FY26_SR.MGMT INSPECTION | 2026-06-24 18:00 | AUD-2026-07-2000015706 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144103 | Completed | SELVAN J | 2026-09-01 | OWS pit was not clean. Gratings on the OWS to be changed. MS Frame has loosened. | 6.2 | Repairs to OWS | 1973 | CASSIMODE BLACK OIL TERMINAL | OWS Pit should be maintained clean. MS grating and frame to be repaired. | SOD | Marketing | SZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015706ACN-2026-07-4000144103 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015706ACN-2026-07-4000144103 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-07-2000015706 - ACN-2026-07-4000144103 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015706ACN-2026-07-4000144103 |  | AUD-2026-07-2000015706ACN-2026-07-4000144103 | 21 |  | 27 | 80 | 0 | 0 | 57
PURANAM PRAKASH | 2026-09-01 | G SADASIVAN | 2026-07-09 | Complied | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143119 | Closed | G SADASIVAN | 2026-07-06 | Checked open patch HCD of TK-102 alarm triggered in Control room, main gate and local hooter also activated, Storm water dyke valveopened for TK-102 local hooter activated, alarm trigerred in control room and main gate | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1777 | Hassan Terminal | HCD integration of TK-302 to be completed | SOD | Marketing | SWZ | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S4 | F2 | 2026-07-15 | AUD-2026-07-2000014942ACN-2026-07-4000143119 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143119 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143119 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143119 | AUD-2026-07-2000014942ACN-2026-07-4000143119 | 21 | 21 | 27 | 80 | 1 | 2 | 46 | 53
PURANAM PRAKASH | 2026-09-01 | G SADASIVAN | 2026-07-09 | Officers operated MEFG, Monitor near TK-102 and MEFG near OWS. Naveen operated Tk101 Sprinkler, Aham operated Tk202 HVLR, Gopichandoperated Tk201 MEFG. Officers were able to operate. | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143120 | Closed | G SADASIVAN | 2026-07-09 | Officers operated MEFG, Monitor near TK-102 and MEFG near OWS. Naveen operated Tk101 Sprinkler, Aham operated Tk202 HVLR, Gopichandoperated Tk201 MEFG. Officers were able to operate. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1777 | Hassan Terminal | Officers able to operate, Foam generation of MEFG of TK-102 & monitor-15 to be checked, | SOD | Marketing | SWZ | 2026-06-30 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S4 | F2 | 2026-06-30 | AUD-2026-07-2000014942ACN-2026-07-4000143120 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143120 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143120 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143120 | AUD-2026-07-2000014942ACN-2026-07-4000143120 | 21 | 21 | 27 | 80 | 1 | 2 | 44 | 53
PURANAM PRAKASH | 2026-09-01 | G SADASIVAN | 2026-07-09 | 1) Gantry cleanliness done 2) MFM area tree branches trimmed 3) Scrap yard cleaned and disposed off 4) Cable drums kept in open atmosphere, shifted inside warehouse and arranged | GM GR AUDIT | 2026-06-04 | AUD-2026-07-2000014942 | 2026-06-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143131 | Closed | G SADASIVAN | 2026-07-09 | All employees and CWM were found with Coverall. Overall Housekeeping to be improved | 3.15 | Housekeeping & PPE usage checked | 1777 | Hassan Terminal | 1) Gantry cleanliness to be done 2) MFM area tree branches to be trimmed 3) Scrap yard to be cleaned and disposed off 4) Cable drums kept in open atmosphere, to be shifted inside warehouse and to be arranged. | SOD | Marketing | SWZ | 2026-07-15 | INSUFFICIENT SUPERVISION | 9 | CONTRACTOR SAFETY | S3 | F3 | 2026-07-15 | AUD-2026-07-2000014942ACN-2026-07-4000143131 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000014942ACN-2026-07-4000143131 | 2026-09-22 17:00 | 27.0455 | 365 | >20 | AUD-2026-07-2000014942 - ACN-2026-07-4000143131 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000014942ACN-2026-07-4000143131 | AUD-2026-07-2000014942ACN-2026-07-4000143131 | 21 | 21 | 27 | 80 | 1 | 2 | 46 | 53
[5 empty] | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150039 | Open |  |  | EM lock 5% check to be done on daily basis and records to be maintained | 3.5 | EM Lock SOP compliance verified | 1221 | DELHI TERMINAL | EM lock 5% check to be done on daily basis and records to be maintained | SOD | Marketing | NZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150039 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150039 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150039 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150039 |  | AUD-2026-09-2000017114ACN-2026-09-4000150039 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150041 | Open |  |  | During the period 25th May'26 to 29th Jul'26, 5 MOCs are reflecting in the system with 2 approved and 3 in submitted status. | 3.17 | MOC status reviewed | 1221 | DELHI TERMINAL | For 2026-27 MOCs, approval for submitted MOCs to be obtained and closure to be ascertained in time bound manner. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150041 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150041 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150041 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150041 |  | AUD-2026-09-2000017114ACN-2026-09-4000150041 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150042 | Open |  |  | 1. OISD Status - All Observations complied and Nil pending. 2. Comprehensive/MDSA status - Total 115 Observations were there and113 closed. Pending observations are as below 1. Pipeline sun set approval 2. Tank Emergency drain Blind (OISD Guideline) 3. Self Safety Audit Status - Total 43 Observations were there and 42 observations were closed. Pending points are as below 1. TankEmergency drain Blind (OISD Guideline) 4. T4S Audit Status - Pending. Was scheduled in June'26- still pending. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1221 | DELHI TERMINAL | 2. Comprehensive/MDSA pending points to be complied in a time bound manner. 3. Self Safety Audit pending Point to be complied ina time bound manner. 4. T4S Audit to be ensured during Q2: 2026-27. | SOD | Marketing | NZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017114ACN-2026-09-4000150042 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150042 | 2026-08-27 | 53.7538 | 486 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150042 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150042 |  | AUD-2026-09-2000017114ACN-2026-09-4000150042 | 21 |  | 27 | 80 | 3 | 3 | 70
|  |  |  | work in progress , 2 No. Inverters repaired awaiting installation | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150045 | Open | GARG PANKAJ | 2026-10-05 | Four invertors out of 11 invertors are down since last two months . Location to expedite rectification and confirm Grass Cutting required in Solar Plant Area . | 6.1 |  | 1221 | DELHI TERMINAL | Solar invertor to be rectified. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150045 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150045 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150045 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150045 |  | AUD-2026-09-2000017114ACN-2026-09-4000150045 | 21 |  | 27 | 80 | 3 | 3 | 57
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-09-01 | access control system at Gwalior IRD 1) License area access control system is fully functional for both Entry and Exit control after replacement of faulty reader units. 2) There are two access turnstiles after security at Main gate entry. 01 turnstile is fully functional for both entry and exit control. However, exit reader of 2nd turnstile is taken by vendor for repairing while Entry control is functional. Since, at main gate both Entry and Exit is controlled through functional access control system, the faulty reader is not creating any bypass/violation and we are following up with the vendor for earliest repairing of faulty reader. Hence the observation of making the access control system functional at Gwalior IRD can be closed. | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141720 | Closed | SINGWAL DEEPAK | 2026-09-01 | Access control system is functional at only one place, i.e. at Main Security Cabin. The 2nd CBAC is down at Main Security Cabin dueto card reader issue and 3rd CBAC is also down meant for licensed area access due to malfunctioning of face and finger print sensor. | 2.8 | Access control systems checked | 1435 | GWALIOR DEPOT | Location to get repaired both these non-functional CBAC system and bring it into working condition on priority. | SOD | Marketing | CEN | 2026-09-30 | THIRD PARTY ERRORS | 15 | PROCESS SAFETY | S3 | F5 | 2026-09-30 | AUD-2026-06-2000015012ACN-2026-06-4000141720 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141720 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141720 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141720 | AUD-2026-06-2000015012ACN-2026-06-4000141720 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 53
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-09-01 | All these open observations of ESA,OISD,SSA & MDSA are related to ongoing railway siding sprinklar project and are common in nature. Hence, their closure is dependent on the completion of project which is expected to be completed by 30.09.2026. Since same observation was also made during previous location visit. Therefore, the compliance of this observation is to be referred from particular no. 1.4 of this audit sheet. | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141725 | Closed | SINGWAL DEEPAK | 2026-09-01 | OISD - 02, SSA - 02 and MDSA - 19 pending against total observation point of 108. Targeted to complete it by Sept' 2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1435 | GWALIOR DEPOT | Open MDSA, SSA and ESA points to be closed by Sept' 2026. | SOD | Marketing | CEN | 2026-09-30 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-06-2000015012ACN-2026-06-4000141725 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141725 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141725 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141725 | AUD-2026-06-2000015012ACN-2026-06-4000141725 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 53
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-09-01 | The pump of TK24 is already sent to vendor and is under repairing. The CBAC system is made functional, the faulty unit is already sent for repairing. Since, at main gate both Entry and Exit is controlled through functional access control system, the faulty reader is not creating any bypass/violation and we are following up with the vendor for earliest repairing of faulty reader. Hence the observation of making the access control system functional at Gwalior IRD can be closed. Closed, Duplicate recommendation, same is mentioned in part code 2.8 | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141726 | Closed | GEETE DEVASHISH | 2026-09-01 | Reviewed. Two are pending. One is pertaining to Ethanol Pump of TK-24 and the other one is related to CBAC System | 4.2 | Maintenance activities reviewed | 1435 | GWALIOR DEPOT | Location to close both these open activities on war footing basis. | SOD | Marketing | CEN | 2026-07-30 | THIRD PARTY ERRORS | 12 | ASSET INTEGRITY | S3 | F4 | 2026-07-30 | AUD-2026-06-2000015012ACN-2026-06-4000141726 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141726 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141726 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141726 | AUD-2026-06-2000015012ACN-2026-06-4000141726 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 53
SINGWAL DEEPAK | 2026-09-01 | GEETE DEVASHISH | 2026-09-01 | Since same observation was also made during previous location visit. Therefore, the compliance of this observation is to be referred from particular no. 1.4 of this audit sheet and from the particular no. 4.3 of previous visit report AUD-2026-03-2000011237 Closed, Duplicate recommendation, same is mentioned in part code 3.17 | LOCATION VISIT AT GWALIOR IRD | 2026-06-20 | AUD-2026-06-2000015012 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141727 | Closed | GEETE DEVASHISH | 2026-09-01 | Yes, TAS Revamp Project is under progress. | 4.3 | Project progress reviewed | 1435 | GWALIOR DEPOT | Location to coordinate with AST for expediting completion of Project at the earliest. | SOD | Marketing | CEN | 2026-09-30 | THIRD PARTY ERRORS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-09-30 | AUD-2026-06-2000015012ACN-2026-06-4000141727 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000015012ACN-2026-06-4000141727 | 2026-08-22 19:00 | 57.9622 | 365 | >20 | AUD-2026-06-2000015012 - ACN-2026-06-4000141727 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000015012ACN-2026-06-4000141727 | AUD-2026-06-2000015012ACN-2026-06-4000141727 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 53
DEWADE SHAHAJI NAGORAO | 2026-09-02 | ANSHU KUMAR SINGH | 2026-09-02 | Faulty tachometer is replaced For FE - 1 Engine. Now, it is working condition. | MIRAJ LOCATION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016453 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146538 | Closed | ANSHU KUMAR SINGH | 2026-09-02 | Checked working of Fire engines and found working. Tachometer of fire engine-1 is not working | 2.5 | Emergency response preparedness reviewed | 1504 | MIRAJ TERMINAL | Corrective action to be taken | SOD | Marketing | WZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016453ACN-2026-07-4000146538 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016453ACN-2026-07-4000146538 | 2026-09-01 | 48.7538 | 366 | >20 | AUD-2026-07-2000016453 - ACN-2026-07-4000146538 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016453ACN-2026-07-4000146538 | AUD-2026-07-2000016453ACN-2026-07-4000146538 | 21 | 21 | 27 | 80 | 0 | -1 | 44 | 53
|  | ANSHU KUMAR SINGH | 2026-09-02 | VA System has been activated. Now working properly. | MIRAJ LOCATION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016453 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146539 | Completed | ANSHU KUMAR SINGH | 2026-09-02 | VA system is intermittently not working. | 2.7 | VA alerts checked / analysed | 1504 | MIRAJ TERMINAL | Location to check and ensure VA system is working continuosly. | SOD | Marketing | WZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-07-2000016453ACN-2026-07-4000146539 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016453ACN-2026-07-4000146539 | 2026-09-01 | 48.7538 | 302 | >20 | AUD-2026-07-2000016453 - ACN-2026-07-4000146539 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016453ACN-2026-07-4000146539 |  | AUD-2026-07-2000016453ACN-2026-07-4000146539 | 21 |  | 27 | 80 | 0 | -1 | 44
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | Open path near MS tank TF07, alarm not generated for 10-40% LEL- HCD was okay, issue was with filter used for checking, new filter procured now. Checked and found working ok. Open Path HCD near TF-7 shifted from drain area to near valves. Photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000140181 | Closed | SINGH PREETI | 2026-09-01 | Checked Open path at Product pump house, Point type at dyke 2 drain. Both performed satisfactory. Open path near MS tank TF07, alarm not generated for 10-40% LEL. Open Path HCD near TF-07 drain in Dyke-02 to be shifted. Open path HCDs are for manifolds/valves. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140181 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140181 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140181 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140181 | AUD-2026-06-2000013929ACN-2026-06-4000140181 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | Drain cleaning near HSD Tank TF-04 done, photos attached. Loose Wires near TF-4 clamped. Photos attached. HVLR-03 Control board placed near control panel. Nozzles for fire hydrant hoses procured. Work Permit locator board displayed, photos attached. Field observation register maintained. Tank Outage Plan maintained. Walkway made near HSD Tank Farm area. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140194 | Closed | SINGH PREETI | 2026-09-01 | • Drain cleaning near HSD Tank TF-04 in Dyke No. 1 to be done • Wire clamp to be fixed near TF-04 • HVLR-03 Control board to be placed near control panel. • Nozzle to be procured for fire hydrant hoses. • Work permit locator board to be displayed. • Field Observation register to be maintained. • Tank outage plan to be maintained. • Walkway to be made near compound wall in Tank farm area. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE SAFETY CULTURE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140194 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140194 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140194 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140194 | AUD-2026-06-2000013929ACN-2026-06-4000140194 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | Transformer daily checklist being maintained daily and signed History Card maintained for Fire Extinguishers. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000140196 | Closed | SINGH PREETI | 2026-09-01 | 1. Transformer daily check list last signed on date Apr'25. 2. Periodic testing of transformer i.e Oil testing, tan-delta, WTI-OTIcalibration carried out by location. 3. History card to be maintained for all Fire extinguishers | 4.4 | Quality of PM compliance reviewed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140196 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140196 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140196 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140196 | AUD-2026-06-2000013929ACN-2026-06-4000140196 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | Interlock for earthing during Ethanol TT unloading is successfully implemented at Bay-7 and Bay-8. Working of interlock is as follows : 1. Ethanol TT unloading pump will not start until the healthiness of earthing. 2. And if there is any interruption in earthing healthiness during the unloading, then pump will get stop immediately. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140813 | Closed | SINGH PREETI | 2026-09-01 | Earthing interlock while Ethanol unloading to be explored and implemented. | 6.16 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140813 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140813 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140813 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140813 | AUD-2026-06-2000013929ACN-2026-06-4000140813 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | All boards in field ensured with Sign and dates. Photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140800 | Closed | SINGH PREETI | 2026-09-01 | Date to be mentioned in all drawings on boards, and to be signed. | 6.3 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE SAFETY CULTURE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140800 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140800 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140800 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140800 | AUD-2026-06-2000013929ACN-2026-06-4000140800 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | Area Classification drawing displayed. Photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140801 | Closed | SINGH PREETI | 2026-09-01 | Area classification drawing to be displayed | 6.4 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | INADEQUATE SAFETY CULTURE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140801 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140801 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140801 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140801 | AUD-2026-06-2000013929ACN-2026-06-4000140801 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
SABLE RONAK MOHANKUMAR | 2026-09-02 | SINGH PREETI | 2026-09-01 | All faded boards in field replaced, photos attached. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140802 | Closed | SINGH PREETI | 2026-09-01 | All faded boards in field to be replaced | 6.5 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140802 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140802 | 2026-08-22 22:00 | 57.8372 | 366 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140802 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140802 | AUD-2026-06-2000013929ACN-2026-06-4000140802 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
[5 empty] | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150316 | Open |  |  | Location is advise to complete the induction of additional TTs to meet DS requirement. | 1.8 | Improvement plans discussed | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150316 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150316 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150316 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150316 |  | AUD-2026-08-2000016904ACN-2026-09-4000150316 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150320 | Open |  |  | 1. HVLR 1 & 2 checked. Both performed satisfactory. 2. Local hooter of dyke 2,3 was not working. 3. Dyke 2 open path HCD checked and found working however local hooter not activated. 4. Sprinkler of TK 06 checked. U11, U20, U21, U22, U23, L15, U25, U26 is found choked. 5. Drain point sprinkler line found open. 6. Fire wall valve is passing for dyke 2. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-15 |  | 1 |  | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016904ACN-2026-09-4000150320 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150320 | 2026-08-06 | 74.7538 | 379 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150320 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150320 |  | AUD-2026-08-2000016904ACN-2026-09-4000150320 | 21 |  | 27 | 80 | 2 | 2 | 55
[5 empty] | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150321 | Open |  |  | As of now, Location has not identified trained personnel with HVD/HZA to move TT. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-15 |  | 1 |  | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016904ACN-2026-09-4000150321 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150321 | 2026-08-06 | 74.7538 | 379 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150321 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150321 |  | AUD-2026-08-2000016904ACN-2026-09-4000150321 | 21 |  | 27 | 80 | 2 | 2 | 55
[5 empty] | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150326 | Open |  |  | Full field visit of Tank farm area, pump house, Sample Room, Fire Engine shed etc, housekeeping and clearance of roads around tank farm is satisfactory. Following observations are made. 1. Holes over wind girder is observed at TK14. 2. SOPs are faded in the field. 3. Wire mesh not available for TK14 foam nozzle. 4. Foam dam bottom openings for tank TK14 was found choked. 5. Wind socks tobe beployed at strategic points. 6. P&I of MS/HSD displayed in the field is not updated. 7. Water tank filling pipe line rusted, painting to be done. 8. Calibration tower water line rusted. Painting to be done. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150326 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150326 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150326 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150326 |  | AUD-2026-08-2000016904ACN-2026-09-4000150326 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150332 | Open |  |  | Location to dispose off documents kept in godown in line with document retention policy. | 6.4 | Additional Observations | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150332 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150332 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150332 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150332 |  | AUD-2026-08-2000016904ACN-2026-09-4000150332 | 21 |  | 27 | 80 | 2 | 2 | 57
TAK MITHLESH KUMAR | 2026-09-02 |  |  | 1. One HVLR is working Fine . Another is working in manual mode however Visit of OEM completed for issue of HVLR . Spare Recommended . Nomination PO Placed. Expected to be completed by Sept-2026 Point Combined with Sr No 2.11 Q2 2026-27 Completed 3. OEM visitedon 27.06.2026 m rectified the issud of HCD-Completed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137161 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | 1. Both available HVLR found not working at location. 2. Point type HCD installed between TW track and dyke 5 area for OWS pit waskept aside and not installed properly. 3. Open path and point type HCD installed in TK09 dyke were found not working. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-06-2000012347ACN-2026-06-4000137161 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137161 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137161 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137161 | AUD-2026-06-2000012347ACN-2026-06-4000137161 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Presently all TT Drivers are available with Hazardous License . Point Combined with Q2 2026-27 Sr No 2.13 | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137162 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-06-2000012347ACN-2026-06-4000137162 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137162 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137162 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137162 | AUD-2026-06-2000012347ACN-2026-06-4000137162 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Eyesight /Colour Blindness Awarness Booklet ordered and received at Location | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137164 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Facility not available. | 2.16 | Eyesight / colour-blindness awareness checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-05 | AUD-2026-06-2000012347ACN-2026-06-4000137164 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137164 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137164 | 532 | 8294 | 21 | 8294 | 116 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137164 | AUD-2026-06-2000012347ACN-2026-06-4000137164 | 21 | 21 | 27 | 80 | 2 | 2 | 43 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | LED lights are repaired in Fire Engine Shed and Hight Mast Lights are repaired in Tank Farm Area . | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137188 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Checked and found adequate at the fire engine shed. Inadequate in tank farm area. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2027-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000012347ACN-2026-06-4000137188 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137188 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137188 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137188 | AUD-2026-06-2000012347ACN-2026-06-4000137188 | 21 | 21 | 27 | 80 | 2 | 2 | 83 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | 1. One HVLR is working Fine . Another is working in manual mode however Visit of OEM completed for issue of HVLR . Spare Recommended . Nomination PO Placed..Point Combined with Sr No 2.11 Q2 2026-27 Completed HCD is working now. FIre Engine No 3 repaired and working . Sequence Work is Completed. Training provided to security guards Empty drums are removed from field and filled drums are placed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137158 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Location to review and strengthen the fire fighting and safety equipment at location. Both HVLR and HCDs in the field were found not in working condition. Fire engine under breakdown and failing to start as per sequance is critical observation. Security guard not aware of fire engine and HVLR operation. All foam canes/drum were found empty at monitor installed near emergency gate and terminal tank farm area. | 2.5 | Emergency response preparedness reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-06-2000012347ACN-2026-06-4000137158 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137158 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137158 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137158 | AUD-2026-06-2000012347ACN-2026-06-4000137158 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Gate is repaired and now in working conditions | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137171 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | 1. Emergency exit gate of MCC room found broken. Same shall be repaired. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-05 | AUD-2026-06-2000012347ACN-2026-06-4000137171 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137171 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137171 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137171 | AUD-2026-06-2000012347ACN-2026-06-4000137171 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Same is also Observed for Q2 Sr Management Inspection 2026-27 Sr No 6.2 | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137176 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Concertina coil shall be installed over security building as it is in continuation of boundary wall. | 6.2 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-06-2000012347ACN-2026-06-4000137176 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137176 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137176 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137176 | AUD-2026-06-2000012347ACN-2026-06-4000137176 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Fire Engine Sequence is updated by TAS vendor however sequence is working fine for Main Fire engines but issue in standyby engines .Work is completed | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137179 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Fire engine as per sequnce failed to start in the field. Sequance set was 1,2,4,5 Main and 3 & 6 standby. Fire engine 1 did not start at all, fire engine no 2 & 4 tripped. Only fire engine 5 successfully ran. | 6.5 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-06-2000012347ACN-2026-06-4000137179 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137179 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137179 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137179 | AUD-2026-06-2000012347ACN-2026-06-4000137179 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 53
|  |  |  | Q4 2025-26 Total 21, Pending -03 Nos . Q1 2026-27 Total 31 , Pending -03. Work under progress for all Pending Points | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147082 | Open | NEHARA AJAY | 2026-10-17 | Compliance to previous audit observation is pending at location. | 1.4 | Earlier action points status checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147082 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147082 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147082 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147082 |  | AUD-2026-08-2000016270ACN-2026-08-4000147082 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | """1. 1. One HVLR is working Fine . Another is working in manual mode however Visit of OEM completed for issue of HVLR . Spare Recommended . Nomination PO Placed. Panel card received at location on 13.10.2026. AMC vendor visit planned for installation and testingin auto mode 2.Fire Engine No 1 is working fine . 3. Foam Drums were replaced with filled drums at all locations in the field . Training is provided to Security Staff for FE operation. """ | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147086 | Open | NEHARA AJAY | 2026-10-17 | Location to review and strengthen the fire fighting and safety equipment at location. One HVLR is not oprational from remote. Fireengine 1 failed to start as per sequance. All foam canes/drum were found empty at monitor installed near emergency gate and terminal tank farm area. Same observation was recorded in last inspection also. Security personnel Sh Balveer Singh was asked to operate DCP and he did same satisfactory. | 2.5 | Emergency response preparedness reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-08-2000016270ACN-2026-08-4000147086 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147086 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147086 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147086 |  | AUD-2026-08-2000016270ACN-2026-08-4000147086 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | """1. One HVLR is working Fine . Another is working in manual mode however Visit of OEM completed for issue of HVLR . Spare Recommended . Nomination PO Placed. Panel card received at location on 13.10.2026. AMC vendor visit planned for installation and testing inauto mode""" | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147089 | Open | NEHARA AJAY | 2026-10-17 | 1. one HVLR not working in remote mode. 2. ESD checked near Tank 312 and found working | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-08-2000016270ACN-2026-08-4000147089 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147089 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147089 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147089 |  | AUD-2026-08-2000016270ACN-2026-08-4000147089 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Present all TT drivers are having vaild Hazardous License . Security Person/other Contract workmen will be identified for HazardousGoods License | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147090 | Open | NEHARA AJAY | 2026-10-17 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-08-2000016270ACN-2026-08-4000147090 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147090 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147090 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147090 |  | AUD-2026-08-2000016270ACN-2026-08-4000147090 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Present Status MDSA 24-25 -02 Nos , MDSA 25-26-15 Nos.Pending points work is in progress. | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147098 | Open | NEHARA AJAY | 2026-10-17 | Location to comply 19 numbers of MDSA 24-25 and 36 numbers of MDSA 25-26 points are required to closed on priority. Location to close open observation of Sr. Management inspection. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147098 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147098 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147098 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147098 |  | AUD-2026-08-2000016270ACN-2026-08-4000147098 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Scrap Valuation is completed for Assets Mentioned in Observations . RFD under process | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147852 | Open | NEHARA AJAY | 2026-10-17 | Scrap disposal to be initaied for fire engine, lights, defective valves, MS pipes, structure, plastic drum/buckets, wooden packing material, idle unused assets, cable etc | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147852 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147852 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147852 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147852 |  | AUD-2026-08-2000016270ACN-2026-08-4000147852 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Concentrina Coil arranged, work under progress, It will be installed by 31.10.2026 | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147854 | Open | NEHARA AJAY | 2026-10-17 | Concertina coil shall be installed over security building as it is in continuation of boundary wall. | 6.2 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-08-2000016270ACN-2026-08-4000147854 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147854 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147854 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147854 |  | AUD-2026-08-2000016270ACN-2026-08-4000147854 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | """Painting is required for all Pipelines and structures at TT Gantry . Additional Budget proposal under progress in MEB . Budget proposal for mechanical works under progress - Supports will be completed once funds are alloted""" | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147862 | Open | NEHARA AJAY | 2026-10-17 | Biodiesel unloading is not painted and getting rusted. Supports are not provided. | 6.10 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147862 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147862 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147862 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147862 |  | AUD-2026-08-2000016270ACN-2026-08-4000147862 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Drain Work under progress. One Pipe is to be provided. | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147864 | Open | NEHARA AJAY | 2026-10-15 | Gantry periphery drain is not in closed loop | 6.12 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-08-2000016270ACN-2026-08-4000147864 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147864 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147864 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147864 |  | AUD-2026-08-2000016270ACN-2026-08-4000147864 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Presently No new Flow meter is available at location . Requirement of Flowmeter will be initiated in next NPCB cycle 2026-27 | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147866 | Open | NEHARA AJAY | 2026-10-17 | Location is using flowmeter made in year 1985 for accounting of HSD being given to Bhuj ASF. | 6.14 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147866 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147866 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147866 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147866 |  | AUD-2026-08-2000016270ACN-2026-08-4000147866 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | """PO No: 5200137692 dated 26/08/2026 placed on M/s MAHAKALI ENTERPRISES For printing of SOPs . SOP Printing work under progress""" | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147870 | Open | NEHARA AJAY | 2026-10-17 | SOP is not displayed at calibration tower and air compressor shed. | 6.18 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016270ACN-2026-08-4000147870 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147870 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147870 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147870 |  | AUD-2026-08-2000016270ACN-2026-08-4000147870 | 21 |  | 27 | 80 | 2 | 2 | 52
|  |  |  | Letter Writing work under progress in terminal, will be completed 31.10.2026 | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147871 | Open | NEHARA AJAY | 2026-10-17 | Relay testing, motor/MCCB/Fuse etc rating are not mentioned over electrical panel inside MCC room. | 6.19 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-08-2000016270ACN-2026-08-4000147871 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147871 | 2026-08-16 | 64.7538 | 364 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147871 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016270ACN-2026-08-4000147871 |  | AUD-2026-08-2000016270ACN-2026-08-4000147871 | 21 |  | 27 | 80 | 2 | 2 | 52
TAK MITHLESH KUMAR | 2026-09-02 |  |  | it is ensured that 100% Valve checking of all TTs are take place | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147083 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | HQO communication of 100% checking of bottom valve is not followed at location. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147083 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147083 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147083 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147083 | AUD-2026-08-2000016270ACN-2026-08-4000147083 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Scrap Disposal is done vide DO order No:MSTC/VAD/23-24/4374 dated 22/11/2023. Preventive Maintenance Activities are carried out in the field as per PM Schdeule | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147084 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Location to expedite the scrap disposal process. Location shall carry out preventive maintenace activity properly in the field. | 1.8 | Improvement plans discussed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016270ACN-2026-08-4000147084 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147084 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147084 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147084 | AUD-2026-08-2000016270ACN-2026-08-4000147084 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | 1. C BAC SYSTEM IS WORKING FINE . 2. ALL Open Access were due to Project works however it was closed after the inspection immediately | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147091 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Yes discussed and found satisfactory. As per location, Trem card with updated number is under printing. Emergency contact number written over TT (2836-654507) found not working. | 2.15 | TT crew roadside emergency procedures checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147091 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147091 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147091 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147091 | AUD-2026-08-2000016270ACN-2026-08-4000147091 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | 1. Fire Chief is giving instruction in Next drill during T4S Audit . 2. Training is provided to contract workmen 3. Valve is serviced .4. All Foam Drums are checkd and replaced with new one . 5. Hydrant Line is charged condition 6. Servicing of DCP carried out onmonthly basis . Powder is replaced 7. Items are kept as per name in emergency trolly | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147085 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Scenerio: Fire in Tank 312 manifold & Fire in UG MS pump. Observation: 1. Fire chief to instruct teams. Fire fighting teams werefound to be taking action as per there understanding. 2. No communication was given to operate foam pourer however same was operated. 3. Considerable time is lost in opening water valve and rotating the both foam monitor used in 1st scenerio. 4. 3 numbers of 200 ltr foam drum were kept near Tank out of which 2 were damaged which could not be used to replenish the foam. 5. Hydrant line ofsecond foam monitor was not charged and isolation valve could not be opened during fire drill. 6. In second scenerio, 2nd DCP could not be operated due to stucked pin. 7. Items are not kept in emergency trolley as per box tag creating confusion. | 2.2 | Double contingency scenario simulated; observations recorded | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147085 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147085 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147085 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147085 | AUD-2026-08-2000016270ACN-2026-08-4000147085 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | all PPEs VA Alerts are closed after propoer action to concern workmen. Counselling is done for all workmen regarding Mandatory Use of PPEs | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147087 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | VA alert related to PPE non compliance are generating at location. Regularly emails are being sent from zone. However numbers are not reducing and repeatative types alerts are still generating. Following VA alerts are reviewed. TAS_1583_SOP043_040726_000080 TAS_1583_SOP043_050726_000089 TAS_1583_SOP043_060726_000090 TAS_1583_SOP043_050726_000082 TAS_1583_SOP043_050726_000083 TAS_1583_SOP043_050726_000085 TAS_1583_SOP043_050726_000088 TAS_1583_SOP043_050726_000086 TAS_1583_SOP043_050726_000087 Location to take corrective action | 2.7 | VA alerts checked / analysed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147087 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147087 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147087 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147087 | AUD-2026-08-2000016270ACN-2026-08-4000147087 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | 1. C BAC SYSTEM IS WORKING FINE . 2. ALL Open Access were due to Project works however it was closed after the inspection immediately | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147088 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | C Bacs system installed near security building to access in license area gate was found not working. 2 other access for entering to license area by bypassing CBAC are found in open condition at location. One is between old canteen and store room and other is near water tank. Both of these gates were found open. | 2.8 | Access control systems checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147088 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147088 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147088 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147088 | AUD-2026-08-2000016270ACN-2026-08-4000147088 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Term Card Updated | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147092 | Closed | TAK MITHLESH KUMAR | 2026-09-02 |  | 3.1 | TT fittings & discipline checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147092 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147092 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147092 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147092 | AUD-2026-08-2000016270ACN-2026-08-4000147092 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | All Waste Material is removed from Canteen Building and over the roof . Security Cabin roof building is cleaned . Admin Building roof is also cleaned | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147096 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | During field round of Tank farm area, pump house, Sample Room, Fire Engine shed etc, housekeeping and clearance of roads around tank farm is satisfactory. Huge dump of material was observed inside old canteen building and over the roof. Food packing wrapper was found inside room above security building Plant (Peepal) of stem diameter upto 2 inches were found over main admin building. Roof was having unorganised cables, choked drain points, exposed column reinforcement. | 3.15 | Housekeeping & PPE usage checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147096 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147096 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147096 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147096 | AUD-2026-08-2000016270ACN-2026-08-4000147096 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Air Dryer is working fine | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147097 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | MOC not available for non operational dryer. | 3.17 | MOC status reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147097 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147097 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147097 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147097 | AUD-2026-08-2000016270ACN-2026-08-4000147097 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | VTS deviation records are maintained, and all corrosponding data available in mail and novex portal. | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147093 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147093 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147093 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147093 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147093 | AUD-2026-08-2000016270ACN-2026-08-4000147093 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Kandla Terminal is manual DIP location . However Details are recorded for approval of Auto DIP | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147094 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Reconciliation is being done basis the daily day end TAS dips by entering tank dips manually. | 3.8 | Auto vs Manual reconciliation checked | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147094 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147094 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147094 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147094 | AUD-2026-08-2000016270ACN-2026-08-4000147094 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Segregation of Material from Store Room Completed . One Security Register is maintianed at location for inventory verification (IN/OUT) | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147095 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Comments are being recorded for abnormal variation. Store room is completely filled with surplus material. Location is not having list of material stored in the room. | 3.9 | Abnormal variations / unused assets reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147095 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147095 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147095 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147095 | AUD-2026-08-2000016270ACN-2026-08-4000147095 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Emergency Exit Gate of MCC is repaired | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147099 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | 1. Emergency exit gate of MCC room found broken. Same shall be repaired. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147099 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147099 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147099 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147099 | AUD-2026-08-2000016270ACN-2026-08-4000147099 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | No Recommendations | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147850 | Closed | TAK MITHLESH KUMAR | 2026-09-02 |  | 4.2 | Maintenance activities reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147850 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147850 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147850 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147850 | AUD-2026-08-2000016270ACN-2026-08-4000147850 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Location is ensuring the same | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147851 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | PM orders are being closed on time. Location to ensure checklist are filled post careful inspection of equipment and accordingly records shall be updated on daily basis. | 4.4 | Quality of PM compliance reviewed | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147851 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147851 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147851 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147851 | AUD-2026-08-2000016270ACN-2026-08-4000147851 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Vertical Support is corrected at TT Gantry Emergency Exit | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147853 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Vertical support of emergency exit at TT gantry are hanging in air, not in contact with ground. | 6.1 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147853 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147853 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147853 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147853 | AUD-2026-08-2000016270ACN-2026-08-4000147853 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Wrapping Coating is provided to Pipelines near TT Gantry | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147863 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Wrapping coating of pipe line laid in pit near TT gantry is not done. | 6.11 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147863 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147863 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147863 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147863 | AUD-2026-08-2000016270ACN-2026-08-4000147863 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | All SOPs are updated and Sent for review at NWZ As per the field Arrangements . | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147865 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Location could not confirm availability of updated HSD own use SOP, product receipt from BPC vessel line as per field arrangement | 6.13 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147865 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147865 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147865 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147865 | AUD-2026-08-2000016270ACN-2026-08-4000147865 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Operating Plateform is fixed near TT Gantry for M01 | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147867 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Operating plateform of monitor M01 in front of TT gantry is not fixed properly on the ground. | 6.15 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147867 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147867 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147867 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147867 | AUD-2026-08-2000016270ACN-2026-08-4000147867 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Safety Inspection is carried out for water tankers also | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147868 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Safety Inspection of water tanker entering in premises is not being done. Vehicle is found with Battery installed outside cabin without rubber cap over terminals and battery storage cabinet cover was mettalic and almost on verge of touching terminals. | 6.16 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147868 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147868 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147868 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147868 | AUD-2026-08-2000016270ACN-2026-08-4000147868 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Transporter is advised for the same . Availability of TT Crew and Wheel Choke is ensured | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147869 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | TT parked at calibration tower is found without TT crew and without wheel choke. SOP violation. | 6.17 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147869 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147869 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147869 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147869 | AUD-2026-08-2000016270ACN-2026-08-4000147869 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Cleaning is done for EP52 Earthpit | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147872 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | EP52 was tested on 03.06.2026 however EP electrode was found completed covered in mud including terminals. | 6.20 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147872 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147872 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147872 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147872 | AUD-2026-08-2000016270ACN-2026-08-4000147872 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | All Sample Bottles are removed from OLD Canteen Building . Cleaning is done . | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147873 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Numbers of filled sample bottles were found kept inside Old canteen building. Location was not aware of same. | 6.21 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147873 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147873 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147873 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147873 | AUD-2026-08-2000016270ACN-2026-08-4000147873 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Wind Grider is cleaned however Bird dropping issue is frequently observed by location | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147874 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Wind girder of MS tank 10 was found covered with bird dropping. | 6.22 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147874 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147874 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147874 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147874 | AUD-2026-08-2000016270ACN-2026-08-4000147874 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Bay Numbering is provided on Back TOP side of TT Gantry | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147875 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Bay numbering is not available at TT gantry. | 6.23 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147875 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147875 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147875 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147875 | AUD-2026-08-2000016270ACN-2026-08-4000147875 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | All SOPs are updated and Sent for review at NWZ As per the field Arrangements . | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147876 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Location to review the availability of updated SOP for available operations. | 6.24 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147876 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147876 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147876 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147876 | AUD-2026-08-2000016270ACN-2026-08-4000147876 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | DP Gauge is repaired at Bay No 4 and working fine | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147855 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | DP gauge found broken and not working at Bay no 4. | 6.3 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147855 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147855 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147855 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147855 | AUD-2026-08-2000016270ACN-2026-08-4000147855 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | One Safety Belt is provided for Helper only . At a time only one person is allowed to go on the TOP of TTs . Hence Not required | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147856 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Safety belt not available for second harness installed at TT gantry. | 6.4 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147856 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147856 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147856 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147856 | AUD-2026-08-2000016270ACN-2026-08-4000147856 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Fire Engines are working in Proper Sequence . Fire Engine No 1 is repaired . | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147857 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Fire engine as per sequnce failed to start in the field. Sequance set was 2,1,4,5 Main and 6 & 3 standby. Fire engine 1 did not start at all. fire engine no 3 started own its own along with fire engine 4. | 6.5 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147857 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147857 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147857 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147857 | AUD-2026-08-2000016270ACN-2026-08-4000147857 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Air Dryer is working fine | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147858 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Dryer was kept in off condition while associated air compressor was in operation. Covers of both air dryer were found kept over unit without screw. | 6.6 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147858 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147858 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147858 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147858 | AUD-2026-08-2000016270ACN-2026-08-4000147858 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | it is ensured that Gate Pass is prepared for water on daily basis | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147859 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Gate pass is not being prepapared of daily basis for drinking water including transport vehicle. Last gate was prepared on date 18.05.2026. | 6.7 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147859 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147859 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147859 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147859 | AUD-2026-08-2000016270ACN-2026-08-4000147859 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Bay No 1 and Bay No 3 JB is plugged properly with dummy Blind Plugs | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147860 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Bay no 1 and Bay no 3 JB found with unplugged openings at TT gantry. | 6.8 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147860 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147860 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147860 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147860 | AUD-2026-08-2000016270ACN-2026-08-4000147860 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
TAK MITHLESH KUMAR | 2026-09-02 |  |  | Jumpers are provided in Black Oil Pipelines | SR MANAGEMENT INSPEC Q2 2026-27KANDLA TM | 2026-08-16 | AUD-2026-08-2000016270 | 2026-08-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147861 | Closed | TAK MITHLESH KUMAR | 2026-09-02 | Jumper are missing for black oil loading line flanges. | 6.9 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016270ACN-2026-08-4000147861 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016270ACN-2026-08-4000147861 | 2026-08-16 | 64.7538 | 366 | >20 | AUD-2026-08-2000016270 - ACN-2026-08-4000147861 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016270ACN-2026-08-4000147861 | AUD-2026-08-2000016270ACN-2026-08-4000147861 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Pending points complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141868 | Closed | PATHAK AHELI | 2026-07-31 | Last visit by Zonal O&D Head in Feb'26. 13 observations complied, 6 are pending. | 1.4 | Earlier action points status checked | 1775 | BENGALURU TERMINAL | Pending observations to be complied by 31.07.2026 | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141868 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141868 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141868 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141868 | AUD-2026-06-2000014499ACN-2026-06-4000141868 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141872 | Closed | PATHAK AHELI | 2026-07-31 | Too many number of registers maintained by security at main gate. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1775 | BENGALURU TERMINAL | Same may be rationalised for effective control | SOD | Marketing | SWZ | 2026-07-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141872 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141872 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141872 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141872 | AUD-2026-06-2000014499ACN-2026-06-4000141872 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Additional Fire monitor near the fabrication shed provided. | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141873 | Closed | PATHAK AHELI | 2026-07-31 | Reviewed during visit; found satisfactory. | 2.5 | Emergency response preparedness reviewed | 1775 | BENGALURU TERMINAL | Addditional Fire monitor near the fabrication shed shall be provided. | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141873 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141873 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141873 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141873 | AUD-2026-06-2000014499ACN-2026-06-4000141873 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141881 | Closed | PATHAK AHELI | 2026-07-31 | Critical Alarms checked in TAS, advised location for detailed descriptions to be made against each alarms. | 3.12 | Critical alarms checked & corrective actions reviewed | 1775 | BENGALURU TERMINAL | Alarms to cleared with correct comments | SOD | Marketing | SWZ | 2026-07-10 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141881 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141881 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141881 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141881 | AUD-2026-06-2000014499ACN-2026-06-4000141881 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-06-4000141885 | Closed | PATHAK AHELI | 2026-07-31 | Same not available in LIC cabin | 5.2 | Updation of various statutory renewal dates in formation in LIC cabin | 1775 | BENGALURU TERMINAL | To be provided with updated details | SOD | Marketing | SWZ | 2026-07-10 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000014499ACN-2026-06-4000141885 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141885 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141885 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141885 | AUD-2026-06-2000014499ACN-2026-06-4000141885 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-09-02 | colour banding done in BAEs. | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141886 | Closed | PATHAK AHELI | 2026-09-02 | Color bands in few BAE's not available . | 6.1 | Additional Observations | 1775 | BENGALURU TERMINAL | Shall be provided as per latest IQCM | SOD | Marketing | SWZ | 2026-07-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-06-2000014499ACN-2026-06-4000141886 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141886 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141886 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141886 | AUD-2026-06-2000014499ACN-2026-06-4000141886 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 53
KUMAR CHAKRABORTI ALOK | 2026-09-02 | PATHAK AHELI | 2026-07-31 | Resolved | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141891 | Closed | PATHAK AHELI | 2026-07-31 | Auto density printing for MS is only 50% | 6.6 | Additional Observations | 1775 | BENGALURU TERMINAL | Issue to be taken up with TAS vendor for resolution | SOD | Marketing | SWZ | 2026-07-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141891 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141891 | 2026-09-24 17:00 | 25.0455 | 366 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141891 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141891 | AUD-2026-06-2000014499ACN-2026-06-4000141891 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 53
SINGH SOURABH | 2026-09-02 | BITTU KUMAR | 2026-09-02 | Training on CCTV monitoring and Fire Alarm Panel operation has been imparted to the security team. The security guards have been briefed on proper monitoring, identification of alarms, and the required response procedures during any abnormal/emergency situation. | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149296 | Closed | BITTU KUMAR | 2026-09-02 | During the night surprise visit, Head Security Guard Shri Arun Pandey and Security Guards Shri Surender, Shri Kashinath, and Shri Asgar Khan were found awake, alert, and vigilant. The security personnel demonstrated adequate awareness regarding the operation of the Fire Engine for handling emergency situations. All relevant gate registers were found to be properly maintained. However, it wasobserved that the security personnel should also be adequately trained in monitoring CCTV cameras and the Fire Alarm Panel to ensure timely detection of abnormalities and prompt response during emergencies. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1319 | MUGHALSARAI DEPOT | Traning to be imparted to security guard for CCTV monitoring and Fire Alarm Panel. | SOD | Marketing | NCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000149296 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000149296 | 2026-09-02 17:30 | 47.0247 | 366 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000149296 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015715ACN-2026-08-4000149296 | AUD-2026-07-2000015715ACN-2026-08-4000149296 | 21 | 21 | 27 | 80 | 1 | 2 | 57 | 53
SINGH SOURABH | 2026-09-02 | BITTU KUMAR | 2026-09-02 | Faulty lights have been rectified and lights have been provided to ensure adequate illumination. | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150503 | Closed | BITTU KUMAR | 2026-09-02 | Lights of Bay 2/3 , Pole No -45 at TK-16 along with additive dosing Shed is found to be faulty | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Faulty Lights to be recitified. | SOD | Marketing | NCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150503 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150503 | 2026-09-02 17:30 | 47.0247 | 366 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150503 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015715ACN-2026-08-4000150503 | AUD-2026-07-2000015715ACN-2026-08-4000150503 | 21 | 21 | 27 | 80 | 1 | 2 | 57 | 53
SINGH SOURABH | 2026-09-02 | BITTU KUMAR | 2026-09-02 | The latest approved EHS Policy has been prominently displayed at the entry of the licensed area and other designated locations to ensure visibility to all employees, contractors, and visitors. | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150502 | Closed | BITTU KUMAR | 2026-09-02 | Old EHS policy found in the Location at the entry of Licence area | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Display the latest approved EHS Policy prominently at the entry of the licensed area and other designated locations to ensure its visibility to all employees, contractors, and visitors | SOD | Marketing | NCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150502 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150502 | 2026-09-02 17:30 | 47.0247 | 366 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150502 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015715ACN-2026-08-4000150502 | AUD-2026-07-2000015715ACN-2026-08-4000150502 | 21 | 21 | 27 | 80 | 1 | 2 | 57 | 53
SINGH SOURABH | 2026-09-02 | BITTU KUMAR | 2026-09-02 | Adequate lighting arrangements have been provided along the boundary wall to ensure proper illumination, enhance visibility, | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150505 | Closed | BITTU KUMAR | 2026-09-02 | At the junction of BPC/HPC boundray wall no lights found | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Lighting arrangement is to be provided at the Boundary wall | SOD | Marketing | NCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150505 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150505 | 2026-09-02 17:30 | 47.0247 | 366 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150505 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015715ACN-2026-08-4000150505 | AUD-2026-07-2000015715ACN-2026-08-4000150505 | 21 | 21 | 27 | 80 | 1 | 2 | 57 | 53
SINGH SOURABH | 2026-09-02 | BITTU KUMAR | 2026-09-02 | Refresher training on the operation of safety equipment has been provided to the security guards to ensure their awareness and effective response during emergencies. | ZONAL INSPECTION Q1-2026-27 MUGHALSARAI | 2026-06-25 17:30 | AUD-2026-07-2000015715 | 2026-06-22 22:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150504 | Closed | BITTU KUMAR | 2026-09-02 | Lack of trainiing found with security guards w.r.t. safety equipment (Hand held MEFG) and CCTV monitoring. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Refresher training programs w.r.t. operation of Safety equipment to be imparted to security guards. | SOD | Marketing | NCR | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000015715ACN-2026-08-4000150504 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015715ACN-2026-08-4000150504 | 2026-09-02 17:30 | 47.0247 | 366 | >20 | AUD-2026-07-2000015715 - ACN-2026-08-4000150504 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015715ACN-2026-08-4000150504 | AUD-2026-07-2000015715ACN-2026-08-4000150504 | 21 | 21 | 27 | 80 | 1 | 2 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-02 | SUNITA | 2026-05-16 | Hydrant line of wagon gantry is painted. Hydrant of TT gantry is being replaced. Rusted toe guards of catwalks are being replaced.Faulty platform and ladders to TWG gantry are being replaced. All Faulty valves of TWG are replaced. Tank 452 and 604 are taken under outage for maintenance | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127128 | Closed | SUNITA | 2026-05-16 | Conduted | 1.2 | Performance review conducted | 1585 | MAHUL TERMINAL | Painting to be started, equipment maintance and structure maintenance to be done | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-30 | AUD-2026-03-2000010975ACN-2026-03-4000127128 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127128 | 2026-10-17 | 2.7538 | 366 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127128 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010975ACN-2026-03-4000127128 | AUD-2026-03-2000010975ACN-2026-03-4000127128 | 21 | 21 | 26 | 80 | 28 | 28 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-02 | SUNITA | 2026-08-27 | Revised Contract Manpower approval taken. NPCB proposals for PA Paging, LPS, Fire hose, hydrants, GI gratings got appproved under NPCB 2026-27. Proposal submitted new CCTV and TT gantry revamp and TAS at location under NPCB 2026-27. NPCB budet also approved under 25-26 for tanks revamp and Approach Road of wagon gantry. | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127130 | Closed | SHINDE ANAND LAXMAN | 2026-09-02 | Budget for M&R, NPCB of criticla items, Manpower | 1.5 | HQO / Zonal support required identified | 1585 | MAHUL TERMINAL | To be re-applied for budget in April 2026 | SOD | Marketing | WZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000010975ACN-2026-03-4000127130 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127130 | 2026-10-17 | 2.7538 | 366 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127130 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010975ACN-2026-03-4000127130 | AUD-2026-03-2000010975ACN-2026-03-4000127130 | 21 | 21 | 26 | 80 | 28 | 28 | 44 | 53
SHINDE ANAND LAXMAN | 2026-09-02 | SUNITA | 2026-08-27 | Portable MEFG is checked as part of Monthly AMC of FFEs. Entry is made in reports as Mobile foam trolley. Hence this observation came for mobile. Sample report from vendor M/s Eversure engg attached. | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127131 | Closed | SUNITA | 2026-08-27 | FE operated, Fe Monitor not operations due to valve failure. Fixed MEFG not availbale at location . Portable MEFG can be operated | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1585 | MAHUL TERMINAL | Portable MEFG to be checked regulary for operations | SOD | Marketing | WZ | 2026-04-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127131 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127131 | 2026-10-17 | 2.7538 | 366 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127131 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010975ACN-2026-03-4000127131 | AUD-2026-03-2000010975ACN-2026-03-4000127131 | 21 | 21 | 26 | 80 | 28 | 28 | 35 | 53
SHINDE ANAND LAXMAN | 2026-09-02 | SUNITA | 2026-05-16 | Strict advise is given to all contractor to ensure PPE adherence to workmen. Safety incidents are recoded for unsafe act of not wearing PPE and explanation is taken. Garbage removal is taken weekly. Garbage removal actvity is slightly delayed due to CISF not providing witness | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127133 | Closed | SUNITA | 2026-05-16 | Hosekeeping poor. Person spoted in pipe alley without PPE | 3.15 | Housekeeping & PPE usage checked | 1585 | MAHUL TERMINAL | Housekeeping to improved. 100% PPE comliance to be done | SOD | Marketing | WZ | 2026-04-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127133 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127133 | 2026-10-17 | 2.7538 | 366 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127133 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010975ACN-2026-03-4000127133 | AUD-2026-03-2000010975ACN-2026-03-4000127133 | 21 | 21 | 26 | 80 | 28 | 28 | 35 | 53
[5 empty] | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150760 | Open |  |  | 28/07/2026 — Contract workmen found without safety belt (Prahalad). | 3.15 | Housekeeping & PPE usage checked | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 |  | 1 |  | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150760 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150760 | 2026-08-22 22:00 | 57.8372 | 374 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150760 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016905ACN-2026-09-4000150760 |  | AUD-2026-08-2000016905ACN-2026-09-4000150760 | 21 |  | 27 | 80 | 1 | 1 | 54
[5 empty] | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150761 | Open |  |  | 1. Terminal cover to be provided on batteries in battery room in Control Room. 2. Oversized glands in battery room in Control Room, to be rectified. 3. Battery stands not earthed. 4. Water seepage issue in Admin building, to be attended. 5. Copper tubing of ACs in Admin building exposed, tubing casing/cover to be provided. 6. Fire engine top up tank cleaning date not updated 7. Water leakage from flange of suction line in Fire Engine No. 4 8. FE SOP to be checked / updated 9. Hooter in Fire Engine panel not working for high temp etc 10. Air dryers of Air compressors not working 11. Due date of hydrotesting of Pressure vessel not updated. 12. UT date of pressure vessel to be mentioned. 13. Fire break wall valve in Dyke-2 found open. 14. End flange to be provided in all tank WDs end | 4.2 | Maintenance activities reviewed | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150761 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150761 | 2026-08-22 22:00 | 57.8372 | 394 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150761 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016905ACN-2026-09-4000150761 |  | AUD-2026-08-2000016905ACN-2026-09-4000150761 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150762 | Open |  |  | Location to identify scrap and usable material and initiate scrap disposal process. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150762 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150762 | 2026-08-22 22:00 | 57.8372 | 394 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150762 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016905ACN-2026-09-4000150762 |  | AUD-2026-08-2000016905ACN-2026-09-4000150762 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150768 | Open |  |  | SOP Boards shall be in local language as well. | 6.1 | Additional Observations | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150768 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150768 | 2026-08-22 22:00 | 57.8372 | 394 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150768 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016905ACN-2026-09-4000150768 |  | AUD-2026-08-2000016905ACN-2026-09-4000150768 | 21 |  | 27 | 80 | 1 | 1 | 57
|  |  |  | Discussion with Zone | GM INSPECTION_VASCO BOT_FEB2026 | 2026-02-28 | AUD-2026-09-2000017258 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150422 | Open | E PAULMURUGAN | 2026-09-03 | YES / 2023-24 Sludge payment / Sludge Qty to be dropped from inventory | 1.3 | Pending issues reviewed | 1551 | VASCO BLACK OIL TERMINAL | 2023-24 Sludge payment to be processed | SOD | Marketing | WZ | 2026-04-30 |  | 4 |  | S2 | F2 | 2026-04-30 | AUD-2026-09-2000017258ACN-2026-09-4000150422 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-09-2000017258ACN-2026-09-4000150422 | 2026-09-04 | 45.7538 | 241 | >20 | AUD-2026-09-2000017258 - ACN-2026-09-4000150422 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-09-2000017258ACN-2026-09-4000150422 |  | AUD-2026-09-2000017258ACN-2026-09-4000150422 | 21 |  | 26 | 80 | 31 | 31 | 35
[5 empty] | GM INSPECTION_VASCO BOT_FEB2026 | 2026-02-28 | AUD-2026-09-2000017258 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150423 | Open |  |  | E0 Officer required to look after ZIAVPL activities | 1.5 | HQO / Zonal support required identified | 1551 | VASCO BLACK OIL TERMINAL | To be discussed with HQO SOD | SOD | Marketing | WZ | 2026-03-31 |  | 1 |  | S1 | F1 | 2026-03-31 | AUD-2026-09-2000017258ACN-2026-09-4000150423 | GA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-09-2000017258ACN-2026-09-4000150423 | 2026-09-04 | 45.7538 | 211 | >20 | AUD-2026-09-2000017258 - ACN-2026-09-4000150423 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-09-2000017258ACN-2026-09-4000150423 |  | AUD-2026-09-2000017258ACN-2026-09-4000150423 | 21 |  | 26 | 80 | 31 | 31 | 31
[5 empty] | GM INSPECTION_VASCO BOT_MAY 2026 | 2026-05-28 | AUD-2026-09-2000017259 | 2026-05-28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150424 | Open |  |  | E0 Officer required to look after ZIAVPL activities | 1.5 | HQO / Zonal support required identified | 1551 | VASCO BLACK OIL TERMINAL | To be discussed with HQO SOD | SOD | Marketing | WZ | 2026-07-31 |  | 9 |  | S3 | F3 | 2026-07-31 | AUD-2026-09-2000017259ACN-2026-09-4000150424 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017259ACN-2026-09-4000150424 | 2026-09-04 | 45.7538 | 333 | >20 | AUD-2026-09-2000017259 - ACN-2026-09-4000150424 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017259ACN-2026-09-4000150424 |  | AUD-2026-09-2000017259ACN-2026-09-4000150424 | 21 |  | 27 | 80 | 31 | 31 | 48
[5 empty] | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150771 | Open |  |  | SKO top & bottom mix SOP at Bay 1 to be displayed | 6.1 | Additional Observations | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150771 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150771 | 2026-08-22 22:00 | 57.8372 | 394 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150771 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016905ACN-2026-09-4000150771 |  | AUD-2026-08-2000016905ACN-2026-09-4000150771 | 21 |  | 27 | 80 | 1 | 1 | 57
SUDHIR KUMAR | 2026-09-03 | SHETTY ANURANJAN | 2026-09-03 | local hooter verified and working. security trained on unhealthy signals in the TAS display board. Advisory also provided that anyunhealthy signal is to be informed to LIC nd control room | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125395 | Closed | SHETTY ANURANJAN | 2026-09-03 | 1. HVLR no. 5 was operated by LIC Jaipur. It worked well. 2. HCD of PH was checked. It gave signal at Control room. However, localhooter didn't sound. 3. Sprinkler operated for TK4 and TK12. It worked well. 4. Rim Seal Fire Protection system checked for TK5 and TK11. It worked well. 5. Foam pourer was operated for TK5. It worked well. 6. PA system at Gantry 1 was not working. 7. It wastried to stop HSD pump by pressing stop button at Gnatry. It worked well. 8. Earthing interlocks are working well at TT gantry. 9. ESD checked near TK8, found okay. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1242 | JAIPUR TERMINAL | Location to check local hooter. It should sound. Secondly, security should be trained that whenver they see any unhealthy signal (red signal) in the TAS display board, they should inform LIC and control room. Training should be enhanced. | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125395 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125395 | 2026-09-30 | 19.7538 | 367 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125395 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125395 | AUD-2026-03-2000011022ACN-2026-03-4000125395 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 53
AILAVARAPU VENKATA KRISHNA MURTY | 2026-09-03 | DIWAKAR KAMLESH KUMAR | 2026-09-02 | At Biometric Gate, Frisking ,is being done as per Guideline of HQO. DFMD madec functional. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143375 | Closed | DIWAKAR KAMLESH KUMAR | 2026-09-02 | Following points were observed during the security check at visitor entry gate: 1. Checking was not done before DFMD. Checking to be done before DFMD. 2. DFMD found to be out of service 3. No Frisking was done by security while entering to the terminal | 2.4 | Security alertness checked (night-halt / surprise checks) | 3708 | VISAKH NBOT | Following points to be ensured during the security check at visitor entry gate: 1. Checking to be done before DFMD. 2. DFMD foundto be repaired 3. Frisking to be done by security for all vistors before entering to the terminal | SOD | Marketing | SCR | 2026-06-18 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-18 | AUD-2026-07-2000015047ACN-2026-07-4000143375 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143375 | 2026-09-18 17:30 | 31.0247 | 367 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143375 | 532 | 8294 | 21 | 8294 | 123 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015047ACN-2026-07-4000143375 | AUD-2026-07-2000015047ACN-2026-07-4000143375 | 21 | 21 | 27 | 80 | 2 | 1 | 42 | 53
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000149674 | Open |  |  | a. Fire engine replacement project tender - Price bid opened. Negotiation etc to be expedited. b. Additional 15 TT for ATF to be expedited requirement. c. Matter of ATF DP/Bonded interswitching of tank to be expedited. d. Stockloss to be monitored on daily basisand corrective action to be taken e. Grass cutting below pipes to be given top priority. e. Tank repairs, Tank painting, ATF Pipeline repair and Boundary wall repairs to be carried out expeditiously. Activity is to be done in a Time bound manner. f. Pipeline thickness survey/ hydrotesting of pipelines to be carried out to ensure integrity of the pipeline system. Activity is to be done in aTime bound manner. | 1.3 | Pending issues reviewed | 1216 | BAHADURGARH TERMINAL | a to f. All pending issues to be complied in a time bound manner. | SOD | Marketing | NZ | 2027-03-30 |  | 1 |  | S1 | F1 | 2027-03-30 | AUD-2026-09-2000016768ACN-2026-09-4000149674 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149674 | 2026-09-05 | 44.7538 | 575 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149674 | 532 | 8294 | 21 | 8294 | -161 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149674 |  | AUD-2026-09-2000016768ACN-2026-09-4000149674 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000149675 | Open |  |  | All open points of Q4 2025-26 .Sr. Management Audit and Q1 2026-27 to be closed in SAP. | 1.4 | Earlier action points status checked | 1216 | BAHADURGARH TERMINAL | Necessary corrective action to be taken. Location to close the previous recommendations physically as well as update the status in SAP. | SOD | Marketing | NZ | 2027-03-30 |  | 1 |  | S1 | F1 | 2027-03-30 | AUD-2026-09-2000016768ACN-2026-09-4000149675 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149675 | 2026-09-05 | 44.7538 | 575 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149675 | 532 | 8294 | 21 | 8294 | -161 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149675 |  | AUD-2026-09-2000016768ACN-2026-09-4000149675 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000149676 | Open |  |  | Additional budget for Grass cutting, Pavement below pipes, Tank repairs, Ethanol pipes, Fire engine . Proposal to be submitted including surplus budget details for shifting of budget | 1.5 | HQO / Zonal support required identified | 1216 | BAHADURGARH TERMINAL | Additional budget for Grass cutting, Pavement below pipes, Tank repairs, Ethanol pipes, Fire engine . Proposal to be submitted including surplus budget details for shifting of budget | SOD | Marketing | NZ | 2027-09-10 |  | 1 |  | S1 | F1 | 2027-09-10 | AUD-2026-09-2000016768ACN-2026-09-4000149676 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149676 | 2026-09-05 | 44.7538 | 739 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149676 | 532 | 8294 | 21 | 8294 | -325 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149676 |  | AUD-2026-09-2000016768ACN-2026-09-4000149676 | 21 |  | 27 | 80 | 9 | 9 | 106
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149678 | Open |  |  | Single Contigency NIght Shift Drill was conducted on the night of 20th-21st August 2026 and following are the observations. The First Fire Extinguisher was operated by Security Guard who directed the Fire Extinguiser in the Air insteads of Hitting the Sourceof Fire. The FE Operator didn't maintain a safe distance from the Fire. The direction of Air was not taken into account whileoperating the Fire Extinguisher which resulted impaired the operators vision. Foam Monitor M53 was operated and the Valve of themonitor was jammed and took considersable time to open. The Foam barrel placed along the Monitor was partially empty. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1216 | BAHADURGARH TERMINAL | 1. Training to be given to all Company and Contractual Staff regarding operation of Fire Extinguishers. 2. Servicing of Fire Fighting equipments to be done on regular basis. 3. Foam Barrels placed along the Fire Fighting equipment to be checked for their Levels and Top to be done after any Usage/ afterr regular Checking. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149678 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149678 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149678 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149678 |  | AUD-2026-09-2000016768ACN-2026-09-4000149678 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149679 | Open |  |  | On Reviewing the Lux Level Report of July-2026 , it was observed that Lux level is not meeting in most places like Pump House, | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1216 | BAHADURGARH TERMINAL | Action for Achieving Recommended lux level to be taken. Format for recording the lux levels to be suitably modified. | SOD | Marketing | NZ | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-09-2000016768ACN-2026-09-4000149679 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149679 | 2026-09-05 | 44.7538 | 363 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149679 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149679 |  | AUD-2026-09-2000016768ACN-2026-09-4000149679 | 21 |  | 27 | 80 | 9 | 9 | 52
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149680 | Open |  |  | Surprise Inspection Register has not been updated after 01-Jan-2025. The same to be updated. Location may make a checklist for things to be focussed during the Surprise Night Inspection. No record of Inspection after Inspection in March which was recorded in lastAudit has been found. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1216 | BAHADURGARH TERMINAL | Location to perform Surprise Night Inspections and maintain record of Inspection along with entries in Gate register about visits done. | SOD | Marketing | NZ | 2026-08-30 |  | 5 |  | S1 | F5 | 2026-08-30 | AUD-2026-09-2000016768ACN-2026-09-4000149680 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149680 | 2026-09-05 | 44.7538 | 363 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149680 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149680 |  | AUD-2026-09-2000016768ACN-2026-09-4000149680 | 21 |  | 27 | 80 | 9 | 9 | 52
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149681 | Open |  |  | Discrepencies found in ERDMP are as below:_ 1. Ethanol Tanks has been shown as 4 instead of Actual 5. 2. TK14 and Tk16 have been taken out of SKO service, have shown in SKO in ERDMP. 3. Occupier Details has not been updated. 4. License Details on Page No. 37 are old, to be updated. 5. Emergency Contract on Page No. 75 to be updated. 6. Manpower Details on Page No. 76 to be updated. 7. First Aid Traning Details on Page No. 127 to. be updated. 8. Discrepencies observed in Sr. Managed Audit Q12026-27 are still pending. 9. LPR for ERDMP has been initiated for __________ | 2.5 | Emergency response preparedness reviewed | 1216 | BAHADURGARH TERMINAL | ERDMP to be thoroughly reveiwed and modified as per the actual site conditions and personnel available. | SOD | Marketing | NZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149681 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149681 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149681 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149681 |  | AUD-2026-09-2000016768ACN-2026-09-4000149681 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149682 | Open |  |  | There are total 139 cameras , 13 are down due to cable cut by Lubes Project team. | 2.6 | CCTV functioning checked | 1216 | BAHADURGARH TERMINAL | Cable repair to be expedited | SOD | Marketing | NZ | 2026-09-15 |  | 5 |  | S1 | F5 | 2026-09-15 | AUD-2026-09-2000016768ACN-2026-09-4000149682 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149682 | 2026-09-05 | 44.7538 | 379 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149682 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149682 |  | AUD-2026-09-2000016768ACN-2026-09-4000149682 | 21 |  | 27 | 80 | 9 | 9 | 55
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149683 | Open |  |  | In was found that the Fire Entinguishers have been painted recently and the Numbering of the Extinguishers has got removed. Contract Worker Mr. Sachidanand was asked to operate 25 KG DCP FE near Tk-28, TK-8. the Fire Extinguiser Operated satisfactorily. However leakage was observed from the Cap theadings of FE and the Contract worker Mr. Sachidanand needs refresher training of FE operation. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1216 | BAHADURGARH TERMINAL | Numbering of all FEs to be done. Fire Extinguisers to be tested periodically for their performance. Refresher training regarding operation of FE to be given | SOD | Marketing | NZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149683 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149683 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149683 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149683 |  | AUD-2026-09-2000016768ACN-2026-09-4000149683 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149687 | Open |  |  | Physical dips, and temparature were verified for tanks TK012 (HSD) and TK5 (MS), TS-04 and TS-03 . Variations under all parameters were found to be withing permissible tolerance limits. However, it has been noticed that RH as per Terminal Records and Actual RH isnot matching. | 3.7 | Inventory physical dip of minimum two tanks taken | 1216 | BAHADURGARH TERMINAL | Corrective Action to be taken. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149687 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149687 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149687 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149687 |  | AUD-2026-09-2000016768ACN-2026-09-4000149687 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149691 | Open |  |  | Boundary Wall - The boundary wall requires civil repair and repainting. At several locations, the plaster has deteriorated and is found to be dislodged. The concertina coil placed along the periphery and is intact. However, provision of broken glass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. At some places, adjoining properties structure have been found erected just near the location's boundary wall which is undesirable. | 3.16 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-09-2000016768ACN-2026-09-4000149691 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149691 | 2026-09-05 | 44.7538 | 485 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149691 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149691 |  | AUD-2026-09-2000016768ACN-2026-09-4000149691 | 21 |  | 27 | 80 | 9 | 9 | 70
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149693 | Open |  |  | No open OISD Points. MDSA 24-25 - 2 Open Points and MDSA 25-26 - 16 Open Points. HLSA - 2 Open points pertaininin to Full hight Turnstyle and Tyre Buster | 3.18 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | Closure of open points to be expedited | SOD | Marketing | NZ | 2027-03-30 |  | 5 |  | S1 | F5 | 2027-03-30 | AUD-2026-09-2000016768ACN-2026-09-4000149693 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149693 | 2026-09-05 | 44.7538 | 575 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149693 | 532 | 8294 | 21 | 8294 | -161 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149693 |  | AUD-2026-09-2000016768ACN-2026-09-4000149693 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149695 | Open |  |  | During the inspection of Tank No. TK12, sweating was observed on roof the floating roof of the tank and heavy pitting was also observed which may lead to further sweating or Leakages. Pin Hole leakages have been found on the Roof of TK-26 and TK-27 as well | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Same to be rectied in time bound manner | SOD | Marketing | NZ | 2027-03-31 |  | 5 |  | S1 | F5 | 2027-03-31 | AUD-2026-09-2000016768ACN-2026-09-4000149695 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149695 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149695 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149695 |  | AUD-2026-09-2000016768ACN-2026-09-4000149695 | 21 |  | 27 | 80 | 9 | 9 | 83
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149697 | Open |  |  | Admin Building : Toilet fitting rusted , need to be replaced. Door Mats in bad shape, one coat of painting required in entrance area, and TW Control room. Worker room false cieling to be rpaired, housekeeping to be improved. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149697 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149697 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149697 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149697 |  | AUD-2026-09-2000016768ACN-2026-09-4000149697 | 21 |  | 27 | 80 | 9 | 9 | 57
[5 empty] | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151050 | Open |  |  | All generated scrap to be disposed by 30.12.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1216 | BAHADURGARH TERMINAL | All generated scrap to be disposed by 30.12.2026 | SOD | Marketing | NZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-09-2000016768ACN-2026-09-4000151050 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000151050 | 2026-09-05 | 44.7538 | 485 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000151050 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000151050 |  | AUD-2026-09-2000016768ACN-2026-09-4000151050 | 21 |  | 27 | 80 | 9 | 9 | 70
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Training given to security on EGKMS. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137063 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Reviewed emergency trolley equipment and emergency gate. EGKMS hooter not working , power cable found disconnected . As per electrician power cable was disconnected as hooter was blowing continuosly. Electrician not aware of resetting the hooter from the push button provided at EGKMS . Same immediately rectified and checked and found the hooter is working.Interacted with officers & security personnel about their roles and responsibilities during emergencies | 2.5 | Emergency response preparedness reviewed | 1979 | VIJAYAWADA TERMINAL | Training to be given to Security for operating the EGKMS key | SOD | Marketing | SCR | 2026-06-05 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-05 | AUD-2026-06-2000012864ACN-2026-06-4000137063 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137063 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137063 | 532 | 8294 | 21 | 8294 | 136 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137063 | AUD-2026-06-2000012864ACN-2026-06-4000137063 | 21 | 21 | 27 | 80 | 12 | 12 | 40 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Tree branches cutting carried out.Lux levels are ok now. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137062 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Lux Levels checked , TT Gantry Bay no 5- 120, Bay no 7 - 130, TT gantry Platform- 190, Product P.H.- 190, Wagon Gantry -92, Tank 2Bmanifold - 39, Road near 1C - 27, Road opposite to TK4C- 23 , Road opposite to TK4A- 32 , Road near exchange pit 3, Control Room - 580, Admin building -128. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1979 | VIJAYAWADA TERMINAL | Lux Level to be improved on minor roads wherever not meeting the required Lux level | SOD | Marketing | SCR | 2026-07-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-30 | AUD-2026-06-2000012864ACN-2026-06-4000137062 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137062 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137062 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137062 | AUD-2026-06-2000012864ACN-2026-06-4000137062 | 21 | 21 | 27 | 80 | 12 | 12 | 48 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Remarks are being mentioned for all critical alarms. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137069 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Critical alarms were reviewed for past two month , alarms of HHH , tank dips variation in dormant state are Nil | 3.12 | Critical alarms checked & corrective actions reviewed | 1979 | VIJAYAWADA TERMINAL | Alarms acknowledged remarks not appearing in report. Officer to ensure remarks for all the critical alarms acknowledged in system | SOD | Marketing | SCR | 2026-06-15 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-15 | AUD-2026-06-2000012864ACN-2026-06-4000137069 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137069 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137069 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137069 | AUD-2026-06-2000012864ACN-2026-06-4000137069 | 21 | 21 | 27 | 80 | 12 | 12 | 41 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Dips are being checked for all TTs. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137067 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Three filled TTs dips checked at TT Gantry . TT no AP16TH7354 dips found OK. TT no AP39UC1414 at bay no 4 , dip of Compt I short by5mm , Compt II short by 4 mm, Compt III, IV & V dips are OK. s, TT no AP27TY1899 at bay no. 2 , dip of Compt I short by 4 mm and compt II & III are OK. | 3.2 | Post-loading dip checks verified | 1979 | VIJAYAWADA TERMINAL | Officers to check TT dips regularly and corrective action to be taken for any deviations | SOD | Marketing | SCR | 2026-06-10 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-10 | AUD-2026-06-2000012864ACN-2026-06-4000137067 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137067 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137067 | 532 | 8294 | 21 | 8294 | 131 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137067 | AUD-2026-06-2000012864ACN-2026-06-4000137067 | 21 | 21 | 27 | 80 | 12 | 12 | 41 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Integration of radar gauges completed with TAS. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137068 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Physical dip has been checked for HSD Tank TK 3B and MS Tank 1A. Tank 3B - Physical dip of 634.1cms against TAS dip of 633.3 cms . Water physical dip observed 4.2 cms against TAS dip of 4.5 cms Variation in dip 8 mm. Tank 1A - Physical dip of 157.7 cms against TAS dip of 157.8 cms . Water physical dip observed 2.6 cms against TAS dip of 2.0 cms . PO placed for integration of the new radar guages with TAS , at present tank dips being updated manually | 3.7 | Inventory physical dip of minimum two tanks taken | 1979 | VIJAYAWADA TERMINAL | Location to take up with M/S AST for completion of the TAS integration of the new Radar guages. | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137068 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137068 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137068 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137068 | AUD-2026-06-2000012864ACN-2026-06-4000137068 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Fire engine display rectified and working OK. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137076 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Fire engine panels display of operating parameters normal range not displayed | 6.2 |  | 1979 | VIJAYAWADA TERMINAL | Fire engine panels display of operating parameters normal range to be displayed | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012864ACN-2026-06-4000137076 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137076 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137076 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137076 | AUD-2026-06-2000012864ACN-2026-06-4000137076 | 21 | 21 | 27 | 80 | 12 | 12 | 44 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Fire engine display rectified and working OK. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123599 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | Fire engine panels display of operating parameters normal range not displayed | 6.4 |  | 1979 | VIJAYAWADA TERMINAL | operating parameters normal range to be displayed | SOD | Marketing | SCR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-03-2000011121ACN-2026-03-4000123599 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123599 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123599 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123599 | AUD-2026-03-2000011121ACN-2026-03-4000123599 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 53
SALADI SRINIVASU | 2026-09-04 | LOMESH KUMAR PATRE | 2026-07-31 | Location is having 930KWp Solar in VVSPL area & 130KWp in terminal roof tops, combined location capacity is 1060 KWp.As per laest AP govt circular, Industries operating at 33KV shall have maximum of 1000KWp solar instalaltion. Hence shifting 55KWpsolar from Suryapet terminal is not feasible. | AUDIT UPLOAD IN SAP | 2026-06-04 20:00 | AUD-2026-06-2000012864 | 2026-06-04 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137079 | Closed | LOMESH KUMAR PATRE | 2026-07-31 | 55KW roof top solar to be shifted to Vjw Terminal from Suryapet terminal | 6.6 |  | 1979 | VIJAYAWADA TERMINAL | 55KW roof top solar to be shifted to Vjw Terminal from Suryapet terminal | SOD | Marketing | SCR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012864ACN-2026-06-4000137079 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012864ACN-2026-06-4000137079 | 2026-08-21 16:00 | 59.0872 | 368 | >20 | AUD-2026-06-2000012864 - ACN-2026-06-4000137079 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012864ACN-2026-06-4000137079 | AUD-2026-06-2000012864ACN-2026-06-4000137079 | 21 | 21 | 27 | 80 | 12 | 12 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-31 | CCTV all 24 Cameras active with VA in relevant cameras. VA alerts are getting generated. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126314 | Closed | SUNITA | 2026-08-31 | CISF issues pertaining to non operation of both gates, CCTV yet to be active with VA. | 1.3 | Pending issues reviewed | 1554 | MR-II TERMINAL | To follow up with vendor to complete the commissioning. | SOD | Marketing | WZ | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 3 | ASSET INTEGRITY | S1 | F3 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126314 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126314 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126314 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126314 | AUD-2026-04-2000011147ACN-2026-04-4000126314 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | Shed constructed for Emergency Fire Trolley. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146651 | Closed | SHINDE ANAND LAXMAN | 2026-09-04 | YES. In Feb 2026. Location to provide shed for Fire Emergency Trolley | 2.1 | Fire drill conducted in last 6 months (surprise) | 1554 | MR-II TERMINAL | Shed to be provided for trolley | SOD | Marketing | WZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146651 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146651 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146651 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146651 | AUD-2026-07-2000016409ACN-2026-07-4000146651 | 21 | 21 | 27 | 80 | 6 | 5 | 48 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | Monitoring format is modified to include time for which camera is observed. Also 4 camera rotating view is set for with 10 secondsrotation for ease of monitoring | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146653 | Closed | SUNITA | 2026-08-10 | CCTV working. PTZ cameras need to set in rotating tour setting. Also View seqeuence to be set for having multiple views in one after another | 2.6 | CCTV functioning checked | 1554 | MR-II TERMINAL | View setting to be done. Monitoring format to include time of observation | SOD | Marketing | WZ | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146653 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146653 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146653 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146653 | AUD-2026-07-2000016409ACN-2026-07-4000146653 | 21 | 21 | 27 | 80 | 6 | 5 | 48 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | CCTV works completed. all 24 cameras are operationized. Display is made available in LIC cabin, Control room and Planning office | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126317 | Closed | SUNITA | 2026-08-10 | 8 cameras functional. SAT pending from 24 Cameras. VA not active | 2.6 | CCTV functioning checked | 1554 | MR-II TERMINAL | CCTV project closure to be expedited | SOD | Marketing | WZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 2 | ASSET INTEGRITY | S1 | F2 | 2026-03-31 | AUD-2026-04-2000011147ACN-2026-04-4000126317 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126317 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126317 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126317 | AUD-2026-04-2000011147ACN-2026-04-4000126317 | 21 | 21 | 26 | 80 | 6 | 5 | 31 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-09-02 | New earth pits made for High masts and tank farms. Total 16 new pits made. All pits resistance below 2 ohms as per Checking Report dt July 2026 | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126322 | Closed | SUNITA | 2026-09-02 | Earth grid layout to be updated, High value pits to be rectified | 3.16 | Earth pits / boundary / vegetation control checked | 1554 | MR-II TERMINAL | Location to rectify | SOD | Marketing | WZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-04-2000011147ACN-2026-04-4000126322 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126322 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126322 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126322 | AUD-2026-04-2000011147ACN-2026-04-4000126322 | 21 | 21 | 26 | 80 | 6 | 5 | 44 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-31 | All Recommendations of MDSA 2023-24 are closed suitably as per location conditions where in MR is reponsible for certain activitiesas MR-II Terminal is located with Mumbai refinery-II | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126324 | Closed | SUNITA | 2026-08-31 | 18 points pending compliance | 3.18 | OISD/MDSA/SSA compliance reviewed | 1554 | MR-II TERMINAL | Location to expedite compliances | SOD | Marketing | WZ | 2026-05-31 | POOR PLANNING OR RISK ASSESSMENT | 2 | PROCESS SAFETY | S1 | F2 | 2026-05-31 | AUD-2026-04-2000011147ACN-2026-04-4000126324 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126324 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126324 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126324 | AUD-2026-04-2000011147ACN-2026-04-4000126324 | 21 | 21 | 26 | 80 | 6 | 5 | 39 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-31 | Transporter meet are organized every quarter. Record of last three meetings are attached. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146661 | Closed | SUNITA | 2026-08-31 | No transporter meeting done in Q1. Location to organise | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1554 | MR-II TERMINAL | Location to ensure one transporter meet per quarter | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146661 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146661 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146661 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146661 | AUD-2026-07-2000016409ACN-2026-07-4000146661 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-09-02 | Contract of Ram Nagar and Kochi has ended in July 1st week. Hence Location is not supplying to Ram Nagar and Kochi Terminal anymore. Hence point is not applicable now. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146656 | Closed | SUNITA | 2026-09-02 | YES, Location has issued letters. Night driving still regular for Kochi terminal and Ram Nagar Lubes | 3.3 | VTS deviations reviewed | 1554 | MR-II TERMINAL | Location to take MOC approval or modify routes for these two locations | SOD | Marketing | WZ | 2026-08-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-30 | AUD-2026-07-2000016409ACN-2026-07-4000146656 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146656 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146656 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146656 | AUD-2026-07-2000016409ACN-2026-07-4000146656 | 21 | 21 | 27 | 80 | 6 | 5 | 52 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-26 | Closure done for projects all physical works. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146663 | Closed | SUNITA | 2026-08-26 | RCC Road project in Progress, LPS work in progress, CCTV and TAS project are comleted by location in H1 | 4.3 | Project progress reviewed | 1554 | MR-II TERMINAL | Location to close the ARs ASAP | SOD | Marketing | WZ | 2026-07-31 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-07-31 | AUD-2026-07-2000016409ACN-2026-07-4000146663 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146663 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146663 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146663 | AUD-2026-07-2000016409ACN-2026-07-4000146663 | 21 | 21 | 27 | 80 | 6 | 5 | 48 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-31 | RCC Road , LPS works, TAS standardization and CCTV projects completed. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000126326 | Closed | SUNITA | 2026-08-31 | RCC Road project in Progress, LPS work in progress, CCTV and TAS project is delayed | 4.3 | Project progress reviewed | 1554 | MR-II TERMINAL | Location to ensure Clsoure within timelines | SOD | Marketing | WZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 2 | ASSET INTEGRITY | S1 | F2 | 2026-03-31 | AUD-2026-04-2000011147ACN-2026-04-4000126326 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126326 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126326 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126326 | AUD-2026-04-2000011147ACN-2026-04-4000126326 | 21 | 21 | 26 | 80 | 6 | 5 | 31 | 53
|  |  |  | Work in progress with Tender due date - 24-09-26 and technical eval has been completed. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150978 | Open | FOUZDAR RISHABH | 2026-09-28 |  | 1.3 | Pending issues reviewed | 1155 | ROORKEE DEPOT | OISD pending points , Bay extension job PO placement | SOD | Marketing | NUZ | 2026-12-30 |  | 4 |  | S4 | F1 | 2026-12-30 | AUD-2026-09-2000016863ACN-2026-09-4000150978 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150978 | 2026-09-03 | 46.7538 | 485 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150978 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016863ACN-2026-09-4000150978 |  | AUD-2026-09-2000016863ACN-2026-09-4000150978 | 21 |  | 27 | 80 | 2 | 2 | 70
|  |  |  | presentation has been prepared, date to be finalised for presentation to be given. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150981 | Open | FOUZDAR RISHABH | 2026-09-28 | To focus on the individual area along with stringet monitoring and applicable clauses, over and above depot regular duties. | 1.6 | Expectations clearly communicated to officers | 1155 | ROORKEE DEPOT | All officers (1+4+E0+contract engineer+GAT) available at depot to redistribute the work among themselves and to focus more on TT inspections, TT gaurdian, Novex,VTS and TAS issues. Each officer to obtain/gain expertise in one subject to give presentation to all zone locations | SOD | Marketing | NUZ | 2026-09-15 |  | 2 |  | S2 | F1 | 2026-09-15 | AUD-2026-09-2000016863ACN-2026-09-4000150981 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150981 | 2026-09-03 | 46.7538 | 379 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150981 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016863ACN-2026-09-4000150981 |  | AUD-2026-09-2000016863ACN-2026-09-4000150981 | 21 |  | 27 | 80 | 2 | 2 | 55
|  |  |  | "1. Ros have been identified and data has been sent to zone for IMM forecasting 2. Valve box inspection tand its compliance is underway 3. TT guardian is strictly monitored and investigation and action taken on identified spots is underway" | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150982 | Open | FOUZDAR RISHABH | 2026-09-28 | 1. Catering of additional outlets from location. 2. Valve box inspection is lacking 3. Investigation and action has been taken onsome spots identified by TT Guardian. | 1.8 | Improvement plans discussed | 1155 | ROORKEE DEPOT | 1. To identify ROs which can be fed by both Sitarganj and Roorkee and to cordinate among each other to prevent dryouts and ullage situations. 2. Valve box inspection to be completed in 1 month, and compliance with norms to be done in 3 months 3. TT guardian to be strictly monitored and investigation and action to be taken on identified spots | SOD | Marketing | NUZ | 2026-12-03 |  | 2 |  | S2 | F1 | 2026-12-03 | AUD-2026-09-2000016863ACN-2026-09-4000150982 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150982 | 2026-09-03 | 46.7538 | 458 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150982 | 532 | 8294 | 21 | 8294 | -44 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016863ACN-2026-09-4000150982 |  | AUD-2026-09-2000016863ACN-2026-09-4000150982 | 21 |  | 27 | 80 | 2 | 2 | 66
|  |  |  | Foam valve is being procured from Madurai and shall be installed on the lines | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150988 | Open | FOUZDAR RISHABH | 2026-09-28 | Worker operated monitors, near TK-9 and operated foam pourer, sprinkler, MEFG of TK-11. Foam and operation found to be adequate | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1155 | ROORKEE DEPOT | Drain valve to be provided to the vertical line going to all foam pourer. | SOD | Marketing | NUZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150988 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150988 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150988 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016863ACN-2026-09-4000150988 |  | AUD-2026-09-2000016863ACN-2026-09-4000150988 | 21 |  | 27 | 80 | 2 | 2 | 57
|  |  |  | Taken up with HQO distribution regarding this issue | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151203 | Open | FOUZDAR RISHABH | 2026-09-28 | 1. To either handover SKO dispatch to IOC or find a way to connect the PLT line to tanks | 6.4 | SKO dispatch | 1155 | ROORKEE DEPOT | 1. To either handover SKO dispatch to IOC or find a way to connect the PLT line to tanks | SOD | Marketing | NUZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000016863ACN-2026-09-4000151203 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000151203 | 2026-09-03 | 46.7538 | 425 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000151203 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016863ACN-2026-09-4000151203 |  | AUD-2026-09-2000016863ACN-2026-09-4000151203 | 21 |  | 27 | 80 | 2 | 2 | 61
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-09-02 | FLP audio Visual hooters are procured and installed for HCDs. Electrical siren instaled for ESD. Documents attached. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-07-4000146664 | Closed | SUNITA | 2026-09-02 | Field Hooters not availble for HCD/ESD. | 5.2 | Functioning of all Hooters in control room | 1554 | MR-II TERMINAL | Location to take NPCB | SOD | Marketing | WZ | 2026-12-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S2 | F2 | 2026-12-30 | AUD-2026-07-2000016409ACN-2026-07-4000146664 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146664 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146664 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146664 | AUD-2026-07-2000016409ACN-2026-07-4000146664 | 21 | 21 | 27 | 80 | 6 | 5 | 70 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-09-02 | ESDs are integrated with siren. Hooter are procured and installed for HCDs. Procuremnet gate pass and installation report attached. ESD and siren checked quarterly and working fine as per Q1 testing report. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-04-4000126327 | Closed | SUNITA | 2026-09-02 | Field Hooters not availble for HCD/ESD and Dyke drains | 5.2 | Functioning of all Hooters in control room | 1554 | MR-II TERMINAL | Location to take NPCB | SOD | Marketing | WZ | 2026-12-30 | POOR PLANNING OR RISK ASSESSMENT | 2 | ASSET INTEGRITY | S1 | F2 | 2026-12-30 | AUD-2026-04-2000011147ACN-2026-04-4000126327 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126327 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126327 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126327 | AUD-2026-04-2000011147ACN-2026-04-4000126327 | 21 | 21 | 26 | 80 | 6 | 5 | 70 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | CISF is under control of Mumbai refinery HR department. Location has written to HR departmnet Mumbai refinery vide emails dt 10.04.2026 reminder are sent vide email dt 10.08.2026,09.06.2026,03.06.2026,02.06.202628.05.2026,22.04.026 Email communication trailattached. Continuous follow up is being maintained on the matter/ | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146666 | Closed | SUNITA | 2026-08-10 | CISF does not do outside boundary patroling. Location has taken up with Head security MR | 6.2 | CISF still does not do outside boundary patroling | 1554 | MR-II TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146666 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146666 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146666 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146666 | AUD-2026-07-2000016409ACN-2026-07-4000146666 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-31 | Location has taken up with DGM Security HR vide a series of communications. The latest communication dt | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000126329 | Closed | SUNITA | 2026-08-31 | CISF does not do outside boundary patroling | 6.2 | CISF does not do outside boundary patroling | 1554 | MR-II TERMINAL | Location to take with MR Security head | SOD | Marketing | WZ | 2026-04-30 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126329 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126329 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126329 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126329 | AUD-2026-04-2000011147ACN-2026-04-4000126329 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | CISF is under control of Mumbai refinery HR department. Location has written to HR departmnet Mumbai refinery vide emails dt 10.04.2026 reminder are sent vide email dt 10.08.2026,09.06.2026,03.06.2026,02.06.202628.05.2026,22.04.026 Email communication trailattached. Continuous follow up is being maintained on the matter. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146667 | Closed | SUNITA | 2026-08-10 | CISF Does not do inside night patroling. Location has taken up with head security MR | 6.3 | CISF still Does not do inside night patroling | 1554 | MR-II TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146667 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146667 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146667 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146667 | AUD-2026-07-2000016409ACN-2026-07-4000146667 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | CISF is under control of Mumbai refinery HR department. Location has written to HR departmnet Mumbai refinery vide emails dt 10.04.2026 reminder are sent vide email dt 10.08.2026,09.06.2026,03.06.2026,02.06.202628.05.2026,22.04.026 Email communication trailattached. Continuous follow up is being maintained on the matter/ | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000126330 | Closed | SUNITA | 2026-08-10 | CISF Does not do inside night patroling | 6.3 | CISF Does not do inside night patroling | 1554 | MR-II TERMINAL | Location to take with MR Security head | SOD | Marketing | WZ | 2026-04-30 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126330 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126330 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126330 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126330 | AUD-2026-04-2000011147ACN-2026-04-4000126330 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-10 | CISF is under control of Mumbai refinery HR department. Location has written to HR departmnet Mumbai refinery vide emails dt 10.04.2026 reminder are sent vide email dt 10.08.2026,09.06.2026,03.06.2026,02.06.202628.05.2026,22.04.026 Email communication trailattached. Continuous follow up is being maintained on the matter. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000126331 | Closed | SUNITA | 2026-08-10 | CISF does not do check vehile satnding outside gates leading to blockage of emergency gates | 6.4 | CISF does not do check vehile standing outside gates leading to blockage of emergency gates | 1554 | MR-II TERMINAL | Location to take with MR Security head | SOD | Marketing | WZ | 2026-04-30 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126331 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126331 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126331 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126331 | AUD-2026-04-2000011147ACN-2026-04-4000126331 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 53
SHINDE ANAND LAXMAN | 2026-09-04 | SUNITA | 2026-08-26 | Rigrous follow up is maintained with HR Security and CISF for Keeping vigil. Latest communication 26.08.2026 attached. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146668 | Closed | SUNITA | 2026-08-26 | CISF does not do check vehile satnding outside gates leading to blockage of emergency gates. Location has informed head security MR | 6.4 | CISF still does not do check vehile satnding outside gates leading to blockage of emergency gates | 1554 | MR-II TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146668 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146668 | 2026-10-16 | 3.7538 | 368 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146668 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146668 | AUD-2026-07-2000016409ACN-2026-07-4000146668 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 53
|  | CHANGMAI RAHUL | 2026-09-04 | approved LPR shared to Zonal CPO.GEM retender is to be done and expected to complete within 3 months from issuance of PO | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000136985 | Completed | CHANGMAI RAHUL | 2026-09-04 | ERDMP certification pending under SSA | 1.4 | Earlier action points status checked | 1708 | DIMAPUR DEPOT | ERDMP certification for the location to be completed | SOD | Marketing | GZR | 2026-06-20 |  | 1 |  | S1 | F1 | 2026-06-20 | AUD-2026-06-2000012955ACN-2026-06-4000136985 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136985 | 2026-09-12 | 37.7538 | 292 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136985 | 532 | 8294 | 21 | 8294 | 121 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136985 |  | AUD-2026-06-2000012955ACN-2026-06-4000136985 | 21 |  | 27 | 80 | 7 | 7 | 42
|  | CHANGMAI RAHUL | 2026-09-04 | Lux meter is under calibration through Guwahati Vendor. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000136989 | Completed | CHANGMAI RAHUL | 2026-09-04 | Lux level couldnot be checked due to unavailibility of calibrated Lux meter. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1708 | DIMAPUR DEPOT | Lux level check to be done throughly and record to be maintained. | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000136989 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000136989 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000136989 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000136989 |  | AUD-2026-06-2000012955ACN-2026-06-4000136989 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-09-04 | 1. GEM tender placed in standalone PO and L1 party selected for VHF supply , budget to be sought 2. ERDMP GeM tender initiated andapplied for Prohibited area in both DC office and factory office | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137151 | Completed | CHANGMAI RAHUL | 2026-09-04 | Compliance status reviewed . OISD PCSA complied except the VHF procurement.2 SSA compliance pending (ERDMP certification and Prohibited area declearation) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1708 | DIMAPUR DEPOT | All pending point to be complied | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000137151 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137151 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137151 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137151 |  | AUD-2026-06-2000012955ACN-2026-06-4000137151 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-09-04 | Acid resistance paint ordered and painting shall be completed as soon as material is received | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137155 | Completed | CHANGMAI RAHUL | 2026-09-04 | Required paiting at Battery room not available | 6.2 | Battery room of control room | 1708 | DIMAPUR DEPOT | Battery room acid resistance painting required | SOD | Marketing | GZR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-06-2000012955ACN-2026-06-4000137155 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137155 | 2026-09-12 | 37.7538 | 302 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137155 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137155 |  | AUD-2026-06-2000012955ACN-2026-06-4000137155 | 21 |  | 27 | 80 | 7 | 7 | 44
|  | CHANGMAI RAHUL | 2026-09-04 | Scrap segregated. Many pipes and cables are being used during maintenance activities. Governement approved valuer communicated for valuation. | SENIOR MANAGEMENT INSPECTION_DIMAPUR | 2026-05-12 | AUD-2026-06-2000012955 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000137154 | Completed | CHANGMAI RAHUL | 2026-09-04 | Scrap need to be identified and disposed off. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1708 | DIMAPUR DEPOT | RFD to be made | SOD | Marketing | GZR | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000012955ACN-2026-06-4000137154 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012955ACN-2026-06-4000137154 | 2026-09-12 | 37.7538 | 332 | >20 | AUD-2026-06-2000012955 - ACN-2026-06-4000137154 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012955ACN-2026-06-4000137154 |  | AUD-2026-06-2000012955ACN-2026-06-4000137154 | 21 |  | 27 | 80 | 7 | 7 | 48
|  |  |  | 2. Fencing utilised for Fencing of 810kVA DG Set | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151075 | Open | SHETTY ANURANJAN | 2026-09-30 | Following points are still not complied: 1. One ESD at TT gantry area is to be shifted behind tank farm. 3 ESDs are more than sufficient at TT gantry area. 2. Fencing utilization in TT parking area is still not done. 3. Meeting with MARG members in presence ofSr. Police Officials not done for year 2026-27. This can be treated as Security Coordination Committee meeting. Factory Inspector should also be invited along with other statutory authorities. 4. MS transmix sent to HMEL from Apr to July 2026 is 6172 Kl. During the same period in year 2025, it was 8379 Kl. Location should put their effort to reduce transportation of MS transmix to HMEL. | 1.4 | Earlier action points status checked | 1242 | JAIPUR TERMINAL | Point no. 1, 2, 3 are to be complied. Point no. 4: Location should put effort to reduce transmix despatch to HMEL. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151075 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151075 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151075 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151075 |  | AUD-2026-09-2000016770ACN-2026-09-4000151075 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151076 | Open |  |  | Structural training of Mr. Anuranjan Shetty and two new joinees to be ensured on HSE and Depot related activities. Live fire drill of these officers to be ensured. | 1.8 | Improvement plans discussed | 1242 | JAIPUR TERMINAL | Location to discuss with Zonal HSE officer for structured training identified for Mr. anuranjan and two new officers (one already joined, one will be joining this month in Sept 26) | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151076 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151076 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151076 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151076 |  | AUD-2026-09-2000016770ACN-2026-09-4000151076 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151078 | Open |  |  | CCTV display screen at security room is not in proper working condition since Feb 2026. This is not acceptable. To be repaired on immediate basis. TAS screen is also not in working condition. Pls do not wait for AR. Replace the screen ithe same is not repairable. CCTV checking report should be communicated to undersign at least once in fortnight. | 2.6 | CCTV functioning checked | 1242 | JAIPUR TERMINAL | A. CCTV screen at security room to be repaired, UPS to be replaced if required. B. TAS screen to be replaced/repaired. C. CCTV checking report should be communicated to undersign at least once in fortnight. | SOD | Marketing | NWF | 2026-10-31 |  | 16 |  | S4 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151078 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151078 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151078 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | HIGH | AUD-2026-09-2000016770ACN-2026-09-4000151078 |  | AUD-2026-09-2000016770ACN-2026-09-4000151078 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151080 | Open |  |  | Foam bladder tank is found 1/4 full. It needs to be topped up at least half. | 2.9 | Foam inventory verified | 1242 | JAIPUR TERMINAL | Pls top up foam tanks with required level as early as possible. | SOD | Marketing | NWF | 2026-10-31 |  | 12 |  | S3 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151080 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151080 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151080 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151080 |  | AUD-2026-09-2000016770ACN-2026-09-4000151080 | 21 |  | 27 | 80 | 0 | 0 | 61
|  |  |  | a. RSFPS of Tk-9 functioning properly | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151081 | Open | SHETTY ANURANJAN | 2026-09-30 | a) RSFPS of TK9 was checked for operation. It disn't work from control rom. However, it was actuated by pressing pushbutton near tank. There is communication failure from contriol room to push button. Pls note that RSFPS is in CAMC and we are paying handsome amount to vendor. These conditions are not desirable. b) NRV of water draw off line is installed in wrong direction in TK-9. It is okayin all other tanks checked by me. c) HCD-02 didn't work for 20% LEL. However, it worked in 40% LEL. d) Checked foam pourer of TK-9 and TK-11. It worked well. Checked HVLR-5 and 6. It worked well. Checked Dyke Valve Position Indicator, DVPI-1. It worked well. e) DVPI-3 is having non standard falnge. To be replaced with correct spec of flange for product line. Local hooter didn't work by opening DVPI-3. It gave signal in control room. f) It is suggested to install water cum foam monitor in ETP area. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1242 | JAIPUR TERMINAL | a. RSFPS of Tk-9 to be corrected b. NRV direction to be changed. C. HCD-02 to be corrected e. DVPI-3 flange to be changed. Localhooter to be work. F) One water cum foam monitor at ETP area | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151081 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151081 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151081 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151081 |  | AUD-2026-09-2000016770ACN-2026-09-4000151081 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151082 | Open |  |  | Branding of TT no. RJ14GL9884, RJ18GB4711 are not good. To be done again. RJ29GL5853 branding is very poor. Pls stop loading of this TT and send the same for painting and branding. | 3.1 | TT fittings & discipline checked | 1242 | JAIPUR TERMINAL | Branding of all Tts to be verified and corrected. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151082 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151082 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151082 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151082 |  | AUD-2026-09-2000016770ACN-2026-09-4000151082 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151084 | Open |  |  | A) There was study of PM checks by AOT in July/August 2026 for all TTs. Pls share the report observed. Location should see that VTSdoes not get faulty due to issue attributable to AOT. If it is still there, location should ensure the followings: 1) Get in writing clearly from AOT representative that VTS became faulty because of issue at their end and the same is not attribuatble to AOT. 2)Keep scan copies of these report by representative signed by HPCL as well as AOT. 3) Issue letter to AOT with these scan copies B) There is distance of at least 4 km between Jaipur Tml and main highway. Some of the loaded Tts were found stopping before highway (that is in the area of 4 km surrounding jaipur tml). It is observed that there are some suspected activities going on. Location needs to ensure the followings: 1. Do not allow loaded TT to stop within distance of 4 km from Jaipur Tml. If they are stopping, give letter to DCT/transporter. If they are still stopping, take action. 2. Check 5 loaded Tts (preferably transport TT, TTs which areblocking etc) every day in VTS portal, once it leaves Terminal. Share the report with Zone/LIC. Complete all transport Tts. | 3.3 | VTS deviations reviewed | 1242 | JAIPUR TERMINAL | A) Pls share PM check report of AOT with your observations. Take all measures as mentioned in my observations for repeated VTS issue by AOT. B) 1) Do not allow loaded TT to stop within distance of 4 km from Jaipur Tml. If they are stopping, give letter to DCT/transporter. If they are still stopping, take action. 2. Check 5 loaded Tts (preferably transport TT, TTs which are blocking etc) every day in VTS portal, once it leaves Terminal. Share the report with Zone/LIC. Complete all transport Tts | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151084 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151084 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151084 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151084 |  | AUD-2026-09-2000016770ACN-2026-09-4000151084 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151085 | Open |  |  | Etahnol belending performance checked for two TTs. Sample drawn from top and bottom of tank trucks. It was verified for ethanol content. Ethanol content is 18% and 18.5% in top and bottom sample. Minimum requirement is 19% for E20. Location needs to verify the same. 1. RJ18GB4711, bay-5: Top sample: 18.54% ethanol, bottom sample: 18.54% ethanol 2. RJ26GA3007: Top sample: 18%, bottom: 18.5% ethanol | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1242 | JAIPUR TERMINAL | Ethanol blending% is less than 19% though ethanol injection is 20%. Pls cross check with AST and revert. You need to analyse the reason and revert for solution | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151085 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151085 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151085 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151085 |  | AUD-2026-09-2000016770ACN-2026-09-4000151085 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151087 | Open |  |  | Dips of all ethanol tanks were checked: Gross dip/Temp 1. TK14: TAS: 428.4/33.5, manual: 428.4/33.5, water nil 2. TK-10: TAS: 689.0/34, manual: 689.3/34.5, water nil 3. TS-4: TAS: 19.0/33.8, manual 19.3/34 4. TS-5: TAS: 171.3/34.3, Manual: 171.4/34 5. TS-6: TAS: 224.0/34.3, manual: 224.6/34 The Location In-charge shall share monthly data of: i) MS RON before PLT, ii) MS trans mix quantity blended (in %), iii) Final MS RON, and iv) Final FBP. Physical dip of Slop Tank TK-9 was checked during the visit. i) The physical total dip observed was 89.3 cm against the TAS dip of 89.1 cm. ii) Physical water dip was recorded as nil with slight traces, whereas the TAS water dip was recorded as nil | 3.7 | Inventory physical dip of minimum two tanks taken | 1242 | JAIPUR TERMINAL | A) Monthly data of MS RON, MS transmix blend %, final FBP, final MS RON to be shared. B) Slop tank to be emptied. Dip difference to be corrected | SOD | Marketing | NWF | 2027-03-31 |  | 10 |  | S2 | F5 | 2027-03-31 | AUD-2026-09-2000016770ACN-2026-09-4000151087 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151087 | 2026-09-30 | 19.7538 | 576 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151087 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151087 |  | AUD-2026-09-2000016770ACN-2026-09-4000151087 | 21 |  | 27 | 80 | 0 | 0 | 83
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151088 | Open |  |  | a. There were cases of abnormal loss/gain as reported by Vigilance Officer in their recent inspection in July 2026. Location was not maintaining PLT receipt loss/gain. However, during visit it was observed that location is maintaining PLT loss/gain report. It is okay. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise. b. Location should also carry out cycle count of material on monthly basis. c. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informedto Zone. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. | 3.9 | Abnormal variations / unused assets reviewed | 1242 | JAIPUR TERMINAL | a. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise. b. Location should also carry out cycle count of material on monthly basis. c. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informed toZone. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151088 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151088 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151088 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151088 |  | AUD-2026-09-2000016770ACN-2026-09-4000151088 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151090 | Open |  |  | a. Dyke-2 was not found clean. Dyke needs to be cleaned at least once in two months during rainy season. Otherwise, once in three months in other season. It should be free from vegetation. Grass observed in paver area. It needs to be cleaned. b. Drain in dyke -1 has not been cleaned for long period. c. There are huge no. of Soap, Floor Cleaner lying inside store. This pertains to Retail Department. Expiry of these materials is before March 2027. Location needs to make follow up for early liquidation of these materialsthrough retail department. d. PCC should be done in scrap yard. Presently, it was full of grass. e. 2 inch line near MDPL gate was found rusted. To be painted | 3.15 | Housekeeping & PPE usage checked | 1242 | JAIPUR TERMINAL | a, b) Make PMS schedule of housekeeping jobs and get the same signed by contractor. It is the responsibility of contractor to get the job done as per PMS schedule. It should be made like this. c) Follow up with Retail team for liquidation of soap, floor cleaner d) PCC in scrap yard e) Patch painting of 2 inch pipeline near MDPL gate | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151090 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151090 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151090 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151090 |  | AUD-2026-09-2000016770ACN-2026-09-4000151090 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151091 | Open |  |  | Checked earth pit no. 220. There is no resistance value mentioned on display board. This is behind transformer. Some of the earth pits were not having funnel. Earth strip was found rusted in EP no. 78. Gap observed between two earth strip in EP 80. Pls check all earth pits and do necessary maintenance in line with IS 3043. Vegetation observed in 4-pole structure. To be removed. | 3.16 | Earth pits / boundary / vegetation control checked | 1242 | JAIPUR TERMINAL | a) All earth pits to be checked and corrective action to be taken as per IS 3043 design and spec b) Vegetation to be removed from 4-pole structure area in presence of qualified electrician | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151091 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151091 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151091 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151091 |  | AUD-2026-09-2000016770ACN-2026-09-4000151091 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151092 | Open |  |  | Sr. management audit points of Q1 are yet to be complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1242 | JAIPUR TERMINAL | Sr. Management Inspection points to be complied. For any discussion, location should come forward | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151092 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151092 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151092 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151092 |  | AUD-2026-09-2000016770ACN-2026-09-4000151092 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151093 | Open |  |  | a. There are lot of new costly items inside store. I observed MOV of 10 inch, ROSOV of 10 and 14, 3 nos. UG submergible pump, many Al. sample containers, new 4 ball valves, 4 nos. of 6 valve, two boxes filled with unidentified materials, bettery etc. Location M&Iofficer was given time for 3 months to identify all materials inside store. Make a list in excel. Identify all disposable materialsand usable materials separately and get RFD approved for disposable materials. B. There should be one register at TT gantry. This register should have entries of all issues at TT gantry. It may be related to maintenance, electrical issue, operational issue. Thismay be filled by contract staff in their language. TAS officer and M&I officer to review this register on weekly basis and LIC to review this register on monthly basis for compliance of job identified by gantry workman/officer C. Cable gland is found oversize and few are not flameproof in UG tank farm. D. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. E. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1242 | JAIPUR TERMINAL | a) Segregation of usable and disposable materials inside store. Make inventory of usable material in excel sheet. Inform Zone. MakeRFD for all scrappable materials seen inside store and scrap yard. B) One register at TT gantry to be maintained. This register should have entries of all issues at TT gantry. It may be related to maintenance, electrical issue, operational issue. This may be filled by contract staff in their language. TAS officer and M&I officer to review this register on weekly basis and LIC to review this register on monthly basis for compliance of job identified by gantry workman/officer. Cable gland is found oversize and few are notflameproof in UG tank farm. D. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is nohole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions.Records should be maintained. E. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151093 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151093 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151093 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151093 |  | AUD-2026-09-2000016770ACN-2026-09-4000151093 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151094 | Open |  |  | TK-9 was found rusted from inside. Pls carry out painting of inside part. It is okay from outside. Locations have carry out patch painting at wind girder area from outside in 4 tanks. This is good and appreciable. Suitable canopy covers shall be provided over the ROSOV and MOVs installed on the AG tank manifold to protect them from adverse weather conditions and bird droppings. | 4.2 | Maintenance activities reviewed | 1242 | JAIPUR TERMINAL | TK-9 was found rusted from inside. Pls carry out painting of inside part. It is okay from outside. Locations have carry out patch painting at wind girder area from outside in 4 tanks. This is good and appreciable. Suitable canopy covers shall be provided over the ROSOV and MOVs installed on the AG tank manifold to protect them from adverse weather conditions and bird droppings. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151094 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151094 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151094 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151094 |  | AUD-2026-09-2000016770ACN-2026-09-4000151094 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151095 | Open |  |  | Loation needs to interchange TK11 and TK15. TK15 to be used for gasohol and TK11 is to be used for HSD. This was informed in June 2026. Location has sent tender to CPO. It is yet to be floated. The existing pumping capacity is 72 KL/hr. For a maximum flow rate of 450 KL/hr, an ethanol pump of 90 KL/hr capacity is required. The adequacy of the existing pipeline size shall be checked by the location. | 4.3 | Project progress reviewed | 1242 | JAIPUR TERMINAL | Loation needs to interchange TK11 and TK15. TK15 to be used for gasohol and TK11 is to be used for HSD. This was informed in June 2026. Location has sent tender to CPO. It is yet to be floated. The existing pumping capacity is 72 KL/hr. For a maximum flow rate of 450 KL/hr, an ethanol pump of 90 KL/hr capacity is required. The adequacy of the existing pipeline size shall be checked by the location. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151095 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151095 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151095 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151095 |  | AUD-2026-09-2000016770ACN-2026-09-4000151095 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151096 | Open |  |  | a. Cathodic Protection display is not in working condition. b. Ethanol VFD is not in working condition. To be brought in operation. C. VRU is not functional. To be repaired. Location informed that vendor is scheduled to visit on 1st Sept 2026. | 4.4 | Quality of PM compliance reviewed | 1242 | JAIPUR TERMINAL | a. Cathodic Protection display is not in working condition. b. Ethanol VFD is not in working condition. To be brought in operation. C. VRU is not functional. To be repaired. Location informed that vendor is scheduled to visit on 1st Sept 2026. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151096 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151096 | 2026-09-30 | 19.7538 | 455 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151096 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151096 |  | AUD-2026-09-2000016770ACN-2026-09-4000151096 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151097 | Open |  |  | Fire engine no. 1 is having starting truble. Pls attend it on priority. You may go for D-check of this fire engine, if OEM suggest.Pls submit Budget proposal online. Fire engine display is not working in FE-2, FE-3. FE-5 is still under repair. Pls bring FE-5 in working condition as early as possible. Fire engines were not found in clean condition. It needs to be cleaned at least once in a month. Platform of Fire engines were found rusted. Needs to be painted. | 6.1 | Fire engine | 1242 | JAIPUR TERMINAL | Fire engine no. 1 is having starting truble. Pls attend it on priority. You may go for D-check of this fire engine, if OEM suggest.Pls submit Budget proposal online. Fire engine display is not working in FE-2, FE-3. FE-5 is still under repair. Pls bring FE-5 in working condition as early as possible. Fire engines were not found in clean condition. It needs to be cleaned at least once in a month. Platform of Fire engines were found rusted. Needs to be painted. | SOD | Marketing | NWF | 2026-09-30 |  | 12 |  | S3 | F4 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151097 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151097 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151097 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151097 |  | AUD-2026-09-2000016770ACN-2026-09-4000151097 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151098 | Open |  |  | 10 MOVs are not communicating. It is again long pending issue which needs to be resolved by location. | 6.3 | mov repair and communication | 1242 | JAIPUR TERMINAL | 10 MOVs are not communicating. It is again long pending issue which needs to be resolved by location. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151098 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151098 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151098 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151098 |  | AUD-2026-09-2000016770ACN-2026-09-4000151098 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151099 | Open |  |  | History card was not found updated for costly equipment like CAMC of RSFPS, Fire engine, HVLR, Pumps, Tank etc. Location should update all visit details in History card. If any parts are replaced (even if cost is not borne by HPCL), pls mention that in history card. | 6.4 | History card | 1242 | JAIPUR TERMINAL | Pls update all details including visit of OEM, any servicing done, any filter changed. Even if material changed is under the scope of CAMC vendor, pls write name of material changed and associated cost | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151099 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151099 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151099 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151099 |  | AUD-2026-09-2000016770ACN-2026-09-4000151099 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151301 | Open |  |  | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. It is advised tomonitor diesel consumption in fire engine and DG. Location can maintain monthly record as per the followings: i) Opening physical inv of HSD in DG tanks; ii) HSD given to DG tank in that month: iii) No. of hrs run by individual DG in zero load, no. of hrs run by individual DG in full load iv) Diesel consumption per hr as communicated by OEM for individual DG in no load and full load respectively. v) HSD consumed theoritically vi) Closing book stock of HSd in DG tank vii) Physical closing stock of HSD in DG tank pls make monthly record of HSD consumption for DG and fire engines. This will keep contriol on own use | 6.6 | Additive stock monitoring | 1242 | JAIPUR TERMINAL | a) Monthly monitoring of inventory of additive stock. Records to be maintained. B) Diesel consumption record on monthly basis. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151301 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151301 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151301 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151301 |  | AUD-2026-09-2000016770ACN-2026-09-4000151301 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151302 | Open |  |  | To be implemented for all toll plaza. | 6.7 | Discounted toll | 1242 | JAIPUR TERMINAL | To be implemented for all toll plaza. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151302 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151302 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151302 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151302 |  | AUD-2026-09-2000016770ACN-2026-09-4000151302 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151303 | Open |  |  | Old Lubes are required to be liquidated | 6.8 | Liquidation of slow moving Lube | 1242 | JAIPUR TERMINAL | Old Lubes are required to be liquidated | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151303 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151303 | 2026-09-30 | 19.7538 | 425 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151303 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151303 |  | AUD-2026-09-2000016770ACN-2026-09-4000151303 | 21 |  | 27 | 80 | 0 | 0 | 61
CHANDRAKANTH JOSHI | 2026-09-05 | ROY TAVARES | 2026-09-05 | Tank 4 repair completed | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122842 | Closed | ROY TAVARES | 2026-09-05 | OISD - Zero, MDSA 24-25 7 /33 pending, 25-26 8/59 pending, SSA 11/67 pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1797 | GULBARGA NEW IRD | LPS point of tank TK4 to be attended by checking . New system for Al dome to be devised | SOD | Marketing | SWZ | 2026-03-20 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-20 | AUD-2026-03-2000010764ACN-2026-03-4000122842 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122842 | 2026-08-19 18:00 | 61.0038 | 369 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122842 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122842 | AUD-2026-03-2000010764ACN-2026-03-4000122842 | 21 | 21 | 26 | 80 | 5 | 5 | 29 | 53
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151574 | Open |  |  | Lux levels checked - PPH- 180, 104 , 3 lights to be replaced , road in front of PPH - 2 , street lights not working, TK 2B manifold- 62, 82, TK 2A manifold 60,65, Control room - 410, admin - 210 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1979 | VIJAYAWADA TERMINAL | Lux levels to be improved at roads | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017501ACN-2026-09-4000151574 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151574 | 2026-08-21 16:00 | 59.0872 | 425 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151574 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151574 |  | AUD-2026-09-2000017501ACN-2026-09-4000151574 | 21 |  | 27 | 80 | 12 | 12 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151575 | Open |  |  | The Emergency Response Toolkit Trolley was inspected. SCABA set not available , only spare cylinder available | 2.5 | Emergency response preparedness reviewed | 1979 | VIJAYAWADA TERMINAL | To take corrective action for emergency trolley availability with all the required items. | SOD | Marketing | SCR | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017501ACN-2026-09-4000151575 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151575 | 2026-08-21 16:00 | 59.0872 | 364 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151575 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151575 |  | AUD-2026-09-2000017501ACN-2026-09-4000151575 | 21 |  | 27 | 80 | 12 | 12 | 52
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151576 | Open |  |  | CCTV functioning checked. Out of 65 CCTV cameras , 61 are working. One camera sent for repair. 3 cameras OFC cable issue being rectified. | 2.6 | CCTV functioning checked | 1979 | VIJAYAWADA TERMINAL | All the non Functional CCTV cameras to be rectified . | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151576 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151576 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151576 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151576 |  | AUD-2026-09-2000017501ACN-2026-09-4000151576 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151577 | Open |  |  | HVLR no. 11, TK-1B open path, TK-1C open path , and TT Pump House Open-Type HCD were operated and found to be functioning satisfactorily. TK1B Rim seal functioning checked , unit no. 1 did not operate in remote and operated manually. AMC vendor rectified immediately and same opertaed in remote. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1979 | VIJAYAWADA TERMINAL | To ensure rim seal proper functioning in remote at all times. | SOD | Marketing | SCR | 2026-08-22 |  | 5 |  | S1 | F5 | 2026-08-22 | AUD-2026-09-2000017501ACN-2026-09-4000151577 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151577 | 2026-08-21 16:00 | 59.0872 | 355 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151577 | 532 | 8294 | 21 | 8294 | 58 | 60 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151577 |  | AUD-2026-09-2000017501ACN-2026-09-4000151577 | 21 |  | 27 | 80 | 12 | 12 | 51
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151578 | Open |  |  | Location does not have any trained personnel with HVD/HZA Endorsement | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1979 | VIJAYAWADA TERMINAL | Location to get security to get HVD/HZA endorsement for movingTT 50–100m in case of any emergency | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151578 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151578 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151578 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151578 |  | AUD-2026-09-2000017501ACN-2026-09-4000151578 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151579 | Open |  |  | The DCP fire extinguisher of TT No. AP39UH5399 was operated by the TT driver S. Simhachalam, discharge duration is less at only 25 seconds. | 2.14 | TT crew fire extinguisher usage checked | 1979 | VIJAYAWADA TERMINAL | TT fire extinguishers to be checked at Terminal at regular intervals | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151579 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151579 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151579 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151579 |  | AUD-2026-09-2000017501ACN-2026-09-4000151579 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151580 | Open |  |  | Checked for TK1B & TK7C. Tank 1B - TAS Readings : Dip Level : 648.2 cms , Water level : 2.7 ,Temp : 30.9°C . Actual Physical Dip Level : 647.5 cms , Water level : 2.6 cms ,Temp : 30.0°C , Tank 7C TAS Readings : Dip Level : 774.9 cms , Water level : 7.9 ,Temp : 31.6°C . Actual Physical Dip Level : 774.0 cms, Water - 8.0 cms, Temp 31.5 deg C | 3.7 | Inventory physical dip of minimum two tanks taken | 1979 | VIJAYAWADA TERMINAL | Location to take up with TAS vendor and ensure that variations in Oil dip remain with in tolerance limit of 3 mm . | SOD | Marketing | SCR | 2026-09-10 |  | 5 |  | S1 | F5 | 2026-09-10 | AUD-2026-09-2000017501ACN-2026-09-4000151580 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151580 | 2026-08-21 16:00 | 59.0872 | 374 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151580 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151580 |  | AUD-2026-09-2000017501ACN-2026-09-4000151580 | 21 |  | 27 | 80 | 12 | 12 | 54
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151581 | Open |  |  | MDSA, TAS, HLSA , Sr.Mgmt Inspn and SSA compliance status was reviewed. The location was advised to ensure 100% compliance with allpending observations within the stipulated target dates. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1979 | VIJAYAWADA TERMINAL | Pending audit observations to be complied as per target dates | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017501ACN-2026-09-4000151581 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151581 | 2026-08-21 16:00 | 59.0872 | 425 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151581 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151581 |  | AUD-2026-09-2000017501ACN-2026-09-4000151581 | 21 |  | 27 | 80 | 12 | 12 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151582 | Open |  |  | Full field round completed (gantry/tank farm/pump house/siding/control room/security/admin). FPH observations - Water leakge observed for Jockey pump no 2, Fire engines not started at rated RPM of 2100 rpm and observed RPM range of 1980 rpm to 2056 rpm . FE1 Fire alarm panel display not showing the parameters limits , FE7 high coolant water temp. and overspeed indicator buttons are not proper, FE6 exhaust pipe under repair, FE2 upon LLOP check engine stopped. FE5 is under repair | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1979 | VIJAYAWADA TERMINAL | Location to take corrective action | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151582 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151582 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151582 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151582 |  | AUD-2026-09-2000017501ACN-2026-09-4000151582 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151583 | Open |  |  | TK 1C roof replacement works in progress , on track for completion well within time. Tank 4A, 4B tank repairs , Tank 4 B conversionto ATF budget received . | 4.3 | Project progress reviewed | 1979 | VIJAYAWADA TERMINAL | To closely monitor the project activities of Tank Repairs and To follow up with vendor for completion of the Robotic Loading arm project by 30.09.2026. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151583 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151583 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151583 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151583 |  | AUD-2026-09-2000017501ACN-2026-09-4000151583 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151584 | Open |  |  | Scrap generated from Tank 1C repair to be disposed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1979 | VIJAYAWADA TERMINAL | RFD to be made and loaction to be scrap free by Q-III | SOD | Marketing | SCR | 2026-12-30 |  | 5 |  | S1 | F5 | 2026-12-30 | AUD-2026-09-2000017501ACN-2026-09-4000151584 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151584 | 2026-08-21 16:00 | 59.0872 | 485 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151584 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151584 |  | AUD-2026-09-2000017501ACN-2026-09-4000151584 | 21 |  | 27 | 80 | 12 | 12 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151585 | Open |  |  | TT crew / Transporter sign in ID not available. | 6 |  | 1979 | VIJAYAWADA TERMINAL | TT crew / Transporter sign in ID not available, to be ensured | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151585 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151585 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151585 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151585 |  | AUD-2026-09-2000017501ACN-2026-09-4000151585 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151586 | Open |  |  | SOP Boards are faded , to be replaced. | 6.1 |  | 1979 | VIJAYAWADA TERMINAL | SOP Boards are faded , to be replaced. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151586 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151586 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151586 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151586 |  | AUD-2026-09-2000017501ACN-2026-09-4000151586 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151587 | Open |  |  | Pressure Guages in PPH calibration date sticker is faded and not readable. | 6.2 |  | 1979 | VIJAYAWADA TERMINAL | Pressure Guages in PPH calibration date sticker to be replaced. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151587 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151587 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151587 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151587 |  | AUD-2026-09-2000017501ACN-2026-09-4000151587 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151588 | Open |  |  | Lighting is not available in the extended PPH | 6.3 |  | 1979 | VIJAYAWADA TERMINAL | Lighting to be provided in the extended PPH | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151588 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151588 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151588 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151588 |  | AUD-2026-09-2000017501ACN-2026-09-4000151588 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-21 16:00 | AUD-2026-09-2000017501 | 2026-08-20 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151589 | Open |  |  | Sand buckets near Bay 20 are only half filled. | 6.4 |  | 1979 | VIJAYAWADA TERMINAL | Sand buckets to be kept filled with sand in full. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017501ACN-2026-09-4000151589 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017501ACN-2026-09-4000151589 | 2026-08-21 16:00 | 59.0872 | 394 | >20 | AUD-2026-09-2000017501 - ACN-2026-09-4000151589 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017501ACN-2026-09-4000151589 |  | AUD-2026-09-2000017501ACN-2026-09-4000151589 | 21 |  | 27 | 80 | 12 | 12 | 57
TYAGI ATUL | 2026-09-07 | MEENA NITESH KUMAR | 2026-08-14 | Complinace taken from all location officers for FY 25-26, 24-25 O&D circulars | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139985 | Closed | MEENA NITESH KUMAR | 2026-08-14 | Interaction was carried out at Rewari Terminal in presence of LIC and all location officers on expectations from location and each officer, compliance to recent HQO/Zonal circulars, improvement plans. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1334 | HPCL REWARI IRD | All circular compliance shall be reviewed by LIC and confirmation to be provided | SOD | Marketing | NZ | 2026-06-30 | INADEQUATE SAFETY CULTURE | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013601ACN-2026-06-4000139985 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139985 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139985 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139985 | AUD-2026-06-2000013601ACN-2026-06-4000139985 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
TYAGI ATUL | 2026-09-07 | MEENA NITESH KUMAR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139987 | Closed |  |  | Last mock drill was conducted by the location during the off-shift hours (night of 4th june'26 during night inspection). However, report for the drill is not made. Similarly, report of mock drill conducted on 30.05.2026 is not available in records. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1334 | HPCL REWARI IRD | Location to ensure preparation of mock drill reports immediately on completion of mock drills. | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013601ACN-2026-06-4000139987 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139987 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139987 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139987 | AUD-2026-06-2000013601ACN-2026-06-4000139987 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 53
TYAGI ATUL | 2026-09-07 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139989 | Closed |  |  | HVLR - Total 06 Nos of HVLR is available at the Location. HVLR No. 04 – Checked for its movement in all directions and found satisfactory. It was operated by the safety officer and his knowledge about the operting procedure for HVLR was found to be adequate. However, following observations were made: 1. The initial HVLR's direction was not found to be targetting the facility for which it isintended to be provided. 2. The power panel for it was found lying on the ground resting on the hydrant ring main. Moreover, the earthing connections for the panel were found severed. RSFPS - Only one tank, TK-26, is equipped with an RSFPS. However, it is brought to notice that operation of the RSFPS cannot be carried out from the control room due to an issue with the software available. HCD - Total 16 Nos of HCD available at the location. Out of which 07 nos are Open path and 09 Nos are Point type HCD. All HCD's are operatinal Open Path Type HCD No: 01 located at Pump House was checked with a filter no. 888260-2 & Sr. no. 1995- local hooter got actuated however, the LEL percentage recorded in the TAS system was 52%. Point type HCD No: 03 was tested thrice using MS fumesand it got operated with local hooter blowing each time @ 20~25% LEL display. 1.However, response from TAS/ Control Room was not received in the field about actuation of the HCD. On further inspection, it was found that the hooter associated with HCD in the TAS/ Control Room is non-operational. 2. As per the CAMC visit done by M/s. HAIL on 1st May'26, values K16 & TK17 are not getting reflected in TAS. Similarly, Open path HCD near TK26 is indicating erratic readings in TAS with readings going on higher side as compared to those in the field. Similarly, issue of erratic readings for Point Type HCD#17 is also recorded in the meeting. ESD - Total 14 No of ESDs are available at the location. Functionality of ESD at Security Cabin was verified during the mock fire drill conducted on 11th Jun'26 and was found to be okay. ESD checking record is also being maintained by the location. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1334 | HPCL REWARI IRD | HVLR: 1. Initial directions of HVLRs as well as FMs should be kept targeting the facility for which they are provided. 2. Power panel of the HVLR#4 to be re-installed in upright position with earthing connections duly restored. RSFPS: The feature of operating of RSFPS from Control room to be made operational. HCD: 1. HCD filters available to be indentified with percentage LEL which are meant for. 2. HCD Hooter in TAS Room to be made operational. 3. Open path HCDs as well as point type HCD found to be having erroneous communication with TAS to be rectified. | SOD | Marketing | NZ | 2026-07-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-10 | AUD-2026-06-2000013601ACN-2026-06-4000139989 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139989 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139989 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139989 | AUD-2026-06-2000013601ACN-2026-06-4000139989 | 21 | 21 | 27 | 80 | 1 | 1 | 45 | 53
TYAGI ATUL | 2026-09-07 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000139992 | Closed |  |  | Random checks of TT crew on roadside emergency procedures were conducted. Two TTs namely HR38X5024 and HR47E3637 were checked for availabilty of emergency kit. Both were not having the required emergency kit and the drivers were not aware about its requirement tobe maintained. Similarly, first aid kit of tanker no. HR38X5024 had expired medicines & disinfectant. | 2.15 | TT crew roadside emergency procedures checked | 1334 | HPCL REWARI IRD | Location to ensure: 1. Availability of emergency kit with all the TTs plying. 2. Enhance knowledge of the TT crew about its usagethru trainings. 3. Availability of first aid kit with all the TTs with valid ingredients inside them. | SOD | Marketing | NZ | 2026-07-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013601ACN-2026-06-4000139992 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139992 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139992 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139992 | AUD-2026-06-2000013601ACN-2026-06-4000139992 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 53
TYAGI ATUL | 2026-09-07 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000139999 | Closed |  |  | 1. TT display Board in TT parking area to be rectified. 2. Gap founf in valve box cover, same to be checked for all TTs and rectified. 3. Flex board outside TT parking area to be rectified. 4. ETP process flow diagram to be updated. SOP boards in ETP area to be updated. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1334 | HPCL REWARI IRD | XX | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013601ACN-2026-06-4000139999 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139999 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139999 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139999 | AUD-2026-06-2000013601ACN-2026-06-4000139999 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 53
TYAGI ATUL | 2026-09-07 | SINGH YUGAL KISHOR | 2026-07-31 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140003 | Closed |  |  | 1. Historical Opex was Rs.119.6/MT. As per the strategic targeted KPI, location is required to reduce it by 5%. 2. Historical Cycle time for Rewari is 56.6'. 3. QC index of Rewari was 91% during 2025-26. 4. Due date of pressure gauge testing is not mentioned on the gauges in the field. 5. Valve V2 of foam pourer line did not open leading to delay in testing of the foam pourer for product tank TK13. 6. Dyke valve# 7 of tank TK27 was found open physically as well as in TAS. Dyke valve B of the Tank Dyke 01 was found tobe open in field but there was not indication in the TAS. 7. Indentification of Dyke Valve as A or B was found missing at Tank Dyke 01. 8. Foam suction/ inlet pipe of foam monitor M13 was found to be removed from the foam drum instead of being ready for operation in case of any emergency. 9. Water Seepage marks were observed from MCC room's walls. 10. All exhaust fans of MCC room were found to be kept in off condition. 11. Power factor in the MCC panel was found to be 0.845 during the visit on 10.06.2026. When probedfurther, it was established that APFC panel was not functioning. On putting on 50KVAR capacitor in the power factor jumped to 0.95.On further pressing additional 25KVAR capacitor into service, the power factor jumped to 0.998 which is desirable under normal circumstances. 12. Single line diagram in the MCC room has mention of 400KVA DG sent + 250KVA DG sent whereas location is having only one 500KVA DG set. 13. Insulation mats were not found on the chequered plate of the cable trench between the 2 VFD panels provided for MS & HSD pumps. 14. Foam tank#01 of capacity 8.5KL was found empty whereas Foam Tank # 02 of 8.5KL capacity was found containingaround 4KL product. However, the outlet valves of both these tanks were found to be kept in closed condition. On enquiring, the valves were closed around 15 days back for maintenance but not re-opened after completion of the maintenance job. 15. Duplication of roles found on the Fire Organisation chart of MCC Room. 16. Wailing mechanism of hand siren#3 was not free. 17. Wrong RPM found mentioned on the Fire Engine display board. 18. SOP for re-fueling of HSD tanks of Fire Engine was found not to be in-line with the existing practice. 19. Heavy leakage was found from the drive end gland packing of Fire Engine no. 1 & 3. 20. Oil Leakage was evident on the body of Fire Engine no. 2. 21. Dirt accumulation was found on Fire Engine No. 1. 22. -ve pressure guage was found installed on the discharge line of Jockey Pump No. 1. A total of 148 instances of bay reallocation are appearing during the period 1st Jan'26 to 10th Feb'26. Out of these, 43 instances are on account of driver not reported. Apparently, biometric verification of all the TT drivers is not enabled for all the TT drivers which is resulting in multiple card swiping by one driver for many TTs and when theturn of the TT comes, actual TT is not available for loading. Location has been advised to enable Bio-metric verification at R1 forall the drivers to avoid bay re-allocation on this account. EDC 15th Mar’26. Two MS Tanks (TK-1 and Tk-2 of Capacity 590 KL Each)and one Slop Tank (TK-17-500 KL) are under Outage for Major Repair. Direction is sought from HQO on whether these tanks are to be repaired or New Tank is to be Built. Proposals for both the Options have been submitted | 6.1 | High priority areas requiring immediate action. | 1334 | HPCL REWARI IRD | 1. Location to restrict the Opex during 2026-27 to Rs.114/MT. 2. Location to restrict the cycle time to 43' as per the AOP target for 2026-27. 3. Location to achieve minimum QC Index of 95% during 2026-27. 4. Due date of testing to be mentioned on each pressure gauge. 5. Valve V2 on the foam pourer line to be rectified immediately for intended functioning. 6. Necessary rectification to be done. Periodic testing of dyke valve and its signal in TAS to be verified with record for testing maintained. 7. Proper identification of valves to be ensured in field to match it with the displayed SOP boards. 8. Foam facilities to be kept in ready condition all the time to tackle any of the emergency in field. 9. Water seepages should be arrested and internal walls of MCC rooms should be repainted after rectification. 10. Exhaust fans of MCC rooms should be kept in on condition as per the protocol. 11. APFC panel should be made functional. Location to start recording PF readings on daily basis with review by the concerned officer. 12. SLD to be rectified as per the actual equipment available. 13. Insulation mats to be provided in the MCC room wherever not available. 14.Location to develop practice of post inspection of the equipment/ site after completion of the maintenance/ other works at the end of each day to avoid such lapses. 15. FOC to be modified. 16. Hand Sirens to be tested and maintained in prime working condition. 17. Proper display of RPM of Fire Engine to be ensured in the pump house. Duplicate boards to be removed. 18. SOP to be modified as per the actual practice. 19. Leakages from glands of Fire Engines to be arrested. 20. Oil leakage from the fire engine to be arrested. 21. Fire Engines to be kept in presentable condition for inspection. 22. Proper pressure gauge to be installed. | SOD | Marketing | NZ | 2027-03-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2027-03-30 | AUD-2026-06-2000013601ACN-2026-06-4000140003 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000140003 | 2026-09-10 17:00 | 39.0455 | 371 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000140003 | 532 | 8294 | 21 | 8294 | -161 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000140003 | AUD-2026-06-2000013601ACN-2026-06-4000140003 | 21 | 21 | 27 | 80 | 1 | 1 | 83 | 53
ALBY ABRAHAM ARACKAL | 2026-09-08 | SRIJIN S | 2026-09-08 | The PESO license for night operations point is already mentioned in one of the compliance point. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130100 | Closed | SRIJIN S | 2026-09-08 | The compliance status of MDSA, SSA pending points are reviewed. Location to comply at the earliest. All the lightings jobs completed and LUX levels are as per OISD-244. Already location submitted the request letter for PLT operations beyond sunset to Dy. Chief Controller of Explosives, Ernakulam.They have advised to submit the application to the Chief Controller of Explosives,Nagpur. | 1.3 | Pending issues reviewed | 1833 | COCHIN BLACK TERMINAL | "1. Comply audit recommendaions in a time bound manner. 2. PESO license for night operations to be taken at the earliest. 3. Complete PL integrity assessement surveys at the earliest possible.Location has recently conducted CAT and CIPL survey. DCVG and LRUT survey under progress. (Last inspection date and status of complaince). Survey recommendations are to be reviewed and action plan to be drawn for timely compliance." | SOD | Marketing | CZR | 2026-12-31 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 6 | PROCESS SAFETY | S2 | F3 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130100 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130100 | 2026-09-08 16:00 | 41.0872 | 372 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130100 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130100 | AUD-2026-05-2000012202ACN-2026-05-4000130100 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 54
ALBY ABRAHAM ARACKAL | 2026-09-08 | SRIJIN S | 2026-09-08 | all the safety committee pending points complied. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130105 | Closed | SRIJIN S | 2026-09-08 | All mock fire drills are single cotingency. Observation recorded and corrective actions taken. Safety committee conducted on 19-03-2026. 7 Recommendation were recorded . 4 pending to be complied. | 2.2 | Double contingency scenario simulated; observations recorded | 1833 | COCHIN BLACK TERMINAL | Four safety committee pending points to be complied by 15-06-2026. Location to review all scenarios considered in ERDMP and conduct drills for all ERDMP scenarios. | SOD | Marketing | CZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012202ACN-2026-05-4000130105 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130105 | 2026-09-08 16:00 | 41.0872 | 372 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130105 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130105 | AUD-2026-05-2000012202ACN-2026-05-4000130105 | 21 | 21 | 27 | 80 | 2 | 0 | 44 | 54
ALBY ABRAHAM ARACKAL | 2026-09-08 | SRIJIN S | 2026-09-08 | ECC (Emergency control center) is marked and maintained as per ERDMP manual. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130108 | Closed | SRIJIN S | 2026-09-08 | Cochin terminal is a non-automated location.No control room available. | 2.8 | Access control system is available for control room entry, log book also maintained.Efficient monitoring is done by location. | 1833 | COCHIN BLACK TERMINAL | ECC (Emergency control center) is to be marked and maintained as per ERDMP manual. | SOD | Marketing | CZR | 2026-05-30 | FAILURE TO FOLLOW PROCEDURES | 2 | EMERGENCY | S2 | F1 | 2026-05-30 | AUD-2026-05-2000012202ACN-2026-05-4000130108 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130108 | 2026-09-08 16:00 | 41.0872 | 372 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130108 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130108 | AUD-2026-05-2000012202ACN-2026-05-4000130108 | 21 | 21 | 27 | 80 | 2 | 0 | 39 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | SATYENDRA CHOURASIA | 2026-09-05 | Fire man Axe & Tester provided in Emergency Kit Trolley. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147035 | Closed | SATYENDRA CHOURASIA | 2026-09-05 | The Emergency Response Toolkit Trolley was inspected, Fire man Axe, tester not available | 2.5 | Emergency response preparedness reviewed | 1919 | SECUNDERABAD TERMINAL | To take corrective action for emergency trolley availability with all the required items. | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147035 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147035 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147035 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147035 | AUD-2026-08-2000016364ACN-2026-08-4000147035 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | SATYENDRA CHOURASIA | 2026-08-22 | Cross-checked all camera angles and realignment done wherever required. Two offline cameras made online. During the service visit by M/s SCORE Information Technologies Limited on 24.08.2026, Tank_3E_PTZ was found faulty. Tank_3E_PTZ has been sent to M/s SCORE Information Technologies Limited for repair under AMC, and are expected to be received and restored within the current month. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147036 | Closed | SATYENDRA CHOURASIA | 2026-09-05 | Out of 72 CCTV cameras, 3 cameras were found offline: PTZ_FLM_18, Tank_4B_PTZ, and Tank_3E_PTZ. Additionally, 2 cameras were operational but had hazy/blurred image quality: Perimeter_17_WT_15 and Perimeter_12_WT_7. | 2.6 | CCTV functioning checked | 1919 | SECUNDERABAD TERMINAL | CCTV cameras to be realigned for proper coverage . To follow up with vendor for rectifying the three cameras. | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147036 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147036 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147036 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147036 | AUD-2026-08-2000016364ACN-2026-08-4000147036 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | SATYENDRA CHOURASIA | 2026-08-24 | the CLMS In Time attendance box has been fixed after the CBAC. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147047 | Closed | SATYENDRA CHOURASIA | 2026-08-24 | CLMS Attendance to be fixed after CBAC. | 6.1 |  | 1919 | SECUNDERABAD TERMINAL | CLMS Attendance to be fixed after CBAC. | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147047 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147047 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147047 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147047 | AUD-2026-08-2000016364ACN-2026-08-4000147047 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | S SWETHA BAI | 2026-09-07 | Bay verification completed, Calibration due in November | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147037 | Closed | S SWETHA BAI | 2026-09-07 | Checked for TT Number : TS08UA8466 at Bay 7 found all compartments OK C1 → 0, C2 → 0, C3 → 0, C4 → 0. For TT Number : TS08T1856 at Bay 4 found C1 → +3 Litres, C2 → 0, C3 → +10 Litres, & TT Number : TG16T5805 found C1 → +6 Litres, C2 → +10 Litres, C3 → -10 Litres. | 3.2 | Post-loading dip checks verified | 1919 | SECUNDERABAD TERMINAL | Location to take take up with TAS vendor and corrective action to be taken | SOD | Marketing | SCR | 2026-10-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147037 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147037 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147037 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147037 | AUD-2026-08-2000016364ACN-2026-08-4000147037 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | SATYENDRA CHOURASIA | 2026-09-08 | Coordinated with Sterna for 2 TTs for EM Lock Rectification | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147038 | Closed | SATYENDRA CHOURASIA | 2026-09-08 | EM Lock functionality of 5 TTs was checked using the Intelligent Key. TS18T5805 – Top & Bottom EM Lock Not OK; TS08UA8469 – Top & Bottom EM Lock OK; TS08U10111 – Top & Bottom EM Lock Not OK; TS08UA9379 – Top & Bottom EM Lock OK; and TS08UA5499 – Top & Bottom EM Lock OK. Overall, 3 TTs were found satisfactory and 2 TTs require rectification of EM Lock system. | 3.5 | EM Lock SOP compliance verified | 1919 | SECUNDERABAD TERMINAL | Overall, 3 TTs were found satisfactory and 2 TTs require rectification of EM Lock system. Location to take up with M/S STERNA | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147038 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147038 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147038 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147038 | AUD-2026-08-2000016364ACN-2026-08-4000147038 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | S SWETHA BAI | 2026-09-07 | As verified on 27.08.2026, TAS and physical values are as below: TAS: level-143.6; Water level- 0; Temperature-28 Physical: level-143.8; Water level- 0;Temperature-27.5 As the difference in TAS and physical within limits, we can say that gauge is working fine. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147039 | Closed | S SWETHA BAI | 2026-09-07 | Checked for TK1A TAS Readings : Dip Level : 184 CMs , Water level : 0 CM ,Temp : 26.7°C . Actual Physical Dip Level : 184.5CMs , Water level : 0 CM ,Temp : 25.5°C Checked for TK3A TAS Readings : Dip Level : 987.2 CMs , Water level : 5.5 CM ,Temp : 28.9°C . Actual Physical Dip Level : 987.5CMs , Water level : 5.2 CM ,Temp : 30°C | 3.7 | Inventory physical dip of minimum two tanks taken | 1919 | SECUNDERABAD TERMINAL | Location to take take up with TAS vendor and corrective action to be taken for TK1A. | SOD | Marketing | SCR | 2026-10-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147039 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147039 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147039 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147039 | AUD-2026-08-2000016364ACN-2026-08-4000147039 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | S SWETHA BAI | 2026-09-07 | Hooters are working and it is reset it system after multiple times of muting | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-08-4000147045 | Closed | S SWETHA BAI | 2026-09-07 | The functioning of the HCD hooter was checked. It was observed that the hooter was kept on mute, and the acknowledgement of a previous hooter alarm was pending. | 5.2 | Functioning of all Hooters in control room | 1919 | SECUNDERABAD TERMINAL | Hooter alarms to be acknowledged by control officer and not be kept pending | SOD | Marketing | SCR | 2026-10-06 | INSTRUMENTATION OR ALARM FAILURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-06 | AUD-2026-08-2000016364ACN-2026-08-4000147045 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147045 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147045 | 532 | 8294 | 21 | 8294 | 13 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147045 | AUD-2026-08-2000016364ACN-2026-08-4000147045 | 21 | 21 | 27 | 80 | 1 | -12 | 58 | 54
NIDAMARTHI NAGA KIRAN | 2026-09-08 | SATYENDRA CHOURASIA | 2026-09-05 | Ethanol testing being carried out strictly as per the prescribed procedure without any deviations. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147046 | Closed | SATYENDRA CHOURASIA | 2026-09-05 | Ethanol testing shall be carried out strictly as per the prescribed procedure without any deviations. | 6 |  | 1919 | SECUNDERABAD TERMINAL | Ethanol testing shall be carried out strictly as per the prescribed procedure without any deviations. | SOD | Marketing | SCR | 2026-10-06 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-06 | AUD-2026-08-2000016364ACN-2026-08-4000147046 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147046 | 2026-08-06 19:00 | 73.9622 | 372 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147046 | 532 | 8294 | 21 | 8294 | 13 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147046 | AUD-2026-08-2000016364ACN-2026-08-4000147046 | 21 | 21 | 27 | 80 | 1 | -12 | 58 | 54
[5 empty] | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151900 | Open |  |  | Pending IRR of Contaminated ethanol reprocessing was reviewed and discussed. Advised location to expedite and close the IRR. | 1.3 | Pending issues reviewed | 1254 | JALANDHAR DEPOT | IRR to be processed immediately. | SOD | Marketing | NFZ | 2026-08-31 |  | 2 |  | S2 | F1 | 2026-08-31 | AUD-2026-09-2000017550ACN-2026-09-4000151900 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151900 | 2026-08-21 | 59.7538 | 364 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151900 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017550ACN-2026-09-4000151900 |  | AUD-2026-09-2000017550ACN-2026-09-4000151900 | 21 |  | 27 | 80 | 0 | -21 | 52
[5 empty] | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151901 | Open |  |  | Two nos.HCD are not functioning, sent for repair. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1254 | JALANDHAR DEPOT | Location to follow up for HCD repair & early installation. | SOD | Marketing | NFZ | 2026-09-15 |  | 3 |  | S1 | F3 | 2026-09-15 | AUD-2026-09-2000017550ACN-2026-09-4000151901 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151901 | 2026-08-21 | 59.7538 | 379 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151901 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017550ACN-2026-09-4000151901 |  | AUD-2026-09-2000017550ACN-2026-09-4000151901 | 21 |  | 27 | 80 | 0 | -21 | 55
[5 empty] | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151903 | Open |  |  | Location has approved RFDs for Miscellaneous scrap of 2MT | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1254 | JALANDHAR DEPOT | Scrap disposal to be completed by 30.09.2026 | SOD | Marketing | NFZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-09-2000017550ACN-2026-09-4000151903 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151903 | 2026-08-21 | 59.7538 | 394 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151903 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017550ACN-2026-09-4000151903 |  | AUD-2026-09-2000017550ACN-2026-09-4000151903 | 21 |  | 27 | 80 | 0 | -21 | 57
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152000 | Open |  |  | 1) There is shortfall in number of TTs at Depot, notification already given for additional TT induction. 2) Ratio of top loading TTs to bottom loading TTs is still high and conversion rate is not as expected. | 1.3 | Pending issues reviewed | 1183 | NALGARH DEPOT | 1).Location to complete the process of additional TT induction by 15.09.2026. 2) Location to complete conversion of top loading TTs to bottom loading TTs in a phased manner without further delay. | SOD | Marketing | NFZ | 2026-09-15 |  | 6 |  | S3 | F2 | 2026-09-15 | AUD-2026-09-2000017600ACN-2026-09-4000152000 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152000 | 2026-08-27 | 53.7538 | 379 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152000 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017600ACN-2026-09-4000152000 |  | AUD-2026-09-2000017600ACN-2026-09-4000152000 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152001 | Open |  |  | 1) All cameras to be made functional 2) Scrap lying in depot to be disposed on priority | 1.4 | Earlier action points status checked | 1183 | NALGARH DEPOT | Location to take action on pending points | SOD | Marketing | NFZ | 2026-09-10 |  | 4 |  | S2 | F2 | 2026-09-10 | AUD-2026-09-2000017600ACN-2026-09-4000152001 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152001 | 2026-08-27 | 53.7538 | 374 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152001 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152001 |  | AUD-2026-09-2000017600ACN-2026-09-4000152001 | 21 |  | 27 | 80 | 1 | 1 | 54
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152002 | Open |  |  | Location is having 40 CCTVs and out of which 38 are working. Checked records of CCTV being analysed by Security. | 2.6 | CCTV functioning checked | 1183 | NALGARH DEPOT | Repair of camera to be expedited.Follow up with vendor to be maintained | SOD | Marketing | NFZ | 2026-09-15 |  | 4 |  | S2 | F2 | 2026-09-15 | AUD-2026-09-2000017600ACN-2026-09-4000152002 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152002 | 2026-08-27 | 53.7538 | 379 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152002 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152002 |  | AUD-2026-09-2000017600ACN-2026-09-4000152002 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152003 | Open |  |  | Housekeeping to be improved in all areas including TT Gantry, Sample Room & elsewhere. Vegetation found near sample room area & under HT cable passing over depot advised to remove. | 3.15 | Housekeeping & PPE usage checked | 1183 | NALGARH DEPOT | Location to take immediate corrective action. | SOD | Marketing | NFZ | 2026-09-10 |  | 10 |  | S2 | F5 | 2026-09-10 | AUD-2026-09-2000017600ACN-2026-09-4000152003 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152003 | 2026-08-27 | 53.7538 | 374 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152003 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017600ACN-2026-09-4000152003 |  | AUD-2026-09-2000017600ACN-2026-09-4000152003 | 21 |  | 27 | 80 | 1 | 1 | 54
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152004 | Open |  |  | Checked & found a lot of vegetation near HT cable. | 3.16 | Earth pits / boundary / vegetation control checked | 1183 | NALGARH DEPOT | Location to take immediate corrective action. | SOD | Marketing | NFZ | 2026-09-10 |  | 10 |  | S2 | F5 | 2026-09-10 | AUD-2026-09-2000017600ACN-2026-09-4000152004 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152004 | 2026-08-27 | 53.7538 | 374 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152004 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017600ACN-2026-09-4000152004 |  | AUD-2026-09-2000017600ACN-2026-09-4000152004 | 21 |  | 27 | 80 | 1 | 1 | 54
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152005 | Open |  |  | Scrap observed at Location, RFD of the same processed but disposal not done despite finalization of bidder in auction two times. Location is in process of getting the auction done again on the basis of lots to ensure disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1183 | NALGARH DEPOT | Actual disposal to be expedited. | SOD | Marketing | NFZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017600ACN-2026-09-4000152005 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152005 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152005 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152005 |  | AUD-2026-09-2000017600ACN-2026-09-4000152005 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152006 | Open |  |  | NH approach road towards Depot is damaged & a safety concern. | 6.1 | Approach Road outside Depot premises | 1183 | NALGARH DEPOT | Location to inform NH authorities in writing. | SOD | Marketing | NFZ | 2026-09-05 |  | 4 |  | S1 | F4 | 2026-09-05 | AUD-2026-09-2000017600ACN-2026-09-4000152006 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152006 | 2026-08-27 | 53.7538 | 369 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152006 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152006 |  | AUD-2026-09-2000017600ACN-2026-09-4000152006 | 21 |  | 27 | 80 | 1 | 1 | 53
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152007 | Open |  |  | Cleaning of worker amenities to be done. Housekeeping to be improved. | 6.2 | TT Parking Area | 1183 | NALGARH DEPOT | Location to take immediate corrective action. | SOD | Marketing | NFZ | 2026-08-31 |  | 3 |  | S3 | F1 | 2026-08-31 | AUD-2026-09-2000017600ACN-2026-09-4000152007 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152007 | 2026-08-27 | 53.7538 | 364 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152007 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152007 |  | AUD-2026-09-2000017600ACN-2026-09-4000152007 | 21 |  | 27 | 80 | 1 | 1 | 52
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152008 | Open |  |  | Earthing strip covering the fence found to be painted, vegetation found inside the yard. | 6.3 | Transformer Yard | 1183 | NALGARH DEPOT | Earthing continuity to be checked, vegetation to be removed. | SOD | Marketing | NFZ | 2026-09-07 |  | 1 |  | S1 | F1 | 2026-09-07 | AUD-2026-09-2000017600ACN-2026-09-4000152008 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152008 | 2026-08-27 | 53.7538 | 371 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152008 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152008 |  | AUD-2026-09-2000017600ACN-2026-09-4000152008 | 21 |  | 27 | 80 | 1 | 1 | 53
[5 empty] | LOCATION VISIT-NALAGARH_25-27.08.26 | 2026-08-27 | AUD-2026-09-2000017600 | 2026-08-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152009 | Open |  |  | Housekeeping to be improved. | 6.4 | Sample Room | 1183 | NALGARH DEPOT | Location to take immediate corrective action. | SOD | Marketing | NFZ | 2026-08-31 |  | 2 |  | S2 | F1 | 2026-08-31 | AUD-2026-09-2000017600ACN-2026-09-4000152009 | HP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017600ACN-2026-09-4000152009 | 2026-08-27 | 53.7538 | 364 | >20 | AUD-2026-09-2000017600 - ACN-2026-09-4000152009 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017600ACN-2026-09-4000152009 |  | AUD-2026-09-2000017600ACN-2026-09-4000152009 | 21 |  | 27 | 80 | 1 | 1 | 52
[5 empty] | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152017 | Open |  |  | Shortfall of TTs due to ongoing court cases observed. | 6.2 | Transportation | 1256 | JAMMU DEPOT | Location to expedite the process of TT induction. | SOD | Marketing | NFZ | 2026-09-09 |  | 6 |  | S3 | F2 | 2026-09-09 | AUD-2026-09-2000017601ACN-2026-09-4000152017 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152017 | 2026-09-04 | 45.7538 | 373 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152017 | 532 | 8294 | 21 | 8294 | 40 | 40 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017601ACN-2026-09-4000152017 |  | AUD-2026-09-2000017601ACN-2026-09-4000152017 | 21 |  | 27 | 80 | 1 | -4 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | HVLR foam pick up hose leakage from coupling has been rectified | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147019 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | HVLR-1 for Tank-1C has been operated by the officer. HVLR Foam pick up hose leakage from coupling observed. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1937 | SURYAPET TERMINAL | HVLR Foam pick up hose leakage from coupling to be rectified. | SOD | Marketing | SCR | 2026-08-05 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-05 | AUD-2026-08-2000016363ACN-2026-08-4000147019 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147019 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147019 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147019 | AUD-2026-08-2000016363ACN-2026-08-4000147019 | 21 | 21 | 27 | 80 | 0 | 0 | 49 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | CCTV cameras have been re-aligned for proper coverage and other two cameras have been repaired by the vendor | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147018 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | CCTV functioning checked . Out of the total 43 CCTV cameras , 2 cameras are not working. CCTV camera 1C is blurred, ETP camera is hazy, perimeter ingate camera and perimeter pipeline inlet/outlet camera showing blank,cameras near watch tower2 and 3 are hazy. | 2.6 | CCTV functioning checked | 1937 | SURYAPET TERMINAL | CCTV cameras to be realigned for proper coverage . To follow up with vendor for rectifying the two cameras. | SOD | Marketing | SCR | 2026-08-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016363ACN-2026-08-4000147018 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147018 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147018 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147018 | AUD-2026-08-2000016363ACN-2026-08-4000147018 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | CBAC system at Ethanol TT out Gate has been Shifted to TTG entry to avoid unauthorized access to TTG. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147031 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | CBAC system at Ethanol TT out Gate to Shifted to TTG entry to avoid unauthorized access to TTG | 6.2 |  | 1937 | SURYAPET TERMINAL | CBAC system at Ethanol TT out Gate to Shifted to TTG entry to avoid unauthorized access to TTG | SOD | Marketing | SCR | 2026-08-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-30 | AUD-2026-08-2000016363ACN-2026-08-4000147031 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147031 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147031 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147031 | AUD-2026-08-2000016363ACN-2026-08-4000147031 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | Payment processed for 14 dormant keys on 5th of september, and recovery of the same to be advised to finance, replacement for thosekeys has been received from vendor | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128232 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | Dormant Keys 7 nos and dormat locks 3 nos to be collected for putting in use | 6.2 |  | 1937 | SURYAPET TERMINAL | Dormant Keys 7 nos and dormat locks 3 nos to be collected for putting in use | SOD | Marketing | SCR | 2026-05-31 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011400ACN-2026-04-4000128232 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128232 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128232 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128232 | AUD-2026-04-2000011400ACN-2026-04-4000128232 | 21 | 21 | 27 | 80 | 0 | 0 | 39 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | Emerson person have visited and reduced the unauthorized flow. Subsequently W &M stamping also been taken. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147022 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | Total 15 instances of unauthorized flow - from 01.04.2026 till date as on 04.08.2026 due to DCV diaghpragm/orings failures & non-availability of AMC for > 6months resulting in delay of zero calibration. All cases are false alarms with no real product flow except 1 instance in July2026. | 3.11 | MFM vs BCU totalizer comparison checked - | 1937 | SURYAPET TERMINAL | Location to take up with TAS vendor for corrective action on false alarms issue | SOD | Marketing | SCR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016363ACN-2026-08-4000147022 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147022 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147022 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147022 | AUD-2026-08-2000016363ACN-2026-08-4000147022 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | Calibration is been done and W&M stamping has been done for the bays on 27.08.2026 | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147024 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | For dates 20th & 22nd July - 4 bays MFM meter factor has been changed including one bay (bay 10) which is under maintenance after conversion to Mixed Bay. By vendor Emerson . | 3.13 | K-factor changes reviewed (if any) - | 1937 | SURYAPET TERMINAL | Bays under observation and W&M stamping to be done. | SOD | Marketing | SCR | 2026-08-31 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016363ACN-2026-08-4000147024 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147024 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147024 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147024 | AUD-2026-08-2000016363ACN-2026-08-4000147024 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | Details are maintained in logbook and remarks are correctly entered in BCU. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147025 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | 33 instances only for MFM verification thru prover including 4 instances of local loading for topping up Fire Engine & DG sets fueloil tanks, | 3.14 | Local loading checks (if applicable) - | 1937 | SURYAPET TERMINAL | Local loading with full remarks to be mentioned in BCU properly. Remarks to be mentioned in Log Books as circulars. Details of UG tanks to be mentioned post Proving and unloading in UG Tank | SOD | Marketing | SCR | 2026-08-05 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-05 | AUD-2026-08-2000016363ACN-2026-08-4000147025 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147025 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147025 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147025 | AUD-2026-08-2000016363ACN-2026-08-4000147025 | 21 | 21 | 27 | 80 | 0 | 0 | 49 | 54
CHOPPA SANTHOSH KUMAR | 2026-09-08 | DAMARAKONDA VARSHITHA | 2026-09-08 | As the truck dips was found abnormal, truck was taken for re-calibration and upon opening the compartment, found, dip pipe which was attached thru bolted arrangement got loosened, resulting in hanging of dip pipe, giving abnormal dip readings. It was rectified and no change in DL/PL. Hence not an issue with bay/MFM accuracy. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147020 | Closed | DAMARAKONDA VARSHITHA | 2026-09-08 | Dips checked in Bay 7, for the truck TG29T3326.Comp I-ok, Comp II -3 mm excess ( BCU overrun of 7 litrs), Comp III-OK , Comp IV -OK, Compt V - 1 cm excess | 3.2 | Post-loading dip checks verified | 1937 | SURYAPET TERMINAL | Location to take take up with TAS vendor and corrective action to be taken | SOD | Marketing | SCR | 2026-08-20 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-20 | AUD-2026-08-2000016363ACN-2026-08-4000147020 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147020 | 2026-08-04 18:45 | 75.9726 | 372 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147020 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147020 | AUD-2026-08-2000016363ACN-2026-08-4000147020 | 21 | 21 | 27 | 80 | 0 | 0 | 51 | 54
LINGAMPALLI SRIHARSHA | 2026-09-08 | KESHETTI SAI MANISH | 2026-09-08 | Camera vendor visited on 03-09-2026. All camera are functioning. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151553 | Closed | KESHETTI SAI MANISH | 2026-09-08 | 3 camera are under breakdown. Calibration shed - Connector issue Out Gate - Sent for repair Railway Siding - Cable procured, installation to be done. Unauthorized bike in parking area. Location informed Police to tow away the vehicle. | 2.6 | CCTV functioning checked | 1915 | RAMAGUNDAM DEPOT | 3 camera functionality to be restored | SOD | Marketing | SCR | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 9 | ASSET INTEGRITY | S3 | F3 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151553 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151553 | 2026-08-26 18:00 | 54.0038 | 372 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151553 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017500ACN-2026-09-4000151553 | AUD-2026-09-2000017500ACN-2026-09-4000151553 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 54
LINGAMPALLI SRIHARSHA | 2026-09-08 | KESHETTI SAI MANISH | 2026-09-08 | Audit: AUD-2026-09-2000017206 uploaded in SAP | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151560 | Closed | KESHETTI SAI MANISH | 2026-09-08 | MDSA, TAS , SSA compliances are revieved .Advised location to ensure 100 % compliance as per target date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1915 | RAMAGUNDAM DEPOT | EDC of FY 26-27 MDSA audit to be submitted and all points to be closed within this FY 2026-27 | SOD | Marketing | SCR | 2026-09-30 | INADEQUATE SAFETY CULTURE | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151560 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151560 | 2026-08-26 18:00 | 54.0038 | 372 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151560 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151560 | AUD-2026-09-2000017500ACN-2026-09-4000151560 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 54
LINGAMPALLI SRIHARSHA | 2026-09-08 | KESHETTI SAI MANISH | 2026-09-08 | HCR alignment carried out and tested. HCD is functional | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151567 | Closed | KESHETTI SAI MANISH | 2026-09-08 | HCD of TKPG Open Path not properly alligned, not working | 6.5 |  | 1915 | RAMAGUNDAM DEPOT | HCD to be repaired and properly alligned | SOD | Marketing | SCR | 2026-09-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S4 | F2 | 2026-09-10 | AUD-2026-09-2000017500ACN-2026-09-4000151567 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151567 | 2026-08-26 18:00 | 54.0038 | 372 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151567 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017500ACN-2026-09-4000151567 | AUD-2026-09-2000017500ACN-2026-09-4000151567 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 54
LINGAMPALLI SRIHARSHA | 2026-09-08 | KESHETTI SAI MANISH | 2026-09-08 | PG testing carried out and stickers updated. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151568 | Closed | KESHETTI SAI MANISH | 2026-09-08 | Pressure Gauge Testing overdue on 24.8.26 | 6.6 |  | 1915 | RAMAGUNDAM DEPOT | Pressure Gauge testing of all gauges to be carried out and sticker with details to be pasted | SOD | Marketing | SCR | 2026-09-10 | COMPLACENCY OR RISK NORMALIZATION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-10 | AUD-2026-09-2000017500ACN-2026-09-4000151568 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151568 | 2026-08-26 18:00 | 54.0038 | 372 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151568 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151568 | AUD-2026-09-2000017500ACN-2026-09-4000151568 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 54
LINGAMPALLI SRIHARSHA | 2026-09-08 | KESHETTI SAI MANISH | 2026-09-08 | The obstruction was informed to local police and the vehicle was towed by the police. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151573 | Closed | KESHETTI SAI MANISH | 2026-09-08 | Obstruction seen at emergency gate exit | 6.11 |  | 1915 | RAMAGUNDAM DEPOT | Obstruction to be removed | SOD | Marketing | SCR | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | EMERGENCY | S4 | F1 | 2026-08-31 | AUD-2026-09-2000017500ACN-2026-09-4000151573 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151573 | 2026-08-26 18:00 | 54.0038 | 372 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151573 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151573 | AUD-2026-09-2000017500ACN-2026-09-4000151573 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | NIMDEO AMIT VINAYAK | 2026-08-25 | a. LPM improviement already underway. Focus is given on moring loads .Improvement will be shared by month end. b. Railway track payment is continuously followed up. Visit paid to DOM office , PO lite approved for payment. Lonks awaited from railway. C. Budget proposal ready , will be sned by 20.03.2026 in coordination with NZ. d. VTS monitring started and will be continued. e. LPM improviement already underway. Focus is given on moring loads.Improvement will be shared by month end | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125552 | Closed | AGARWAL VIPUL | 2026-03-18 | a. TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlier VC's with all Location TAS officer. To expedite AMC PO placement. b. Shift officers - expediting railway payment and siding track maintenance job along with Physical pipeline qty verification c. Maintenace officer - Seeking budget for tank and pipeline maintenance and repair jobs d. Transportation - Maintaining Annex-1 of VTS circular and ensuring thgat all TT's are covered for VTS and EM locking check on monthly baisis with record e. TT Gantry officer - Improvement in LPM | 1.8 | Improvement plans discussed | 1216 | BAHADURGARH TERMINAL | a. The TAS Officer should focus on improving TT exit time and LPM at the location also to Expedited placement of the AMC PO should also be ensured. b. Expedite railway payment processes and the siding track maintenance job alonwith Physical verification of pipeline quantity and record same c. Initiate the process for seeking the required budget for tank and pipeline maintenance and repair works. d. Annexure-1 of the VTS circular to be maintained and ensure that all TTs are covered under VTS. Monthly checks for VTS functionality and EM locking should be carried out and proper records maintained. e. The TT Gantry Officer should take necessary steps to improve the LPM at the gantry to enhance operational efficiency. | SOD | Marketing | NZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125552 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125552 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125552 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125552 | AUD-2026-03-2000011128ACN-2026-03-4000125552 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | ANKIT KUMAR | 2026-09-08 | HCD repair is under process being sent to vendor. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125560 | Closed | AGARWAL VIPUL | 2026-03-18 | HCD - Total 22 Nos of HCD available at the location. Out of which 12 nos are Open path and 10 Nos are Point type HCD. HCD of TK-19 and TK-14 are faulty. Open Path Type HCD No: 03 located at Pump House operated; and tested for 20% LEL using test film. TAS log also generated. Point type HCD No: 06 Located at Pump House operated; and found to be operated at 40% LEL. TAS log also generated. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1216 | BAHADURGARH TERMINAL | Faulty HCD's to be repaired and ensure operational rediness at all times. | SOD | Marketing | NZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 2 | ASSET INTEGRITY | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011128ACN-2026-03-4000125560 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125560 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125560 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125560 | AUD-2026-03-2000011128ACN-2026-03-4000125560 | 21 | 21 | 26 | 80 | 9 | 9 | 44 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | ANKIT KUMAR | 2026-09-08 | Surprise night inspection by DSO for this month has been planned by 20.03.2026. In subsequent months, surprise visits will be carried out and records will be maintained | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125555 | Closed | AGARWAL VIPUL | 2026-03-18 | Surprise visit was done at terminal around 22:00 hours of 27/02/2026 and fould all security guards in alert position. Security shift was headed by Head guard Sh Ajay along with Guards Dilbag Singh, Sandeep, Harish Kumar, Sanjay, Naresh, Sombir and Naseeb. Further, location is not maintaining records of Surprise night inspections. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1216 | BAHADURGARH TERMINAL | Location to perform Surprise Night Inspections and maintain record of Inspection along with entries in Gate register about visits done | SOD | Marketing | NZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125555 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125555 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125555 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125555 | AUD-2026-03-2000011128ACN-2026-03-4000125555 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | ANKIT KUMAR | 2026-08-21 | Faulty server has been replaced on 14.03.2026.Now 100% VA enabled cameras are online.Alerts are being closed on daily basis. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125558 | Closed | AGARWAL VIPUL | 2026-03-18 | A total of 82 CCTVs are integrated with the VA system, out of which 30 CCTVs are currently non-functional. One server has been identified as faulty and is presently under maintenance. As verified on 25/02/2026, one VA alert remains open pertaining to Gantry Bay 13–14, indicating “Absence of Wheel Choke.” | 2.7 | VA alerts checked / analysed | 1216 | BAHADURGARH TERMINAL | The faulty server under maintenance should be rectified and restored at the earliest to avoid disruption in the VA system. Ensure 100% compliance towards closing all VA Alerts in NOVEX, with proper documentation of the root cause for each alert. Necessary corrective and preventive actions must be implemented to prevent recurrence and ensure non-repeatability of such alerts. | SOD | Marketing | NZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125558 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125558 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125558 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125558 | AUD-2026-03-2000011128ACN-2026-03-4000125558 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | ANKIT KUMAR | 2026-09-08 | Mentioned TT No.HR58 B0999 was recitifed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125563 | Closed | ANKIT KUMAR | 2026-09-08 | Part B check was done on DCT HR58 B0999, of M/s Mahindra service station on 26/02/2026. Following are the observations 1. HAZ Chemsticker to be updated 2. Condition of Steel Guards requires painting 3. Hose not available in the TT 4. ABS not active in the TT 5. Protective screen for exhaust pipe to be made available 6. HAZ Endorsed licence was not available with the Driver, however Training Licence is available in the record and Valid till: 27/07/2026 | 3.1 | TT fittings & discipline checked | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-03-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-03-2000011128ACN-2026-03-4000125563 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125563 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125563 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125563 | AUD-2026-03-2000011128ACN-2026-03-4000125563 | 21 | 21 | 26 | 80 | 9 | 9 | 30 | 54
NIMDEO AMIT VINAYAK | 2026-09-08 | ANKIT KUMAR | 2026-09-08 | Daily Auto Reconciliation is being carriied out to improve TFMS% | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125568 | Closed | ANKIT KUMAR | 2026-09-08 | Avg. TFMS-SAP reconciliation % for the period Apr'25 to Jan'26 is 92%. | 3.1 | TFMS/SAP reconciliation checked | 1216 | BAHADURGARH TERMINAL | Location to further improve the % of TFMS-SAP reconciliation. | SOD | Marketing | NZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125568 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125568 | 2026-09-05 | 44.7538 | 372 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125568 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125568 | AUD-2026-03-2000011128ACN-2026-03-4000125568 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-10 | Concertina coil in Raiway siding areas near JB No-19 is repaired. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143488 | Closed | DAS DARSHAN | 2026-08-10 | Boundary Wall - The boundary wall requires civil repair at some places along with wall painting. The concertina coil installed along the periphery is intact, except in Raiway siding areas near JB No-19. | 3.16 | Earth pits / boundary / vegetation control checked | 1292 | LUCKNOW DEPOT | Concertina coil in Raiway siding areas near JB No-19 needs to be attended immediately. | SOD | Marketing | NCR | 2026-07-30 | THIRD PARTY ERRORS | 9 | PROCESS SAFETY | S3 | F3 | 2026-07-30 | AUD-2026-06-2000013451ACN-2026-07-4000143488 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143488 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143488 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013451ACN-2026-07-4000143488 | AUD-2026-06-2000013451ACN-2026-07-4000143488 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-07 | lock number HE31703 of TT UP32EN7345 was sent for inspection and report says that there is no such case of tampering. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122658 | Closed | DAS DARSHAN | 2026-08-07 | EM lock SOP compliance verified at field and found to be being followed. TT no UP30AT4511 & UP32JN7262 checked with unauthorised Key and lock did not open. Checking of TT locks done with intelligent key. One lock of TT UP32EN7345 lock number HE31703 found suspected. | 3.5 | EM Lock SOP compliance verified | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122658 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122658 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122658 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122658 | AUD-2026-03-2000011009ACN-2026-03-4000122658 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-10 | The Standard Operating Procedures (SOPs) for HCD operations is displayed. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143495 | Closed | DAS DARSHAN | 2026-08-10 | Standard Operating Procedures (SOPs) for HCD operations not displayed near HCD's. Additionally, the drain flow direction scheme should be prominently displayed for operational awareness | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Display the Standard Operating Procedures (SOPs) for HCD operations and the drain flow direction scheme at prominent places to enhance operational awareness and facilitate effective emergency response. | SOD | Marketing | NCR | 2026-07-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-30 | AUD-2026-06-2000013451ACN-2026-07-4000143495 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143495 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143495 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143495 | AUD-2026-06-2000013451ACN-2026-07-4000143495 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-19 | A pipeline is directly connected from the sump of VRU to the drainage route of ETP to ensure effective drainage of spilled product,if any. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143492 | Closed | DAS DARSHAN | 2026-08-19 | The drain depth in the vicinity of the Ethanol Gantry is inadequate. The drains should be deepened and provided with an appropriateslope to ensure effective drainage of spilled product, if any. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Deepen the drains in the Ethanol Gantry area and provide adequate slope to ensure effective drainage and safe handling of accidental product spillages. | SOD | Marketing | NCR | 2026-08-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143492 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143492 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143492 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143492 | AUD-2026-06-2000013451ACN-2026-07-4000143492 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-10 | The damaged earthpit chamber has been repaired and the cables are laid properly near boundary wall. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122663 | Closed | DAS DARSHAN | 2026-08-10 | 1. Security & Admin Blocks: ok 2. Tank Farm: Emergency drain checked for TK6, found satisfactory. Pontoon P-02 & P-04 checked for TK06 and found good. Seals checked between P-06 P-07 and P-11 P-12. Found good. 3. PMCC room: Electrical panel: back light sheet tobe provided in Panel MCC-4, height to be increased to cover bus bar. Meter room: Creepers to be cut in transformer yard. Training to be imparted to electrician. 4. Pump house: Ok 5. Siding: One EP Chamber found damaged, cable to be laid properly near boundary wall. 6. Control room: Ok | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Corrective action to be taken. | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122663 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122663 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122663 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122663 | AUD-2026-03-2000011009ACN-2026-03-4000122663 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-10 | The foundation of the Ethanol Pump is restored to maintain structural integrity and safe operation. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143494 | Closed | DAS DARSHAN | 2026-08-10 | The foundation of the Ethanol Pump is found to be deteriorated and requires repair/restoration to maintain structural integrity andsafe operation. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Repair and restore the deteriorated foundation of the Ethanol Pump to maintain structural stability, equipment reliability, and safe operation. | SOD | Marketing | NCR | 2026-08-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013451ACN-2026-07-4000143494 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143494 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143494 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143494 | AUD-2026-06-2000013451ACN-2026-07-4000143494 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 54
VED PRAKASH | 2026-09-09 | DAS DARSHAN | 2026-08-10 | Scrap of cables, UPS, IT assets, lights, Top loading arm etc disposed off in 2 lots. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122667 | Closed | DAS DARSHAN | 2026-08-10 | Location to identify and segregate scrap available in store room. Scrap like defective valves, cables, TAS panel, UPS, IT assets, lights, Top loading arm etc are available for disposal. Location has been given 7 days’ time to prepare RFD. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1292 | LUCKNOW DEPOT | Corrective action shall be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122667 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122667 | 2026-09-03 | 46.7538 | 373 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122667 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122667 | AUD-2026-03-2000011009ACN-2026-03-4000122667 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Budget has been reviewed and necessary re-appropriation within the location has been initiated. Additional budget requirement has also been projected to HQO with proper justification for approval. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125704 | Closed | MD KASHIF | 2026-09-08 | Additional MEB budget in M&R CE | 1.5 | HQO / Zonal support required identified | 1742 | BOKARO DEPOT | Advised for shifting of budget within location & also project the addl. Budget required from HQO with full justification | SOD | Marketing | PZR | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 12 | ASSET INTEGRITY | S3 | F4 | 2026-03-15 | AUD-2026-03-2000010870ACN-2026-03-4000125704 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125704 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125704 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010870ACN-2026-03-4000125704 | AUD-2026-03-2000010870ACN-2026-03-4000125704 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Planning Officer and other officers carry out random checks of TTs and ensure availability of at least one serviceable fire extinguisher in each TT before allowing movement. The same is being followed by security personnels for sustained compliance. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125712 | Closed | MD KASHIF | 2026-09-08 | Found Okay . | 2.14 | TT crew fire extinguisher usage checked | 1742 | BOKARO DEPOT | Advised planning officer to check for all TTs on random basis and use atleast one TT Fire ext. | SOD | Marketing | PZR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125712 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125712 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125712 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125712 | AUD-2026-03-2000010870ACN-2026-03-4000125712 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | It is being addressed under fit for road campaign. Eye test being done | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125713 | Closed | MD KASHIF | 2026-08-10 | Equipment not available in location. | 2.16 | Eyesight / colour-blindness awareness checked | 1742 | BOKARO DEPOT | LIC advised to procure the same immediately and advise security to check randomly | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125713 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125713 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125713 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125713 | AUD-2026-03-2000010870ACN-2026-03-4000125713 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | All observations of fire drills are being implemented & complied with | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125706 | Closed | MD KASHIF | 2026-08-10 | Location is falls under Double contingency . Spillage scenerio in valve of one of the tank created in mock drill on 29.1.26 | 2.2 | Double contingency scenario simulated; observations recorded | 1742 | BOKARO DEPOT | 1. improvement in action taken during spillage scenerio by the team 2. Usage of PA system during drill by leader 3. some safetyitems not available in emergency trolley 4. delay in action by rescue team | SOD | Marketing | PZR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125706 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125706 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125706 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010870ACN-2026-03-4000125706 | AUD-2026-03-2000010870ACN-2026-03-4000125706 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Wild vegetation along the boundary wall has been cleared and regular monitoring has been instituted to prevent recurrence. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125709 | Closed | MD KASHIF | 2026-09-08 | CCTV footage checked and found stoarge of footage 93 day. Some portion of boundary wall is covered with wild trees | 2.6 | CCTV functioning checked | 1742 | BOKARO DEPOT | Location advised to clear all wild plants from boundary wall | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125709 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125709 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125709 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125709 | AUD-2026-03-2000010870ACN-2026-03-4000125709 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | The issue has been taken up with the VA vendor and necessary corrective action has been initiated. System is restored and functionality found OK. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125710 | Closed | MD KASHIF | 2026-09-08 | Location is facing false VA alerts for spillages , wheel chokes | 2.7 | VA alerts checked / analysed | 1742 | BOKARO DEPOT | Location advised to write to VA vendor and get the issue resolved | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125710 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125710 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125710 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125710 | AUD-2026-03-2000010870ACN-2026-03-4000125710 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Painting requirements have been identified and additional budget has been sought. Painting work will be taken up on priority upon budget availability. Touch up painting being done on regular basis. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125717 | Closed | MD KASHIF | 2026-09-08 | Main entrance area , gates , office building , security room , planning room required painting to have good ambience of location | 3.15 | Housekeeping & PPE usage checked | 1742 | BOKARO DEPOT | Location advised to carry out painting with addl. Budget sought | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125717 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125717 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125717 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125717 | AUD-2026-03-2000010870ACN-2026-03-4000125717 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Housekeeping activities are being closely monitored and the housekeeping contractor has been instructed to ensure compliance with the prescribed housekeeping standards. Regular follow-up is being carried out by the location. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125718 | Closed | MD KASHIF | 2026-09-08 | Housekeeping in operation area , siding area needs improvement | 3.16 | Earth pits / boundary / vegetation control checked | 1742 | BOKARO DEPOT | Special focus on this aspect to be given by location by strict follow up on housekeeping contractor | SOD | Marketing | PZR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010870ACN-2026-03-4000125718 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125718 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125718 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125718 | AUD-2026-03-2000010870ACN-2026-03-4000125718 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | VTS deviations are being regularly highlighted during transporter meetings and gate meetings to improve awareness and ensure strictcompliance. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125714 | Closed | MD KASHIF | 2026-09-08 | Deviation mostly related to night driving , speed voilation during return trip , route deviation , Devise tampering, etc found | 3.3 | VTS deviations reviewed | 1742 | BOKARO DEPOT | These VTS deviations to be discussed in transporter meet, gate meetings | SOD | Marketing | PZR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125714 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125714 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125714 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010870ACN-2026-03-4000125714 | AUD-2026-03-2000010870ACN-2026-03-4000125714 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | all applicable locks through the intelligent key system are checked and maintain proper records of the checks. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125715 | Closed | MD KASHIF | 2026-09-08 | 10 nos. TTs checked with intelliegnt key and all locks found okay | 3.5 | EM Lock SOP compliance verified | 1742 | BOKARO DEPOT | advised LIC to check all locks using intelligent key and have record | SOD | Marketing | PZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 10 | ASSET INTEGRITY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125715 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125715 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125715 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010870ACN-2026-03-4000125715 | AUD-2026-03-2000010870ACN-2026-03-4000125715 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | The improvement in ethanol stock loss is being sustained through enhanced verification of TT calibration and closer monitoring of ethanol receipts/dispatches. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125716 | Closed | MD KASHIF | 2026-09-08 | Stock losses in ethanol receipt checked | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1742 | BOKARO DEPOT | Stock loss in ethanol has come down in last 2-3 months after location advised to increase checking of calibration of ethanol TTs | SOD | Marketing | PZR | 2026-04-30 | THIRD PARTY ERRORS | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125716 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125716 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125716 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125716 | AUD-2026-03-2000010870ACN-2026-03-4000125716 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Disposal of the identified tank has been taken up on priority. Housekeeping and painting requirements of the main gate, office building and planning room have also been identified for necessary action and being followed. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125720 | Closed | MD KASHIF | 2026-09-08 | Round taken and found 1 scrap tank , calibration shed housekeeping , siding area housekeeping , ect . Also main entrance & office building paint condition bad | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1742 | BOKARO DEPOT | Location advised for disposal of tank and improve housekeeping & painting of main gate & office building , planning room to be done | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125720 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125720 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125720 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010870ACN-2026-03-4000125720 | AUD-2026-03-2000010870ACN-2026-03-4000125720 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 54
|  | MD KASHIF | 2026-08-10 | - | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125723 | Open | MD KASHIF | 2026-08-10 | Few TTs found operating without fire screen or improper screen | 6.1 | Safety Fittings -TT | 1742 | BOKARO DEPOT | Advised location to immediately inform TPT/DCT to provide the same & give them 1 week time | SOD | Marketing | PZR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125723 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125723 | 2026-09-19 10:00 | 30.3372 | 241 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125723 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010870ACN-2026-03-4000125723 |  | AUD-2026-03-2000010870ACN-2026-03-4000125723 | 21 |  | 26 | 80 | 1 | 1 | 35
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Required testing/inspection status has been updated on the panel body and records are being maintained accordingly. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-06-4000136343 | Closed | MD KASHIF | 2026-09-08 | Electrical system: Relay setting testing reportedly done in Dec 25, but the same not updated on body of panels. | 6.2 | Quarterly Inspection | 1742 | BOKARO DEPOT | Testing to the updated on the panel body. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136343 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136343 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136343 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000136343 | AUD-2026-06-2000012744ACN-2026-06-4000136343 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Registers are being reviewed daily basis and signature is being done. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26QUARTERLY INSPECTION | ACN-2026-06-4000137717 | Closed | MD KASHIF | 2026-08-10 | Officers signature were missing | 6.26 | Quarterly Inspection | 1742 | BOKARO DEPOT | Register Review by officers needs to be done regularly. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137717 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137717 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137717 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137717 | AUD-2026-06-2000012744ACN-2026-06-4000137717 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Record keeping training is being regularly given. Security supervisor, security agency is being counselled on regular basis. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27QUARTERLY INSPECTION | ACN-2026-06-4000137718 | Closed | MD KASHIF | 2026-08-10 | Blank space were found in the register which needs to stiken off | 6.27 | Quarterly Inspection | 1742 | BOKARO DEPOT | Register Review by officers needs to be done regularly.Alos to sensitize the guards on propoer eecord keeping.. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137718 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137718 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137718 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137718 | AUD-2026-06-2000012744ACN-2026-06-4000137718 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Being ensured. SOP being followed. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.30QUARTERLY INSPECTION | ACN-2026-06-4000137720 | Closed | MD KASHIF | 2026-08-10 | Tankers taken inside for verification in case of any abnormality are staying inside for more than 1 day. To be avoided. | 6.30 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to release the tankers in the shortest possible time. Tanker not to be inside depot fro more than 24 hrs. | SOD | Marketing | PZR | 2026-07-15 | FATIGUE AND STRESS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137720 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137720 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137720 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137720 | AUD-2026-06-2000012744ACN-2026-06-4000137720 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Night patrolling has been reinforced and Safety Officer/LIC have been instructed to ensure regular patrolling with proper recordingin the prescribed register. Time stamping system available and functional. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.32QUARTERLY INSPECTION | ACN-2026-06-4000137722 | Closed | MD KASHIF | 2026-09-08 | CCTV footage review: Not footage available for guards patrolling in night. 2:00 AM to 4:00 AM | 6.32 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer and LIC to ensure patrolling during night hours and propoer record of the same to be maintained. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137722 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137722 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137722 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137722 | AUD-2026-06-2000012744ACN-2026-06-4000137722 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Guard patrolling system available. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.34QUARTERLY INSPECTION | ACN-2026-06-4000137724 | Closed | MD KASHIF | 2026-09-08 | 7 nos. out of 15 RFID readers used for tagging during patrol are non functional. | 6.34 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety offfice to ensure replacment of readers immediately. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137724 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137724 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137724 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137724 | AUD-2026-06-2000012744ACN-2026-06-4000137724 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Guard patrolling unit available. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.35QUARTERLY INSPECTION | ACN-2026-06-4000137725 | Closed | MD KASHIF | 2026-09-08 | NO manual record available for patrol in case RFID readers are not functional. | 6.35 | Quarterly Inspection | 1742 | BOKARO DEPOT | In case of delay in RFID reader replacement. Proper manual record to be mainted and acknowledged by officer. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137725 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137725 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137725 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137725 | AUD-2026-06-2000012744ACN-2026-06-4000137725 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | CCTV footage is observed on daily basis. Same being reviewed by Safety officer for compliances. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.36QUARTERLY INSPECTION | ACN-2026-06-4000137726 | Closed | MD KASHIF | 2026-08-10 | Security supervisor is not regularly monitoring the CCTV footage. | 6.36 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer to sensitized the supervisior to review the CCTV footage regularly. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137726 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137726 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137726 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137726 | AUD-2026-06-2000012744ACN-2026-06-4000137726 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | No action required | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.39QUARTERLY INSPECTION | ACN-2026-06-4000137729 | Closed | MD KASHIF | 2026-08-10 | Strainer cleaning for TLF pump house was established for 9/4/26. | 6.39 | Quarterly Inspection | 1742 | BOKARO DEPOT | OK | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137729 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137729 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137729 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137729 | AUD-2026-06-2000012744ACN-2026-06-4000137729 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Being ensured. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.40QUARTERLY INSPECTION | ACN-2026-06-4000137730 | Closed | MD KASHIF | 2026-08-10 | Strainer cleaning for Fire pump house could not be established for 7/4/26. | 6.40 | Quarterly Inspection | 1742 | BOKARO DEPOT | Strainer cleaning to be recorded and produced when reviewed. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137730 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137730 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137730 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137730 | AUD-2026-06-2000012744ACN-2026-06-4000137730 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Same being ensure timely completion and signing of all closure forms. Compliance is being monitored. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.41QUARTERLY INSPECTION | ACN-2026-06-4000137731 | Closed | MD KASHIF | 2026-09-08 | Work Permit: LIC signature is missing on the work permit for activities that were completed. | 6.41 | Quarterly Inspection | 1742 | BOKARO DEPOT | LIC to ensure the closure forms are signed on time. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137731 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137731 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137731 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137731 | AUD-2026-06-2000012744ACN-2026-06-4000137731 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | tanker validation is witnessed by the designated officers and proper records are maintained. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.42QUARTERLY INSPECTION | ACN-2026-06-4000137732 | Closed | MD KASHIF | 2026-09-08 | CCTV Footage for caliberation shed: NO officer was witnessing the validation of the tankers being done. | 6.42 | Quarterly Inspection | 1742 | BOKARO DEPOT | LIC to ensure officers are witness the validation of tankers. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137732 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137732 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137732 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137732 | AUD-2026-06-2000012744ACN-2026-06-4000137732 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | The facility is not under the control of HPCL neither it is operated by HPCL. Hence complied. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-06-4000136345 | Closed | MD KASHIF | 2026-09-08 | Electrical system: GO switch of electrical supply is located outside location. It is operated by utility supplier. There are no earthpits in that area. Location needs to take up with electricity supplier. | 6.4 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location needs to take up with electricity supplier for earth pits. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136345 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136345 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136345 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000136345 | AUD-2026-06-2000012744ACN-2026-06-4000136345 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-09-08 | Drain valves are being kept locked at all times. Necessary arrangements for quick shut-off and proper locking of the body valve arebeing ensured. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-06-4000136346 | Closed | MD KASHIF | 2026-09-08 |  | 6.5 | Quarterly Inspection | 1742 | BOKARO DEPOT | Ensure locking at all times for drain valve. Valve needs to be quick shut off type. Propoer locking arrangement to be provided to body valve. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136346 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136346 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136346 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000136346 | AUD-2026-06-2000012744ACN-2026-06-4000136346 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Mud and vegetation around TK-206 have been removed and regular housekeeping has been reinforced to prevent recurrence. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-06-4000136347 | Closed | MD KASHIF | 2026-09-08 | Tankfarm: Green vegetation on deposited mud of drain inside dyke of Tk 206. | 6.6 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure removal of mud and vegetation of TK 206. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136347 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136347 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136347 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000136347 | AUD-2026-06-2000012744ACN-2026-06-4000136347 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Vegetation around TK-202 has been cleared and periodic monitoring/housekeeping has been instituted. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-06-4000136348 | Closed | MD KASHIF | 2026-09-08 | Tankfarm: Vegetation growth found in aprons of 202. | 6.7 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure removal of vegetation of TK 202. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136348 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136348 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136348 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000136348 | AUD-2026-06-2000012744ACN-2026-06-4000136348 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
MAZUMDER SAUVIK | 2026-09-09 | MD KASHIF | 2026-08-10 | Being ensured. Night patrolling by security guards has been reinforced, particularly in critical and vulnerable areas. Proper patrolling records are being maintained and periodically reviewed by the concerned officers. Guard patrolling system available. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-06-4000137700 | Closed | MD KASHIF | 2026-09-08 | Tokens with RFID tag to be used security guards during Night patrol. CCTV footage does not show guards on patrol during 2:00 AM to 4:00 AM. | 6.9 | Quarterly Inspection | 1742 | BOKARO DEPOT | Loaction to ensure propoer patroling is being done by the guiards espicially during the night hours. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137700 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137700 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137700 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137700 | AUD-2026-06-2000012744ACN-2026-06-4000137700 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
|  | MD KASHIF | 2026-08-10 | Being ensured. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-06-4000136349 | Open | MD KASHIF | 2026-08-10 | Tankfarm: Difference observed in water level in TFMS Vs Actual Tank dip TK 207 TAS dip Nil actual 9.4 cm. Auto Temp 30.3 Deg cent Actual 33 Deg Cent | 6.8 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location TAS to ensure there in no difference in TAS and actuals | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136349 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136349 | 2026-09-19 10:00 | 30.3372 | 317 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136349 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012744ACN-2026-06-4000136349 |  | AUD-2026-06-2000012744ACN-2026-06-4000136349 | 21 |  | 27 | 80 | 1 | 1 | 46
SINGWAL DEEPAK | 2026-09-10 | GEETE DEVASHISH | 2026-09-01 | access control system at Gwalior IRD 1) License area access control system is fully functional for both Entry and Exit control after replacement of faulty reader units. 2) There are two access turnstiles after security at Main gate entry. 01 turnstile is fully functional for both entry and exit control. However, exit reader of 2nd turnstile is taken by vendor for repairing while Entry control is functional. Since, at main gate both Entry and Exit is controlled through functional access control system, the faulty reader is not creating any bypass/violation and we are following up with the vendor for earliest repairing of faulty reader. Hence the observation of making the access control system functional at Gwalior IRD can be closed. | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127197 | Closed | SINGWAL DEEPAK | 2026-09-01 | Access control systems is available and working. However, one of the access detection module is faulty and taken by vendor for repair and no replacement has been provided till date. | 2.8 | Access control systems checked | 1435 | GWALIOR DEPOT | Location is advised to take up with vendor to make faulty Access control system functional. | SOD | Marketing | CEN | 2026-04-30 | THIRD PARTY ERRORS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011237ACN-2026-03-4000127197 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127197 | 2026-08-22 19:00 | 57.9622 | 374 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127197 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011237ACN-2026-03-4000127197 | AUD-2026-03-2000011237ACN-2026-03-4000127197 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 54
SINGWAL DEEPAK | 2026-09-10 | GEETE DEVASHISH | 2026-09-01 | Scrap disposal proposal has already been initiated by Retail team and the proposals are at HQO level for final approval. Hence thisrecommendation of coordination with retail team for scrap disposal can be closed. | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127301 | Closed | SINGWAL DEEPAK | 2026-09-01 | Reviewed Scrap available at location, majorly consisting of Retail DU unit lying at location. RFD has already been initiated by Retail team. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1435 | GWALIOR DEPOT | Location to coordinate with Retail team for disposal of DU unit placed at Depot. | SOD | Marketing | CEN | 2026-06-30 | POOR COMMUNICATION | 1 | ENVIRONMENTAL | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011237ACN-2026-03-4000127301 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127301 | 2026-08-22 19:00 | 57.9622 | 374 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127301 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011237ACN-2026-03-4000127301 | AUD-2026-03-2000011237ACN-2026-03-4000127301 | 21 | 21 | 26 | 80 | 2 | 2 | 44 | 54
|  |  |  | Cleaning of Oil traces is done, and area is maintained clean | LONI TERMINAL VISIT 25.07.2026 | 2026-07-25 | AUD-2026-09-2000017901 | 2026-07-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152219 | Open | JERRY JOSEPH | 2026-09-10 | Oil traces are observed near pump house piping | 6.1 |  | 1584 | LONI TERMINAL | To be checked and kept clean. | SOD | Marketing | WZ | 2026-08-10 |  | 4 |  | S2 | F2 | 2026-08-10 | AUD-2026-09-2000017901ACN-2026-09-4000152219 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017901ACN-2026-09-4000152219 | 2026-10-15 | 4.7538 | 343 | >20 | AUD-2026-09-2000017901 - ACN-2026-09-4000152219 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017901ACN-2026-09-4000152219 |  | AUD-2026-09-2000017901ACN-2026-09-4000152219 | 21 |  | 27 | 80 | 18 | 18 | 49
|  |  |  | Works are in progress. Plate Supply is awaited from the Vendor. | LONI TERMINAL VISIT 25.07.2026 | 2026-07-25 | AUD-2026-09-2000017901 | 2026-07-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152220 | Open | JERRY JOSEPH | 2026-09-10 | Tank Revamp project works status is checked and works are in progress | 6.2 |  | 1584 | LONI TERMINAL | Tank Revamp project to be completed on priority. | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S4 | F1 | 2027-03-31 | AUD-2026-09-2000017901ACN-2026-09-4000152220 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017901ACN-2026-09-4000152220 | 2026-10-15 | 4.7538 | 576 | >20 | AUD-2026-09-2000017901 - ACN-2026-09-4000152220 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017901ACN-2026-09-4000152220 |  | AUD-2026-09-2000017901ACN-2026-09-4000152220 | 21 |  | 27 | 80 | 18 | 18 | 83
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152225 | Open |  |  | Reviewed .Some deviations noted ex. daily gate meeting not conducted | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1585 | MAHUL TERMINAL | 100% Compliance required | SOD | Marketing | WZ | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-07-2000016410ACN-2026-09-4000152225 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152225 | 2026-10-17 | 2.7538 | 363 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152225 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152225 |  | AUD-2026-07-2000016410ACN-2026-09-4000152225 | 21 |  | 27 | 80 | 28 | 28 | 52
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152227 | Open |  |  | CCTV with VA not availble at location. | 2.7 | VA alerts checked / analysed | 1585 | MAHUL TERMINAL | To propose CCTV Projects in NPCB 2026-27 | SOD | Marketing | WZ | 2027-12-31 |  | 4 |  | S2 | F2 | 2027-12-31 | AUD-2026-07-2000016410ACN-2026-09-4000152227 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152227 | 2026-10-17 | 2.7538 | 851 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152227 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152227 |  | AUD-2026-07-2000016410ACN-2026-09-4000152227 | 21 |  | 27 | 80 | 28 | 28 | 122
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152228 | Open |  |  | Housekeeping to be improved near Tank wagon gantry area. | 3.15 | Housekeeping & PPE usage checked | 1585 | MAHUL TERMINAL | To complete site clearance activity | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152228 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152228 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152228 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152228 |  | AUD-2026-07-2000016410ACN-2026-09-4000152228 | 21 |  | 27 | 80 | 28 | 28 | 57
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152229 | Open |  |  | Erathpit condition to be revived and additional Eatthpits to be provided as per requirement | 3.16 | Earth pits / boundary / vegetation control checked | 1585 | MAHUL TERMINAL | To construct Earthpit and review. | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152229 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152229 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152229 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152229 |  | AUD-2026-07-2000016410ACN-2026-09-4000152229 | 21 |  | 27 | 80 | 28 | 28 | 57
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152230 | Open |  |  | YES. VRU MOC still pending approval | 3.17 | MOC status reviewed | 1585 | MAHUL TERMINAL | Location to submit to Zone along with VRU operations SOP | SOD | Marketing | WZ | 2026-08-30 |  | 4 |  | S2 | F2 | 2026-08-30 | AUD-2026-07-2000016410ACN-2026-09-4000152230 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152230 | 2026-10-17 | 2.7538 | 363 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152230 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152230 |  | AUD-2026-07-2000016410ACN-2026-09-4000152230 | 21 |  | 27 | 80 | 28 | 28 | 52
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152233 | Open |  |  | Reviewed and advised the team to expedite the job | 4.2 | Maintenance activities reviewed | 1585 | MAHUL TERMINAL | All Tank repair job to complete within provided Timelines | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-07-2000016410ACN-2026-09-4000152233 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152233 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152233 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152233 |  | AUD-2026-07-2000016410ACN-2026-09-4000152233 | 21 |  | 27 | 80 | 28 | 28 | 83
[5 empty] | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152235 | Open |  |  | RFD to be initiated for Miscellaeous Scrap and Scrap Tanks to be handed over to MR for further disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1585 | MAHUL TERMINAL | To initiate RFD Activities immediately. | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-07-2000016410ACN-2026-09-4000152235 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152235 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152235 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152235 |  | AUD-2026-07-2000016410ACN-2026-09-4000152235 | 21 |  | 27 | 80 | 28 | 28 | 83
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-08-21 | Proper Housekeeping is being maintained by clearing all debris | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125569 | Closed | AGARWAL VIPUL | 2026-03-18 | Housekeeping - Housekeeping of the location is found to be satisfactory with some areas requireing major upkeep which were discussed during field round with location team. | 3.15 | Housekeeping & PPE usage checked | 1216 | BAHADURGARH TERMINAL | Housekeeping to be properly maintained. | SOD | Marketing | NZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125569 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125569 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125569 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125569 | AUD-2026-03-2000011128ACN-2026-03-4000125569 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-08-21 | Henceforth same shall be ensured. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125570 | Closed | AGARWAL VIPUL | 2026-03-18 | Earth Pits - Total 456 Nos of Earth pits are there at the location. Earth Pit No 20 & 68 Checked and Found Individual and Grid Reading as mentioned Individual Reading of EP 20 - 1.5 Ω Grid Reading of EP-20 - 0.54 Ω Individual Reading of EP 68 - 0.98 Ω GridReading of EP-68 - 0.41 Ω While revieweing the work permit it is observed that location has not taken Electrical Isolation / energization permit for earthpits connected to Electical equipment. | 3.16 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | A separate Electrical Isolation/Energization Permit shall be obtained while carrying out half-yearly checks of earth pits connectedto electrical equipment. The CWP and the Electrical Isolation/Energization Permit shall also be properly linked. | SOD | Marketing | NZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125570 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125570 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125570 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125570 | AUD-2026-03-2000011128ACN-2026-03-4000125570 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-08-21 | Anti weed spary is being applied to restrict growth | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125572 | Closed | AGARWAL VIPUL | 2026-03-18 | Vegetation Control - At some places Encroaching/Overgrown vegetation observed. Vegetaion control measures to be ensured | 3.16 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | Vegetation control measures to be taken by the location | SOD | Marketing | NZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125572 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125572 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125572 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125572 | AUD-2026-03-2000011128ACN-2026-03-4000125572 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-09-08 | Watsapp Group already available. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125577 | Closed | ANKIT KUMAR | 2026-09-08 | a. VTS blocking of TT : DCT transporters enquired about issue of VTS blocking. GM O&D suggested them that TT if loaded does not follow approved route, it will get blocked. If transporters feel there is issue with approved route, they may get it changed from fieldofficer with the help of terminal officials. b. Late reporting of DCT : DCT Transporters were advised to get their TT reported by 3:30 Pm , so that Terminal operation can be closed timely and night driving can be avoided. | 3.2 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1216 | BAHADURGARH TERMINAL | Whatsapp group to be created for sharing of information. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125577 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125577 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125577 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125577 | AUD-2026-03-2000011128ACN-2026-03-4000125577 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-09-08 | 5% VTS checking record is being maintained | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125564 | Closed | ANKIT KUMAR | 2026-09-08 | Check for 5% VTS deviation is being done by the location and has been reviewed during visit. Proper record to be maintained | 3.3 | VTS deviations reviewed | 1216 | BAHADURGARH TERMINAL | Proper records to be maintained | SOD | Marketing | NZ | 2026-03-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-03-2000011128ACN-2026-03-4000125564 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125564 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125564 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125564 | AUD-2026-03-2000011128ACN-2026-03-4000125564 | 21 | 21 | 26 | 80 | 9 | 9 | 30 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-09-08 | 5% EM Locks mothly checking record being maintained | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125565 | Closed | ANKIT KUMAR | 2026-09-08 | Check for 5% EM locks on daily basis and all locks on monthly basis , proper record to be maintained. | 3.5 | EM Lock SOP compliance verified | 1216 | BAHADURGARH TERMINAL | Proper record to be maintained. All used locked recovered from TTs to be sent back to sterna for refurbishment and rechecking of integrity before reissuing to other TTs | SOD | Marketing | NZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011128ACN-2026-03-4000125565 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125565 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125565 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125565 | AUD-2026-03-2000011128ACN-2026-03-4000125565 | 21 | 21 | 26 | 80 | 9 | 9 | 35 | 54
NIMDEO AMIT VINAYAK | 2026-09-10 | ANKIT KUMAR | 2026-08-21 | Same will be ensured henceforth. Control room officers and Operation incharge sensitized. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125566 | Closed | AGARWAL VIPUL | 2026-03-18 | Out of total 4222 tank reconciliations done during the period 1st Oct'25 to 22nd Feb'26, only 306 instances of manual dip entries are there in SAP. Reconciliation based on auto dip was done for 92.75% of tanks during the period. Out of the 306 reconciliations done based on manual dips, 48 instances were for month end reconciliations when manual dip entries were mandated by HQO. 258 instances are pertaining to reconciliations done on manual dips on days other than month ends. Location's control room officers are entering the reasons for manual dip reconciliation at daily day end closing in the google spreadsheet provided by zonal operations | 3.8 | Auto vs Manual reconciliation checked | 1216 | BAHADURGARH TERMINAL | Location to reduce the instance of manual Reconciliation and continue to update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125566 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125566 | 2026-09-05 | 44.7538 | 374 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125566 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125566 | AUD-2026-03-2000011128ACN-2026-03-4000125566 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
KAUSHIK ANIL | 2026-09-11 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | All officers are going around the field on regular basis and checking for irregularties and non-compliances if any. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147877 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Interacted with all Officers on their roles & responsibilities. Emphasised on the need to focus in depth on their respective roles and excel in each area. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1895 | MANGALORE TERMINAL | All officers, irrespective of the profiles they are handling, have to visit all areas of location viz TTG, Ethanol Gantry, Tank Farm, TWG, Area between Railway Gate and Jokkate Gate etc on regular basis and monitor/check for irregularities if any. | SOD | Marketing | SWZ | 2026-08-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ENVIRONMENTAL | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000147877 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147877 | 2026-07-29 17:00 | 82.0455 | 375 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147877 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147877 | AUD-2026-08-2000016271ACN-2026-08-4000147877 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 54
KAUSHIK ANIL | 2026-09-11 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Gaps on either side of TT out gate sealed with chain link fencing and gate provided for controlled use. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147881 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Access controls at visitor gate, TT entry gates, jokatte gates are found okay. However, certain gaps near TT out gate are found, which needs to be sealed. | 2.8 | Access control systems checked | 1895 | MANGALORE TERMINAL | Gaps on either side of TT out gate to be sealed with chain link fencing. | SOD | Marketing | SWZ | 2026-08-10 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-10 | AUD-2026-08-2000016271ACN-2026-08-4000147881 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147881 | 2026-07-29 17:00 | 82.0455 | 375 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147881 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147881 | AUD-2026-08-2000016271ACN-2026-08-4000147881 | 21 | 21 | 27 | 80 | 2 | 2 | 49 | 54
KAUSHIK ANIL | 2026-09-11 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Temporary barricade arranged, Follow-up being done with MRPL on regular basis for completion of job. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147885 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | MRPL Compound wall collapsed near TK-27 | 6.1 | Compound wall | 1895 | MANGALORE TERMINAL | Temporary barricade to be arranged at the location where compound wall has collapsed. Follow-up with MRPL to be done for permanent repair works | SOD | Marketing | SWZ | 2026-08-06 | POOR COMMUNICATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-06 | AUD-2026-08-2000016271ACN-2026-08-4000147885 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147885 | 2026-07-29 17:00 | 82.0455 | 375 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147885 | 532 | 8294 | 21 | 8294 | 74 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147885 | AUD-2026-08-2000016271ACN-2026-08-4000147885 | 21 | 21 | 27 | 80 | 2 | 2 | 49 | 54
KAUSHIK ANIL | 2026-09-11 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Cotton waste collected and kept in designated place. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147893 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Cotton waste etc. found in TT Gantry cabin. | 6.9 | Oily waste & Cotton waste | 1895 | MANGALORE TERMINAL | Cotton waste etc. not to be put in TT Gantry cabin. Other unwanted containers if any shall be removed. | SOD | Marketing | SWZ | 2026-08-05 | LACK OF TRAINING OR COMPETENCY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-08-05 | AUD-2026-08-2000016271ACN-2026-08-4000147893 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147893 | 2026-07-29 17:00 | 82.0455 | 375 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147893 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147893 | AUD-2026-08-2000016271ACN-2026-08-4000147893 | 21 | 21 | 27 | 80 | 2 | 2 | 49 | 54
KAUSHIK ANIL | 2026-09-11 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Repairs of 3 nos of Jokkatte Gates and 1 no of Railway gate completed. Projections provided at bottom to bridge gap between gate and ground. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000148002 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | 3 Nos of gates at Jokkatte are not in good condition. | 6.18 | Gate Repair | 1895 | MANGALORE TERMINAL | 3 Nos of Gates at Jokkatte Gate to be repaired | SOD | Marketing | SWZ | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016271ACN-2026-08-4000148002 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000148002 | 2026-07-29 17:00 | 82.0455 | 375 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000148002 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000148002 | AUD-2026-08-2000016271ACN-2026-08-4000148002 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 54
[5 empty] | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152271 | Open |  |  | Yes, Location is advised to expedite closure of all 03 open MDSA Audit observation points. | 1.6 | Expectations clearly communicated to officers | 1457 | INDORE DEPOT | Location is advised to expedite closure of all 03 open MDSA Audit observation points. | SOD | Marketing | CEN | 2026-10-31 |  | 4 |  | S1 | F4 | 2026-10-31 | AUD-2026-09-2000017752ACN-2026-09-4000152271 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152271 | 2026-09-09 19:00 | 39.9622 | 425 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152271 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152271 |  | AUD-2026-09-2000017752ACN-2026-09-4000152271 | 21 |  | 27 | 80 | 0 | -3 | 61
[5 empty] | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152272 | Open |  |  | Last fire drill was carried out on 27.08.2026 at ETP Area. Also, surprised drill was carried out during location visit on 08.09.2024 at TK-24. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1457 | INDORE DEPOT | Following are the Observations during surprise Fire Drill: 1) The response time can be further improved. 2) To bring more clarityin job role of each fire fighting team. | SOD | Marketing | CEN | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152272 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152272 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152272 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152272 |  | AUD-2026-09-2000017752ACN-2026-09-4000152272 | 21 |  | 27 | 80 | 0 | -3 | 57
[5 empty] | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152274 | Open |  |  | Lux level checked and found to be inadequate at Tank Manifold Area, TLF Pump House, Transformer Yard Area and Battery Room. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1457 | INDORE DEPOT | Additional fixtures to be provided at the mentioned locations to improve the lux level and to meet OISD norms. | SOD | Marketing | CEN | 2026-10-15 |  | 4 |  | S1 | F4 | 2026-10-15 | AUD-2026-09-2000017752ACN-2026-09-4000152274 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152274 | 2026-09-09 19:00 | 39.9622 | 409 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152274 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152274 |  | AUD-2026-09-2000017752ACN-2026-09-4000152274 | 21 |  | 27 | 80 | 0 | -3 | 59
[5 empty] | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152283 | Open |  |  | Checked and found to be okay. Vegetation to be removed. | 3.16 | Earth pits / boundary / vegetation control checked | 1457 | INDORE DEPOT | Vegetation to be removed. Earth pit board to be replaced with new one with revised date of testing/validity. | SOD | Marketing | CEN | 2026-10-15 |  | 4 |  | S1 | F4 | 2026-10-15 | AUD-2026-09-2000017752ACN-2026-09-4000152283 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152283 | 2026-09-09 19:00 | 39.9622 | 409 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152283 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152283 |  | AUD-2026-09-2000017752ACN-2026-09-4000152283 | 21 |  | 27 | 80 | 0 | -3 | 59
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152020 | Open |  |  | Tot. 60 no of CCTVs are available at the location out of which only 59 CCTVs are working. For Remaining 1 no of CCTV sent to the AMC vendor for repair vide Gate Pass Nos. 11319-R-017143 and 11319-R-017898 dated 12.06.2026. 92 days CCTV recording was available & regular basis reviews were made and records maintained. | 2.6 | CCTV functioning checked | 1319 | MUGHALSARAI DEPOT | The non-functional CCTV cameras to be restored at the earliest. | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017403ACN-2026-09-4000152020 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152020 | 2026-09-02 17:30 | 47.0247 | 486 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152020 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152020 |  | AUD-2026-09-2000017403ACN-2026-09-4000152020 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152021 | Open |  |  | During the Visit Access control at main gate was checked and found that CBAC Systen was fully functional along with Biomatric operational at Main gate and Control room. The PAMS visitor management system is in place for all the visitors entrering the premises. However, the CBAC turnstile at the Licensed Area entry point was found non-functional and found in a collapsed position, rendering theaccess control arrangement ineffective. As an interim security measure, one security guard has been deployed at the location. | 2.8 | Access control systems checked | 1319 | MUGHALSARAI DEPOT | Location to take corrective action at the earliest and put CBAC system in use at licensed area entry point. | SOD | Marketing | NCR | 2026-10-31 |  | 2 |  | S2 | F1 | 2026-10-31 | AUD-2026-09-2000017403ACN-2026-09-4000152021 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152021 | 2026-09-02 17:30 | 47.0247 | 425 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152021 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152021 |  | AUD-2026-09-2000017403ACN-2026-09-4000152021 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152022 | Open |  |  | OISD - The last OISD audit was conducted during July'25. A total of 26 observations were raised, 25 are complied. T4S - The last T4S audit was conducted during May'26. A total of 20 observations were raised, 13 observations complied. MDSA/Comprehensive Audit - The last Comprehensive audit was conducted during March'26. A total of 58 observations were raised, 24 observations complied. SSA -Last SSA was conducted during Sep'25. A total of 35 observations were raised, 33 complied HLSA - Last HLSA was conducted in June'26. A total of 13 observations were raised, 10 complied | 3.18 | OISD/MDSA/SSA/T4S/HLSA compliance reviewed | 1319 | MUGHALSARAI DEPOT | Location is advsied to Comply with the audit observation in time bound manner and update compliance status in SAP | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017403ACN-2026-09-4000152022 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152022 | 2026-09-02 17:30 | 47.0247 | 486 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152022 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152022 |  | AUD-2026-09-2000017403ACN-2026-09-4000152022 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152023 | Open |  |  | Air Conditioner of Control room is not effective. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Periodic maintenance and repair of Air conditioning system is to be ensured by the location. | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017403ACN-2026-09-4000152023 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152023 | 2026-09-02 17:30 | 47.0247 | 425 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152023 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152023 |  | AUD-2026-09-2000017403ACN-2026-09-4000152023 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152024 | Open |  |  | During Randon inspection, Only one harness found at Bay no-03 at TT gantry and Calibration tower. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Each bay should be equipped with 2 nos of Safety Harness. Location to comply. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017403ACN-2026-09-4000152024 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152024 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152024 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152024 |  | AUD-2026-09-2000017403ACN-2026-09-4000152024 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152025 | Open |  |  | Tell Tale clock not operational since 2019. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | The Tell-Tale Clock to be made operational on priority to ensure continuous monitoring and recording of security patrols. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017403ACN-2026-09-4000152025 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152025 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152025 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152025 |  | AUD-2026-09-2000017403ACN-2026-09-4000152025 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152026 | Open |  |  | The painting on the above-ground HSD tank was observed to be faded. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Location to comply. | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017403ACN-2026-09-4000152026 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152026 | 2026-09-02 17:30 | 47.0247 | 486 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152026 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152026 |  | AUD-2026-09-2000017403ACN-2026-09-4000152026 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152027 | Open |  |  | At sludge pit/Pond SOP board found faded. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Ensure all boards displayed in the field are inspected for fading and take prompt corrective action. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017403ACN-2026-09-4000152027 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152027 | 2026-09-02 17:30 | 47.0247 | 394 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152027 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152027 |  | AUD-2026-09-2000017403ACN-2026-09-4000152027 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | ZONAL INSPECTION Q2-2026-27 MUGHALSARAI | 2026-09-02 17:30 | AUD-2026-09-2000017403 | 2026-08-31 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152028 | Open |  |  | Various scrap items were observed lying in the Scrap Yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1319 | MUGHALSARAI DEPOT | Scrap to be identified and RFD to be initiated at the earliest. | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017403ACN-2026-09-4000152028 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017403ACN-2026-09-4000152028 | 2026-09-02 17:30 | 47.0247 | 486 | >20 | AUD-2026-09-2000017403 - ACN-2026-09-4000152028 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017403ACN-2026-09-4000152028 |  | AUD-2026-09-2000017403ACN-2026-09-4000152028 | 21 |  | 27 | 80 | 1 | 2 | 70
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Sand buckets have been completely filled.Painting job of sand Buckets is under progess | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125579 | Closed | AGARWAL VIPUL | 2026-03-18 | Sand bucket found to be partially filled with sand. Also, paiting is required for sand buckets | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Ensure sand buckets to be filled adequately and painting to be done | SOD | Marketing | NZ | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125579 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125579 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125579 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125579 | AUD-2026-03-2000011128ACN-2026-03-4000125579 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Replaced in the same day | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125580 | Closed | AGARWAL VIPUL | 2026-03-18 | Shower Tie rod to be replaced in Eye wash placed near Licence area entry point | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Shower tie rod to be replaced in Eye wash | SOD | Marketing | NZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125580 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125580 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125580 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125580 | AUD-2026-03-2000011128ACN-2026-03-4000125580 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Spilled oil cleared | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125581 | Closed | AGARWAL VIPUL | 2026-03-18 | Oil spillage found in Bay-03 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Necessary measures should be taken to arrest oil spillage and ensure that the location is maintained as a zero-spill area. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125581 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125581 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125581 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125581 | AUD-2026-03-2000011128ACN-2026-03-4000125581 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | oil soaked soil removed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125582 | Closed | AGARWAL VIPUL | 2026-03-18 | Oil soaked soil observed near Bay-04 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Oil-soaked soil observed near Bay-04 should be removed immediately and the area should be cleaned and restored to prevent contamination and ensure safe housekeeping. | SOD | Marketing | NZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125582 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125582 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125582 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125582 | AUD-2026-03-2000011128ACN-2026-03-4000125582 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Locking nut put in the date of Audit | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125583 | Closed | AGARWAL VIPUL | 2026-03-18 | The locking nut intended to restrict the vertical movement of Foam Monitor No. 95 was observed to be broken. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Locking nut to be placed for proper working of Foam Monitor | SOD | Marketing | NZ | 2026-03-15 | HARSH WORKING CONDITIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125583 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125583 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125583 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125583 | AUD-2026-03-2000011128ACN-2026-03-4000125583 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Cold weld applied and holes attended. Permanent repair attended | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125585 | Closed | ANKIT KUMAR | 2026-08-21 | Pitting corrosion has been observed at several locations on the roof of A/G Tank No. 10. Five pinholes were also identified and temporarily repaired using cold welding. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | A detailed inspection should be carried out and permanent repairs to the tank roof should be undertaken. | SOD | Marketing | NZ | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 2 | ASSET INTEGRITY | S2 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125585 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125585 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125585 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125585 | AUD-2026-03-2000011128ACN-2026-03-4000125585 | 21 | 21 | 26 | 80 | 9 | 9 | 57 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | JB properly fixed and glands installed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125587 | Closed | AGARWAL VIPUL | 2026-03-18 | Junction Box No. CCTV-64 is not properly fixed and proper glands have not been used for termination. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The junction box should be securely fixed and proper glands should be installed to ensure safe and proper termination. | SOD | Marketing | NZ | 2026-03-15 | HARSH WORKING CONDITIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125587 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125587 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125587 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011128ACN-2026-03-4000125587 | AUD-2026-03-2000011128ACN-2026-03-4000125587 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | New SOP board has been placed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125588 | Closed | AGARWAL VIPUL | 2026-03-18 | Near 4 pole structure, SOP board for VCB operation observed to be broken. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The board should be replaced to ensure clear display of operating procedures. | SOD | Marketing | NZ | 2026-03-15 | HARSH WORKING CONDITIONS | 4 | CONTRACTOR SAFETY | S1 | F4 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125588 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125588 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125588 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125588 | AUD-2026-03-2000011128ACN-2026-03-4000125588 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Pump repair completed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125590 | Closed | ANKIT KUMAR | 2026-08-21 | Leakage from the mechanical seal of the MS product pump has been observed. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The pump should be inspected and the mechanical seal should be repaired or replaced to prevent product leakage and ensure safe operation. | SOD | Marketing | NZ | 2026-04-15 | HARSH WORKING CONDITIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000011128ACN-2026-03-4000125590 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125590 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125590 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125590 | AUD-2026-03-2000011128ACN-2026-03-4000125590 | 21 | 21 | 26 | 80 | 9 | 9 | 33 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | All boards installed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125591 | Closed | ANKIT KUMAR | 2026-08-21 | New MSDS to be placed in product pump house | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | MSDS board to be replaced | SOD | Marketing | NZ | 2026-03-31 | HARSH WORKING CONDITIONS | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125591 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125591 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125591 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125591 | AUD-2026-03-2000011128ACN-2026-03-4000125591 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Cup repalced. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125593 | Closed | AGARWAL VIPUL | 2026-03-18 | Leakage from Oil Cup observed in HSD pumps in product pump house | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Leakage from the oil cup observed in the HSD pumps at the Product Pump House should be attended to and rectified to prevent productloss and maintain proper equipment condition. | SOD | Marketing | NZ | 2026-03-15 | HARSH WORKING CONDITIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125593 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125593 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125593 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125593 | AUD-2026-03-2000011128ACN-2026-03-4000125593 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Double isolation valves provided | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125597 | Closed | ANKIT KUMAR | 2026-08-21 | Double isolation is to be provided in Strainer drain line in TT Gantry | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Double isolation should be provided in the strainer drain line at the TT Gantry to enhance operational safety and maintenance flexibility. | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125597 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125597 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125597 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125597 | AUD-2026-03-2000011128ACN-2026-03-4000125597 | 21 | 21 | 26 | 80 | 9 | 9 | 57 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Gland replaced | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125598 | Closed | ANKIT KUMAR | 2026-08-21 | Double compression gland found missing in JB-196 in TT Gantry in Bay no 09 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Double compression gland to be used for ensuring proper cable termination and ingress protection. | SOD | Marketing | NZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125598 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125598 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125598 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125598 | AUD-2026-03-2000011128ACN-2026-03-4000125598 | 21 | 21 | 26 | 80 | 9 | 9 | 57 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Jumper installed | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125599 | Closed | ANKIT KUMAR | 2026-08-21 | Jumper is missing in HSD line after DCV in TT Gantry Bay no-09 | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Jumper should be provided to ensure proper electrical continuity/bonding. | SOD | Marketing | NZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011128ACN-2026-03-4000125599 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125599 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125599 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125599 | AUD-2026-03-2000011128ACN-2026-03-4000125599 | 21 | 21 | 26 | 80 | 9 | 9 | 44 | 54
NIMDEO AMIT VINAYAK | 2026-09-11 | ANKIT KUMAR | 2026-08-21 | Nitrogen cylinder placed securedly. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125601 | Closed | AGARWAL VIPUL | 2026-03-18 | Nitrogen Cylinders in VRU shed found to be lying unattended. It should be fixed and placed to avoid any untowards situation/mishap | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Nitrogen cylinders should be properly secured and placed in designated stands or racks to avoid any untoward incident or mishap. | SOD | Marketing | NZ | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011128ACN-2026-03-4000125601 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125601 | 2026-09-05 | 44.7538 | 375 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125601 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125601 | AUD-2026-03-2000011128ACN-2026-03-4000125601 | 21 | 21 | 26 | 80 | 9 | 9 | 26 | 54
SABLE RONAK MOHANKUMAR | 2026-09-12 | SINGH PREETI | 2026-09-11 | 1. Lights provided in staircase to admin roof. Lux level adequate now. 2. Lights in Battery room in control room rectified, lux level adequate now. Photos attached. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150754 | Closed | SINGH PREETI | 2026-09-11 | 1. No Lights in staircase to admin roof 2. Lights in Battery room in control room not working | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150754 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150754 | 2026-08-22 22:00 | 57.8372 | 376 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150754 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150754 | AUD-2026-08-2000016905ACN-2026-09-4000150754 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 54
SABLE RONAK MOHANKUMAR | 2026-09-12 | SINGH PREETI | 2026-09-05 | All readings have variations within acceptable limits of Gross Dip: ± 3mm, Water Level: ± 5mm, Temp: ± 1 deg. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150758 | Closed | SINGH PREETI | 2026-09-05 | 1. Tank No: TF-9: TAS: Product level: 1691 CM, Water level: 65 mm Temp: 29.2 Manual: Product level: 1688 Cm, Water dip: 65 cm, Temp: 29.50 2. Tank no: TF-17: TAS: Product level: 5889 cm, Water level: 00, temp: 31.2 Manual: Product level: 5887 cm, Water dip: 00, Temp: 30.75 | 3.7 | Inventory physical dip of minimum two tanks taken | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150758 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150758 | 2026-08-22 22:00 | 57.8372 | 376 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150758 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150758 | AUD-2026-08-2000016905ACN-2026-09-4000150758 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 54
SABLE RONAK MOHANKUMAR | 2026-09-12 | SINGH PREETI | 2026-09-04 | ROSOV declared surplus in Asset Management portal as well as SOD SBU site. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150759 | Closed | SINGH PREETI | 2026-09-04 | 1. ROSOV 10” lying in scrap yard, to be declared surplus | 3.9 | Abnormal variations / unused assets reviewed | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150759 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150759 | 2026-08-22 22:00 | 57.8372 | 376 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150759 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150759 | AUD-2026-08-2000016905ACN-2026-09-4000150759 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 54
|  | KUMAR SANJAY | 2026-09-12 | The existing Contract Expired and no Contract TT avialable at location, Hence Meeting cannot be conducted. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152232 | Completed | KUMAR SANJAY | 2026-09-12 | No transporter meeting done in Q4. Location to organise | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1585 | MAHUL TERMINAL | Location to ensure one transporter meet per quarter | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152232 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152232 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152232 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152232 |  | AUD-2026-07-2000016410ACN-2026-09-4000152232 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | KUMAR SANJAY | 2026-09-12 | New Bitumen Road connecting from Ramp to Wagon Gantry construction Completed. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152234 | Completed | KUMAR SANJAY | 2026-09-12 | Bitumen Road near tank Wagon Gantry reviewed .Quick Action to be taken to complete the Project | 4.3 | Project progress reviewed | 1585 | MAHUL TERMINAL | To complete it at the earliest | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152234 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152234 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152234 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152234 |  | AUD-2026-07-2000016410ACN-2026-09-4000152234 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-12 | PCSA Compliance Report is attached. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152231 | Completed | SUNITA | 2026-09-12 | PCSA Audit carried out in Jan26. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1585 | MAHUL TERMINAL | More than 60 points pending compliance | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152231 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152231 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152231 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152231 |  | AUD-2026-07-2000016410ACN-2026-09-4000152231 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-12 | HCD hooter available for all HCD except UG tank Farm, VRU and PH-B. Refer attached test repoprt pof Pentax Engg dt June 2026. New Hooter is procured and installed for UG tank farm as per attached Records. Existingg Spare Hooters of defunct class A tabnks are connected for PH-B and VRU HCDs all Hooters thus functional. 23 ESD availbale at location and are configured with electrical siren Dyke drain and their Hooters are covered under point no. . Henec closed this point. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-09-4000152236 | Completed | SUNITA | 2026-09-12 | Field Hooters not availble for HCD/ESD and Dyke drains | 5.2 | Functioning of all Hooters in control room | 1585 | MAHUL TERMINAL | Location to take NPCB | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-07-2000016410ACN-2026-09-4000152236 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152236 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152236 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152236 |  | AUD-2026-07-2000016410ACN-2026-09-4000152236 | 21 |  | 27 | 80 | 28 | 28 | 83
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-13 | LIC has taken resposibility to ensure for gouding the new officers as well as for knowledge transfer | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125530 | Completed | G RAMADOSS | 2026-03-22 | Interacted openly with all Officers and found them motivated with interest to perfrom well | 1.1 | Interaction with all officers (1–1.5 hrs) | 1991 | CHENNAI TERMINAL | Considering that DPC list published the Location In-Charge (LIC) and senior officers were directed to prioritize comprehensive knowledge sharing. This will ensure seamless operational continuity. | SOD | Marketing | SZ | 2026-03-31 |  | 2 |  | S1 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125530 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125530 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125530 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125530 |  | AUD-2026-03-2000010826ACN-2026-03-4000125530 | 21 |  | 26 | 80 | 42 | 42 | 31
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152301 | Open |  |  | Review of major KPIs including operational performance, cost leadership,scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1677 | GUWAHATI DEPOT | Cycle time improvement noticed,to be sustained and to keep as per Target,as discussed for cost optimistaion measures are to monitorand maintain including inhouse activities,2 nos old TTs RFD is approved , Disposal to be Completed.M&I inspection are done as per schedule and to ensure compliances in time bound manner.All projects to be completed as per Schedule.Give special focus on FE supply and commissioning. | SOD | Marketing | GZR | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017852ACN-2026-09-4000152301 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152301 | 2026-09-01 | 48.7538 | 409 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152301 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152301 |  | AUD-2026-09-2000017852ACN-2026-09-4000152301 | 21 |  | 27 | 80 | 5 | 5 | 59
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152302 | Open |  |  | PCSA and commissioning of TK-11. For OISD compliance fund allocated | 1.3 | Pending issues reviewed | 1677 | GUWAHATI DEPOT | Zone already taken up with HQO for fund for completion of TK-11 Automation Job.HVLR has been arranged in co-ordination with HQO,complete commissioning activities.Arrangement to be done for call for PCSA.Peending compliance of OISD to be complted in time bound manner | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152302 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152302 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152302 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152302 |  | AUD-2026-09-2000017852ACN-2026-09-4000152302 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152303 | Open |  |  | Status Checked and 6 points pending,details attached. | 1.4 | Earlier action points status checked | 1677 | GUWAHATI DEPOT | Balalnce pending points to comply in Time bound manner. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152303 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152303 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152303 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152303 |  | AUD-2026-09-2000017852ACN-2026-09-4000152303 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152304 | Open |  |  | Random VA alerts checked.Mostly alerts at approach road for overcrowing being generated.In non-hazardous area also showing PPE alerts. To take action accordingly. | 2.7 | VA alerts checked / analysed | 1677 | GUWAHATI DEPOT | To check and take corrective action to avoid false alerts so as to minimise unnecessary alerts and concentrting on real alerts. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152304 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152304 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152304 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152304 |  | AUD-2026-09-2000017852ACN-2026-09-4000152304 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152305 | Open |  |  | Fire water required as per OISD calculation - 2184 KL/Fire water available at site - 2380 KL on the date of inspection.Fire water tanks are being fed through 2 bore well.FW Tanks are schedule for cleaning. | 2.10 | Fire water levels verified | 1677 | GUWAHATI DEPOT | Tanks cleaning are to be planned phasewise and all Mutual aid members to be informed including nearesr Fire brigade. | SOD | Marketing | GZR | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017852ACN-2026-09-4000152305 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152305 | 2026-09-01 | 48.7538 | 409 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152305 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152305 |  | AUD-2026-09-2000017852ACN-2026-09-4000152305 | 21 |  | 27 | 80 | 5 | 5 | 59
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152306 | Open |  |  | Roadside emergency procedure awareness checked with TT crews. TT crews were aware of emergency procedure.TREM Card availability checked on TT and are available. | 2.15 | TT crew roadside emergency procedures checked | 1677 | GUWAHATI DEPOT | Gantry officer advised to check the correctness of Contact Nos. available in TREM card and for updation. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152306 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152306 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152306 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152306 |  | AUD-2026-09-2000017852ACN-2026-09-4000152306 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152307 | Open |  |  | Random TT fitting check being carried out.Some TTs cheked and found ok. | 3.1 | TT fittings & discipline checked | 1677 | GUWAHATI DEPOT | In addition to 3rd party check ,officers to ensure random checking of TTs and its compliances. | SOD | Marketing | GZR | 2026-09-15 |  | 1 |  | S1 | F1 | 2026-09-15 | AUD-2026-09-2000017852ACN-2026-09-4000152307 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152307 | 2026-09-01 | 48.7538 | 379 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152307 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152307 |  | AUD-2026-09-2000017852ACN-2026-09-4000152307 | 21 |  | 27 | 80 | 5 | 5 | 55
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152308 | Open |  |  | It was given to understand that the reco is being done on Auto dips only except in case of exception.Recently TFMS equipments are changed.Monitoring are being done through manual dips. | 3.8 | Auto vs Manual reconciliation checked | 1677 | GUWAHATI DEPOT | TFMS File note approval for Auto dip posting are being processed as confirmed by Location.Expedite the activity. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152308 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152308 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152308 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152308 |  | AUD-2026-09-2000017852ACN-2026-09-4000152308 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152309 | Open |  |  | Earth pits are maintained ok. | 3.16 | Earth pits / boundary / vegetation control checked | 1677 | GUWAHATI DEPOT | Old Earthpits are to be dismantled. | SOD | Marketing | GZR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017852ACN-2026-09-4000152309 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152309 | 2026-09-01 | 48.7538 | 425 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152309 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152309 |  | AUD-2026-09-2000017852ACN-2026-09-4000152309 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152310 | Open |  |  | MOC 5 Nos prepared.However few open MOC are to be closed. | 3.17 | MOC status reviewed | 1677 | GUWAHATI DEPOT | All open MOC to be reviewed by LIC and to close. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017852ACN-2026-09-4000152310 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152310 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152310 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152310 |  | AUD-2026-09-2000017852ACN-2026-09-4000152310 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152311 | Open |  |  | OISD - 29 (18 pending) SSA - 7 pending Comprehensive Audit - 7 pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1677 | GUWAHATI DEPOT | All pending point to be complied as per Target | SOD | Marketing | GZR | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017852ACN-2026-09-4000152311 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152311 | 2026-09-01 | 48.7538 | 576 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152311 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152311 |  | AUD-2026-09-2000017852ACN-2026-09-4000152311 | 21 |  | 27 | 80 | 5 | 5 | 83
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152312 | Open |  |  | Yes. 1.Entrace gate area proper RCC to be done. 2. Near Battery room cable tray fixing to be done/check for others also 3. Near hazrdous entry access points DOs/Don't board display to be provided. 4.Water logging from Tank dyke area to be removed on regular basiswith supervision during rainy season. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1677 | GUWAHATI DEPOT | All points to be checked and to be complied. | SOD | Marketing | GZR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017852ACN-2026-09-4000152312 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152312 | 2026-09-01 | 48.7538 | 424 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152312 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152312 |  | AUD-2026-09-2000017852ACN-2026-09-4000152312 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR MANAGEMENT AUDIT | 2026-09-01 | AUD-2026-09-2000017852 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152313 | Open |  |  | OWS Job under progress,Supply and commissioning of FE to be monitored and take corrective action. | 4.3 | Project progress reviewed | 1677 | GUWAHATI DEPOT | All projects to be completed as per schedule. | SOD | Marketing | GZR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017852ACN-2026-09-4000152313 | AS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017852ACN-2026-09-4000152313 | 2026-09-01 | 48.7538 | 486 | >20 | AUD-2026-09-2000017852 - ACN-2026-09-4000152313 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017852ACN-2026-09-4000152313 |  | AUD-2026-09-2000017852ACN-2026-09-4000152313 | 21 |  | 27 | 80 | 5 | 5 | 70
BANTHIYA RITESH DEELIP | 2026-09-14 | PANWAR VIPIN SINGH | 2026-08-09 | 1. Malpractices cases handled very carefully, all TTs having shortage of 100 Ltrs, joint inspection done for these cases and actiontaken as per ITDG. 2. Ethanol TT MP20ZN5417 ( Narmada Sugar Pvt. Ltd. ) ITDG action taken for Irregularity 3. Nil accident in Q1for roady and at location and SOP training provided to all TT crew , CW , security and Officers as per OISD 154. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127302 | Closed | PANWAR VIPIN SINGH | 2026-08-09 | Interaction was made with all the officers reviewing performance of each department in brief. Matters discussed were as follows: 1. Discussed malpractices cases which happened during the past in SOD locations and precautions to be taken by individuals. 2. Discussed safety related incidents which occurred at other locations and need for alertness & strict adherence to SOPs was emphasized. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1436 | SAGAR DEPOT | XX | SOD | Marketing | CEN | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127302 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127302 | 2026-08-07 19:00 | 72.9622 | 378 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127302 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011238ACN-2026-03-4000127302 | AUD-2026-03-2000011238ACN-2026-03-4000127302 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 54
BANTHIYA RITESH DEELIP | 2026-09-14 | PANWAR VIPIN SINGH | 2026-08-09 | Card replaced and now all CBAC entry working at location. | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127305 | Closed | PANWAR VIPIN SINGH | 2026-08-09 | Access control systems was checked for location. Access control for restricted area is not functional. As per location due to card/screen issue all readers were sent for repair in Dec-25 and the same are awaited. received. | 2.8 | Access control systems checked | 1436 | SAGAR DEPOT | Location to follow up with the vendor for receipt of card and make access control functional at the earliest. | SOD | Marketing | CEN | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011238ACN-2026-03-4000127305 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127305 | 2026-08-07 19:00 | 72.9622 | 378 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127305 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011238ACN-2026-03-4000127305 | AUD-2026-03-2000011238ACN-2026-03-4000127305 | 21 | 21 | 26 | 80 | 4 | 2 | 35 | 54
[5 empty] | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152315 | Open |  |  | CCTV Server issue observed.As confirmed from Location,auto switched off happens and another server not getting auto started. | 1.3 | Pending issues reviewed | 1708 | DIMAPUR DEPOT | Location to take up suitably and keep the system running all the time. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017853ACN-2026-09-4000152315 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152315 | 2026-09-12 | 37.7538 | 394 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152315 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152315 |  | AUD-2026-09-2000017853ACN-2026-09-4000152315 | 21 |  | 27 | 80 | 7 | 7 | 57
[5 empty] | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152316 | Open |  |  | One centrifugal Pump for Fire fighting water requirements to be installed. | 1.4 | Earlier action points status checked | 1708 | DIMAPUR DEPOT | To take action for shifting the Pump and installation. | SOD | Marketing | GZR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017853ACN-2026-09-4000152316 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152316 | 2026-09-12 | 37.7538 | 424 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152316 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152316 |  | AUD-2026-09-2000017853ACN-2026-09-4000152316 | 21 |  | 27 | 80 | 7 | 7 | 61
[5 empty] | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152317 | Open |  |  | CCTV sever down since 18.8.26. Total 27 nos of CCTV are installed | 2.6 | CCTV functioning checked | 1708 | DIMAPUR DEPOT | Officer to follow up with CCTV vendor for restoration immediately. | SOD | Marketing | GZR | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-09-2000017853ACN-2026-09-4000152317 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152317 | 2026-09-12 | 37.7538 | 394 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152317 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152317 |  | AUD-2026-09-2000017853ACN-2026-09-4000152317 | 21 |  | 27 | 80 | 7 | 7 | 57
[5 empty] | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152322 | Open |  |  | Scrap need to be identified and disposed off. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1708 | DIMAPUR DEPOT | Through MSTC aution RFD to be cleared. | SOD | Marketing | GZR | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017853ACN-2026-09-4000152322 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152322 | 2026-09-12 | 37.7538 | 455 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152322 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152322 |  | AUD-2026-09-2000017853ACN-2026-09-4000152322 | 21 |  | 27 | 80 | 7 | 7 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122612 | Open |  |  | Fire drill was conducted with tank valve section on fire | 2.2 | Double contingency scenario simulated; observations recorded | 1712 | BARAUNI POL IRD | approach to sudden mock drill was good . Fire scenerio was on tank 6 & tk 5 cooling to be done but some 6-7 nozzles found to be choked . Delay in starting of sprinkler of 2nd nearby tank . All other system worked . Training of all concern to improve mock drills | SOD | Marketing | PZR | 2026-03-31 |  | 12 |  | S4 | F3 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122612 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122612 | 2026-09-03 | 46.7538 | 211 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122612 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-02-2000011302ACN-2026-03-4000122612 |  | AUD-2026-02-2000011302ACN-2026-03-4000122612 | 21 |  | 26 | 80 | 1 | 1 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122624 | Open |  |  | vendor to be called for proper functioning | 6.1 | CEMS WORK | 1712 | BARAUNI POL IRD | Training of CEMS system to be given | SOD | Marketing | PZR | 2026-04-15 |  | 4 |  | S2 | F2 | 2026-04-15 | AUD-2026-02-2000011302ACN-2026-03-4000122624 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122624 | 2026-09-03 | 46.7538 | 226 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122624 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-02-2000011302ACN-2026-03-4000122624 |  | AUD-2026-02-2000011302ACN-2026-03-4000122624 | 21 |  | 26 | 80 | 1 | 1 | 33
[5 empty] | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122627 | Open |  |  | Both approach road having fencing instead of boundary wall of 3 m height | 6.5 | Approach and Exit road to depot | 1712 | BARAUNI POL IRD | As road belongs to HPCL , proper safety of road to be done and necessary NPCB to be projected | SOD | Marketing | PZR | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-02-2000011302ACN-2026-03-4000122627 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122627 | 2026-09-03 | 46.7538 | 486 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122627 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-02-2000011302ACN-2026-03-4000122627 |  | AUD-2026-02-2000011302ACN-2026-03-4000122627 | 21 |  | 26 | 80 | 1 | 1 | 70
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-06-4000138541 | Open |  |  | Electrical Earthpit nos 45, 157 were found to have proper connections. However Earthpit no 151 found to have improper connections of clamps, etc Leak of coolant observed from 320 KVA DG. Floor of 500 KVA DG found soaked with oil. | 6.5 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Review and checking of all earth pits to be done. Wrong connections to be corrected. Propoer house keepoing of the DG area to be done. LIC to ensrue. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138541 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138541 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138541 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138541 |  | AUD-2026-06-2000013057ACN-2026-06-4000138541 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-06-4000138501 | Open |  |  | Earth pit signages missing at depot entry near admin building.Even the electrodes and connections found improper | 6.8 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Pit nos to be mentioned. Pits to be maintained as per IS3043 | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138501 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138501 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138501 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138501 |  | AUD-2026-06-2000013057ACN-2026-06-4000138501 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-06-4000138503 | Open |  |  | Reviewed 6 random CCTV footages (Night) for Railway Siding, Lube Godowns, ETP, Rail Gate, Ethanol gantry, MS/HSD Gantry. Guards were seen only at Ethanol gantry during the time captured as per the Patrol report. | 6.10 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Footage to be captured in camera view. Safety officer to ensure the readrer tags are placed in camera view OR security to visit thespot and tag the reader while on patrol | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138503 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138503 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138503 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138503 |  | AUD-2026-06-2000013057ACN-2026-06-4000138503 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-06-4000138509 | Open |  |  | Monitor at ther parking yard were not maintained properly. No. 1 &2 at the parking yard | 6.16 | Quarterly Inspection | 1712 | BARAUNI POL IRD | safety officer to ensure proper access to the fire fighting faciltiy at the parking area. Removal of all vegation growth in and around the facility. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138509 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138509 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138509 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138509 |  | AUD-2026-06-2000013057ACN-2026-06-4000138509 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-06-4000138511 | Open |  |  |  | 6.18 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location and saftey officer to ensure that exact remakrs to be entered in the register and take corrective action. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138511 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138511 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138511 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138511 |  | AUD-2026-06-2000013057ACN-2026-06-4000138511 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-06-4000138514 | Open |  |  | Sprinklers T : 12,11,10,9,8,6,5 and B: 10,5,4,3of TK1 found choked. | 6.21 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Periodic checking and clearing blockages of Sprinkler nozzles needs to be done | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138514 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138514 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138514 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138514 |  | AUD-2026-06-2000013057ACN-2026-06-4000138514 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26QUARTERLY INSPECTION | ACN-2026-06-4000138519 | Open |  |  | LUX reading was below te prescribed limit for Control room 300 against 400 and at Fire Engine shed 85 against 100-150 | 6.26 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Corrective action to be taken by Location by increaing illumination. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138519 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138519 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138519 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138519 |  | AUD-2026-06-2000013057ACN-2026-06-4000138519 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.29QUARTERLY INSPECTION | ACN-2026-06-4000138521 | Open |  |  | Toolbox talks are not being carried out as per HQO circular. Lack of awareness on points mentioned in Work permits found in Ms Aradhya, Junior Executive- Operations | 6.29 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Tool box talks to be done as per HQO circular and reported in the format provided. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138521 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138521 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138521 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138521 |  | AUD-2026-06-2000013057ACN-2026-06-4000138521 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.31QUARTERLY INSPECTION | ACN-2026-06-4000138523 | Open |  |  | Boards to be updated in the electrical panel room. | 6.31 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Details on the board at the EPR to be updated. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138523 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138523 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138523 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138523 |  | AUD-2026-06-2000013057ACN-2026-06-4000138523 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.36QUARTERLY INSPECTION | ACN-2026-06-4000138528 | Open |  |  | PM actitivity for Fire engine was not OK. Daily checklist was not available. Shutoff pressure record was noit available. Actitivty was marked OK in SAP while on ground the same was not produced to us. | 6.36 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Leakage to be arrested. Pump houses to be visited daily by LIC and other officers to detect leak, if any and corrective action | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138528 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138528 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138528 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138528 |  | AUD-2026-06-2000013057ACN-2026-06-4000138528 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.40QUARTERLY INSPECTION | ACN-2026-06-4000138532 | Open |  |  | Fire Drill :showcasing all possibilities for rescue and auxiliary team. | 6.40 | Quarterly Inspection | 1712 | BARAUNI POL IRD | LIC to ensure all senarios are showcased in any fire drill | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138532 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138532 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138532 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138532 |  | AUD-2026-06-2000013057ACN-2026-06-4000138532 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.43QUARTERLY INSPECTION | ACN-2026-06-4000138535 | Open |  |  | Dialogue with Contract workmen and security was done and issues raised was for providing proper eating space. | 6.43 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Basic amenity to be provided for the contract men such as fan, and proper the eating area | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138535 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138535 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138535 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138535 |  | AUD-2026-06-2000013057ACN-2026-06-4000138535 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.44QUARTERLY INSPECTION | ACN-2026-06-4000138536 | Open |  |  | Fire Drill :showcasing all possibilities for rescue and auxiliary team. | 6.44 | Quarterly Inspection | 1712 | BARAUNI POL IRD | LIC to ensure all senarios are showcased in any fire drill | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138536 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138536 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138536 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138536 |  | AUD-2026-06-2000013057ACN-2026-06-4000138536 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.45QUARTERLY INSPECTION | ACN-2026-06-4000138537 | Open |  |  | Guidance/ directions were not being taken form LIC during fire instances. | 6.45 | Quarterly Inspection | 1712 | BARAUNI POL IRD | To be ensured. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138537 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138537 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138537 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138537 |  | AUD-2026-06-2000013057ACN-2026-06-4000138537 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.47QUARTERLY INSPECTION | ACN-2026-06-4000138539 | Open |  |  | Fire Dril other observations: Traffic evacuation movement was cluttered, NO Fire extinguishers near the farication work going on, late evacuation of tankers from gantry, obstruction in fire fighting at site, No flag shown to convey the message of fire spot. | 6.47 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Propoer training to be given to the manpower staff for emergency situation. Safety officer to ensure the same. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138539 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138539 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138539 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138539 |  | AUD-2026-06-2000013057ACN-2026-06-4000138539 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.48QUARTERLY INSPECTION | ACN-2026-06-4000138540 | Open |  |  | Emergency trolley found to be not maintained with all facilities. Even some of the compartment doors could not be opened. Compartments were having material different from what was mentioned on display tag | 6.48 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Emergency trolley to be maintained properly | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138540 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138540 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138540 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138540 |  | AUD-2026-06-2000013057ACN-2026-06-4000138540 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.54QUARTERLY INSPECTION | ACN-2026-06-4000138543 | Open |  |  | CCTV system:No officer monitors CCTV system. Safety officer has no understanding of intended purpose of cameras along perimeter wall. Security supervisor maintains a record of CCTV monitoring, where only information about whether a camera is functioning or not, is mentioned. | 6.54 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to take CCTV monitoring with seriouness. LIC to sensitize the officers and security guards to review the footage on regualr basis. CCTV camera views to be free from any view obstruction. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138543 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138543 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138543 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138543 |  | AUD-2026-06-2000013057ACN-2026-06-4000138543 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.56QUARTERLY INSPECTION | ACN-2026-06-4000138544 | Open |  |  | Housekeeping: Vegetations blocking view of view of CCTVs, covering pipelines almost completely, found at different places of location. Lube oil leak observed in lube godown. | 6.56 | Quarterly Inspection | 1712 | BARAUNI POL IRD | pipelines to be made vegetation free. i.e. removal of all vegetative growth on top of the pipes. Oil leaks to be checked and sealeswhere ever required. CCTV canera view to be restored with clear vision. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138544 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138544 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138544 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138544 |  | AUD-2026-06-2000013057ACN-2026-06-4000138544 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.58QUARTERLY INSPECTION | ACN-2026-06-4000138545 | Open |  |  |  | 6.58 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to use standard formats for checking and LIC to review these checklist in regular intervals. These checklists to be signedby officials after review. | SOD | Marketing | PZR | 2026-07-15 |  | 8 |  | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138545 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138545 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138545 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000013057ACN-2026-06-4000138545 |  | AUD-2026-06-2000013057ACN-2026-06-4000138545 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-08-4000149490 | Open |  |  | Earthpit no 152 of solar light body found with single clamp and single bolt connection. A wood cutting saw found inside Earthpit no170. This earthpit is also having single clamp and single bolt connection. Similar condition found for Earthpit no 205 of himast. | 6.2 | Quarterly Inspection | 1712 | BARAUNI POL IRD | These earthpits to be made as per IS3043 | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149490 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149490 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149490 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149490 |  | AUD-2026-08-2000017151ACN-2026-08-4000149490 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-08-4000149495 | Open |  |  | There are no roof on electrical panel room of ETP | 6.7 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Roof to be provided | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149495 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149495 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149495 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149495 |  | AUD-2026-08-2000017151ACN-2026-08-4000149495 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-08-4000149497 | Open |  |  | At the road corner near calibration tower, there are two CCTV cameras installed on a slanting pole, one of which is pointing towards Emergency gate, but the other one is pointing towards the pole itself. The pole is engulfed with creepers upto almost half of its height. | 6.9 | Quarterly Inspection | 1712 | BARAUNI POL IRD | The pole is to be made erect and the faulty camera to be repaired/ its line of vision to be corrected | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149497 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149497 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149497 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149497 |  | AUD-2026-08-2000017151ACN-2026-08-4000149497 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-08-4000149702 | Open |  |  | Concertina coils are covered by green vegetations, on a large nos of lengths across the location. | 6.14 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Concertina coils to be made free of green vegetation | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149702 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149702 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149702 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149702 |  | AUD-2026-08-2000017151ACN-2026-08-4000149702 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-08-4000149703 | Open |  |  | Scrap cut plates, old pipeline lengths, kept alongside roads, near fire water pumphouse, inside scrap yard, rolls of barbed wires, cut angles, building rods, fan cover, fan blades, etc, in scrap yard, along with other retail outlet scraps in the scrap yard, completely covered by vegetation. | 6.15 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to segregate SOD scraps from Retail scrap and dispose off within next three months, take up with Retail for disposing off their scraps and also maintain the scrap yard properly. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149703 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149703 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149703 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149703 |  | AUD-2026-08-2000017151ACN-2026-08-4000149703 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-08-4000149704 | Open |  |  | No coupling guard found for Fire engine no 01. Leak from the gland is making areas around the fire engine water soaked. There is accumulation of mud and water inside base frame | 6.16 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to take corrective action by doing proper maintenance | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149704 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149704 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149704 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149704 |  | AUD-2026-08-2000017151ACN-2026-08-4000149704 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-08-4000149705 | Open |  |  | Leak observed from gland of Jockey pump 1, spreading water around the pump. | 6.17 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to take corrective action by doing proper maintenance | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149705 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149705 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149705 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149705 |  | AUD-2026-08-2000017151ACN-2026-08-4000149705 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-08-4000149706 | Open |  |  | Sprinkler system of Tk13 was operated. Nozzles M24, M25, M31, M32, M33, M35 and T30 found choked. T33 nozzle has come out. | 6.18 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to take corrective action by doing proper maintenance | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149706 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149706 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149706 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149706 |  | AUD-2026-08-2000017151ACN-2026-08-4000149706 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-08-4000149707 | Open |  |  | There are no direction boards towards HVLR operating panel no 8, used for Tk19. Visibility of the HVLR from the panel is completelyblocked by vegetation. | 6.19 | Quarterly Inspection | 1712 | BARAUNI POL IRD | HVLR panel direction board to be put up. Vegetation to be cut so that proper visibility of HVLR from operating panel is there | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149707 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149707 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149707 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149707 |  | AUD-2026-08-2000017151ACN-2026-08-4000149707 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-08-4000149708 | Open |  |  | Sample disposal register has no signature of any officer, after reported disposal. Even samples of 2022 found kept, keeping some racks occupied. Location does not have any record of these samples. | 6.20 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Periodic review od sample register to be done by LIC to ensure no such miss out is there. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149708 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149708 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149708 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149708 |  | AUD-2026-08-2000017151ACN-2026-08-4000149708 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-08-4000149709 | Open |  |  | Daily safety checklist is not being maintained properly with almost no facts and figures mentioned in it. Weekly, monthly, qtrly checklists are not there | 6.21 | Quarterly Inspection | 1712 | BARAUNI POL IRD | LIC to ensure that periodic rounds of the location is taken and location is operated as per direction given in the checklists and the checklists are maintained properly | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149709 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149709 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149709 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149709 |  | AUD-2026-08-2000017151ACN-2026-08-4000149709 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.30QUARTERLY INSPECTION | ACN-2026-08-4000149717 | Open |  |  | Parking area housekeeping and tanker parking was haphazard was very poor. Observed vegetation growth on Firefighting equipment platform. | 6.30 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to ensure tankers are parked in proper manner avoiding congestion and not to be hinderance during any firefighting event. Location to remove the vegetation over all the platforms and its surroundings where firefighting facility is installed. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149717 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149717 | 2026-09-03 | 46.7538 | 384 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149717 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017151ACN-2026-08-4000149717 |  | AUD-2026-08-2000017151ACN-2026-08-4000149717 | 21 |  | 27 | 80 | 1 | 1 | 55
VED PRAKASH | 2026-09-15 | DAS DARSHAN | 2026-09-14 | List of unused assets has been updated as per material available in store. Material like ROSOVs, MOVs, Vertical pumps, motors etc have been segregated and kept in store | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122659 | Closed | DAS DARSHAN | 2026-09-14 | List of unused assets to be updated as per material available in store. Material like ROSOVs, MOVs, Pipe line fitting, cables, Vertical pumps, Ethanol Soft Starter Panel and motors etc are available in store. | 3.9 | Abnormal variations / unused assets reviewed | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122659 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122659 | 2026-09-03 | 46.7538 | 379 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122659 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122659 | AUD-2026-03-2000011009ACN-2026-03-4000122659 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 55
VED PRAKASH | 2026-09-15 | DAS DARSHAN | 2026-09-14 | The latest approved P&ID has been displayed in the field. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143496 | Closed | DAS DARSHAN | 2026-09-14 | The latest approved P&ID not displayed in the field. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Ensure that the latest approved P&ID is displayed prominent place in the field for ready reference. | SOD | Marketing | NCR | 2026-07-30 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-30 | AUD-2026-06-2000013451ACN-2026-07-4000143496 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143496 | 2026-09-03 | 46.7538 | 379 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143496 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013451ACN-2026-07-4000143496 | AUD-2026-06-2000013451ACN-2026-07-4000143496 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152408 | Open |  |  | 1. HLSA : Open points : 5/13. Critical open observation is related to CBACS/Biometric system implementation at location. Requirement is already submitted with HQO for consolidation 2. GM visit points of Q4 : Open points : 5/19 3. GM visit points of FY 26 Q1 : Open points : 6/20 4. Safe 100 : Open points : 6/61 Critical open point is related to PESO approval for carrying out operations beyond sunset & Jetty pipeline. PESO Kakkanad local Cochin office replied to location with an advise to submit the application at Nagpur office. Location to expedite Lighting Jobs and apply for PESO permission. 5. T4S : Open points 10 6. MDSA FY 24 : Open points 3 /70 Critical open point is related to PESO approval for carrying out operations beyond sunset & Jetty pipeline. 7. MDSA FY 25 : Open points 16/28 | 1.4 | Earlier action points status checked | 1833 | COCHIN BLACK TERMINAL | Location to comply all audit recommendations in a time bound manner. Pending >2 Years : 0 No audit recommendation to remain openfor more than a year and immediate action is advised for closing the open points | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152408 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152408 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152408 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152408 |  | AUD-2026-09-2000017851ACN-2026-09-4000152408 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152409 | Open |  |  | Budget required for civil repair jobs for the boundary wall. PR submitted to CPO for tendering works, budget requirement will be arrived after placement of PO, for the works based on the inspection report | 1.5 | HQO / Zonal support required identified | 1833 | COCHIN BLACK TERMINAL | To complete boundary wall repair works | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152409 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152409 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152409 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152409 |  | AUD-2026-09-2000017851ACN-2026-09-4000152409 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152410 | Open |  |  | Compliances reviewed and complied. Advised to submit Monthly Highlights on time w.r.t key AOP targets 1. Slow moving stocks are to be liquidated in coordination with Lubes RO. Regular follow up is to be maintained. 2. Th 305 proposal is to be submitted urgently since the tank is not in services for more than a year. 3. Due importance is to be accorded for daily reco and stock accounting. SOPs to be reviewed for Stock accounting 4. PL patrolling reports + integrity survey : To complete ongoing integrity surveys for Jetty line and rectification methods. Maintain pipeline patrolling / inspection reports inline with OISD std | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1833 | COCHIN BLACK TERMINAL | Location to attend each of the point, in a time bound manner, in all respects | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152410 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152410 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152410 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152410 |  | AUD-2026-09-2000017851ACN-2026-09-4000152410 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152412 | Open |  |  | Total 6 no. of SOPs are available in online portal in approved status | 2 |  | 1833 | COCHIN BLACK TERMINAL | Location to review and ensure all regular O&M activities are covered in approved SOP | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017851ACN-2026-09-4000152412 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152412 | 2026-09-08 16:00 | 41.0872 | 425 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152412 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152412 |  | AUD-2026-09-2000017851ACN-2026-09-4000152412 | 21 |  | 27 | 80 | 2 | 0 | 61
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152413 | Open |  |  | Last mock fire drill was conducted on 05-08-2026 near MCC room area. Last L2 mock fire drill conducted on 19-01-2026. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1833 | COCHIN BLACK TERMINAL | Location to conduct DCMP (L2) drill once in six months in cooridnation with Dept. of F&B and mutual aid group | SOD | Marketing | CZR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017851ACN-2026-09-4000152413 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152413 | 2026-09-08 16:00 | 41.0872 | 394 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152413 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152413 |  | AUD-2026-09-2000017851ACN-2026-09-4000152413 | 21 |  | 27 | 80 | 2 | 0 | 57
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152415 | Open |  |  | Location informed that 10 numbers of Light sensors were installed at different locations. The job for lux level improvement is in progress. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1833 | COCHIN BLACK TERMINAL | Location to complete lux level improvement and submit PESO application for operations after sunset so as to close open MDSA & Safe 100 points | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017851ACN-2026-09-4000152415 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152415 | 2026-09-08 16:00 | 41.0872 | 425 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152415 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152415 |  | AUD-2026-09-2000017851ACN-2026-09-4000152415 | 21 |  | 27 | 80 | 2 | 0 | 61
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152418 | Open |  |  |  | 3.7 | Inventory physical dip of minimum two tanks taken | 1833 | COCHIN BLACK TERMINAL | TFMS - SAP integration file note is to be submitted urgently. The issue with density probes is to be resolved without further delayin coordination with OEM M/s. Honeywell | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017851ACN-2026-09-4000152418 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152418 | 2026-09-08 16:00 | 41.0872 | 425 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152418 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152418 |  | AUD-2026-09-2000017851ACN-2026-09-4000152418 | 21 |  | 27 | 80 | 2 | 0 | 61
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152422 | Open |  |  | Status is provided as above | 3.18 | OISD/MDSA/SSA compliance reviewed | 1833 | COCHIN BLACK TERMINAL | To be complied at the earliest | SOD | Marketing | CZR | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152422 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152422 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152422 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152422 |  | AUD-2026-09-2000017851ACN-2026-09-4000152422 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152424 | Open |  |  | Capitalization of all the physically completed projects completed | 4.3 | 2 projects to be completed for which the job is under progress | 1833 | COCHIN BLACK TERMINAL | Location to follow up and complete roof top solar power panels installation and commissioning | SOD | Marketing | CZR | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152424 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152424 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152424 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152424 |  | AUD-2026-09-2000017851ACN-2026-09-4000152424 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152425 | Open |  |  | RFD for two company owned jeeps completed | 4.5 | scrap disposal progress reviewed/scrap free environment checked. | 1833 | COCHIN BLACK TERMINAL | Location to segregate scrap items and take action suitably | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152425 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152425 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152425 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017851ACN-2026-09-4000152425 |  | AUD-2026-09-2000017851ACN-2026-09-4000152425 | 21 |  | 27 | 80 | 2 | 0 | 70
MAZUMDER SAUVIK | 2026-09-15 | MD KASHIF | 2026-09-15 | The meeting and stakeholder interaction were conducted with the transporters. The transporters have shared the list of toll gates, and the toll route setup is currently under progress in coordination with the Retail team. The activity is being taken up as a continuous process for further updation and validation. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-06-4000137710 | Closed | MD KASHIF | 2026-09-15 | Stake holder interaction: A meeting was held with around 20 Transporters, where various VTS deviations, requirement of TT movement monitoring, TT blocking, etc. were discussed. The transporters raised issue of non availability of toll gates on routes set, which is causing them loss. Transporters have been requested to share list of such toll gates, destination wise so that we can get the sameset thru Retail. | 6.19 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to followup for the list and ensure communication to Sales team for updation of toll gates. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137710 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137710 | 2026-09-19 10:00 | 30.3372 | 379 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137710 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137710 | AUD-2026-06-2000012744ACN-2026-06-4000137710 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
MAZUMDER SAUVIK | 2026-09-15 | MD KASHIF | 2026-09-15 | Registers are being reviewed regularly by officers. Being ensured that registers are properly recorded and updated. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25QUARTERLY INSPECTION | ACN-2026-06-4000137716 | Closed | MD KASHIF | 2026-09-15 | Visitor registers needs to be updated. | 6.25 | Quarterly Inspection | 1742 | BOKARO DEPOT | Register Review by officers needs to be done regularly. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137716 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137716 | 2026-09-19 10:00 | 30.3372 | 379 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137716 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137716 | AUD-2026-06-2000012744ACN-2026-06-4000137716 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
MAZUMDER SAUVIK | 2026-09-15 | MD KASHIF | 2026-09-15 | Record keeping training is being regularly given. Security supervisor, security agency is being counselled on regular basis. Theconcerned security personnel have been instructed not to use pencil for any entries or remarks in the gate pass register. It has also been ensured that all cancelled gate passes are duly handed over to Security for proper record and verification. The practice is being monitored for continued compliance. All officers are periodically reviewing the security documents and registers for sustained compliance. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.29QUARTERLY INSPECTION | ACN-2026-06-4000137719 | Closed | MD KASHIF | 2026-09-15 | Gate pass registers had entries in pencil for cancelled passes. Justification not mentioned. | 6.29 | Quarterly Inspection | 1742 | BOKARO DEPOT | Avoid usingh pencil for writing any remarks. Cancelled gate pas also to haned over to security. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137719 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137719 | 2026-09-19 10:00 | 30.3372 | 379 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137719 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137719 | AUD-2026-06-2000012744ACN-2026-06-4000137719 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
MAZUMDER SAUVIK | 2026-09-15 | MD KASHIF | 2026-09-15 | The CCTV storage issue has been raised to OEM & HQ. There is disk error due to VA & NAS server issue. It is under consideration by Zonal & HQ team for resolution. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.33QUARTERLY INSPECTION | ACN-2026-06-4000137723 | Closed | MD KASHIF | 2026-09-15 | CCTV Footage : 7th and 8th May recording not available | 6.33 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to take it up with vendor for record to stored. | SOD | Marketing | PZR | 2026-07-15 | INSTRUMENTATION OR ALARM FAILURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137723 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137723 | 2026-09-19 10:00 | 30.3372 | 379 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137723 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137723 | AUD-2026-06-2000012744ACN-2026-06-4000137723 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
MAZUMDER SAUVIK | 2026-09-15 | MD KASHIF | 2026-09-15 | CCTV footage is observed on daily basis by security personnel. Same being reviewed periodically by Safety officer for compliances. TT cabin is being checked on each trip bye security guard positioned on the Gate. Training to new New security agency are being provided for sustained compliances. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.37QUARTERLY INSPECTION | ACN-2026-06-4000137727 | Closed | MD KASHIF | 2026-09-15 | CCTV Footage Review: Security guards are not checking the tanker cabin when they are entring for loading | 6.37 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer to sensitized the supervisior to review the CCTV footage regularly. Ensure Security to check cabin. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137727 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137727 | 2026-09-19 10:00 | 30.3372 | 379 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137727 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137727 | AUD-2026-06-2000012744ACN-2026-06-4000137727 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
|  | JOSVIN SUNNY | 2026-09-15 | Risk register is maintained and fire extingusher availability vs requirement chart is developed | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137543 | Completed | JOSVIN SUNNY | 2026-09-15 | Reviewed during visit; found satisfactory. | 2.5 | Emergency response preparedness reviewed | 1892 | KOZHIKODE DEPOT | Advised to maintain risk register. Develop FFE availability Vs requirement chart. | SOD | Marketing | CZR | 2026-07-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013060ACN-2026-06-4000137543 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137543 | 2026-09-17 16:00 | 32.0872 | 332 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137543 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013060ACN-2026-06-4000137543 |  | AUD-2026-06-2000013060ACN-2026-06-4000137543 | 21 |  | 27 | 80 | 2 | -4 | 48
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-05-4000131444 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Siren at the location was tested every week, however there was no person being sent outside to confirm the siren being audible at 3kms range. | 6.1 | Quarterly Inspection | 1723 | PATNA DEPOT | One person needs to be sent to 3 km range to confirm siren audibility | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131444 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131444 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131444 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131444 | AUD-2026-05-2000012355ACN-2026-05-4000131444 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-05-4000131445 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Armed guard name was not updated in the register. | 6.2 | Quarterly Inspection | 1723 | PATNA DEPOT | Name to be updated in the register | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131445 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131445 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131445 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131445 | AUD-2026-05-2000012355ACN-2026-05-4000131445 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-05-4000131446 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Material gate pass was not upto date. Last entry was for 19-5-26. Officer sign was missing. | 6.3 | Quarterly Inspection | 1723 | PATNA DEPOT | HPCL Location Officer to sign the register | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131446 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131446 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131446 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131446 | AUD-2026-05-2000012355ACN-2026-05-4000131446 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-05-4000131447 | Closed | JHA RAJAN KUMAR | 2026-09-15 | In / Out entry registry for contract workman not update since 16-5-26 | 6.4 | Quarterly Inspection | 1723 | PATNA DEPOT | register to be updated daily or when ever there is any entry | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131447 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131447 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131447 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131447 | AUD-2026-05-2000012355ACN-2026-05-4000131447 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-05-4000131448 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Updating of phones nos. such as RM, M&I, Location In charge needs to done at the entry gate. | 6.5 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to upodate the details | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131448 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131448 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131448 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131448 | AUD-2026-05-2000012355ACN-2026-05-4000131448 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-05-4000131491 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Random checking of PM schedule compliance was done. As per PM schedule, checking of silica gel of UG Ethanol tanks have been done, but in field, old Silicsa gel which has lost its utility, found | 6.5 | Quarterly Inspection | 1723 | PATNA DEPOT | PM to be carried in true spirit | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131491 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131491 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131491 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131491 | AUD-2026-05-2000012355ACN-2026-05-4000131491 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-05-4000131449 | Closed | JHA RAJAN KUMAR | 2026-09-15 | In / Out entry registry for contract workman not update since 16-5-26 | 6.6 | Quarterly Inspection | 1723 | PATNA DEPOT | Registers to be updated on daily basis | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131449 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131449 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131449 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131449 | AUD-2026-05-2000012355ACN-2026-05-4000131449 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-05-4000131450 | Closed | JHA RAJAN KUMAR | 2026-09-15 | In Material gate pass had correction pen marks. Register was updated till 18-5-26 only. | 6.7 | Quarterly Inspection | 1723 | PATNA DEPOT | Correctionpen needs to be discontinued and any wrong entry to be strike off. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131450 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131450 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131450 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131450 | AUD-2026-05-2000012355ACN-2026-05-4000131450 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-05-4000131451 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Earth pit signages missing at depot entry near admin building.Even the electrodes and connections found improper | 6.8 | Quarterly Inspection | 1723 | PATNA DEPOT | Pit nos to be mentioned. Pits to be maintained as per IS3043 | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131451 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131451 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131451 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131451 | AUD-2026-05-2000012355ACN-2026-05-4000131451 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-05-4000131452 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Tokens with RFID tag to be usedb security guards during Night patrol started form 2-5-26. Earlier depot had a manual system where the guards were supposed to enter the time of patrolling, confirmed by the safety officer in the next day via CCTV footage, but thereis no signature of the HPCL officer in the slips | 6.9 | Quarterly Inspection | 1723 | PATNA DEPOT | Safety officer to sign the slip for confirmation. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131452 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131452 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131452 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131452 | AUD-2026-05-2000012355ACN-2026-05-4000131452 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-05-4000131453 | Closed | JHA RAJAN KUMAR | 2026-09-15 | Reviewed 6 random CCTV footages (Night) for Railway Siding, Lube Godowns, ETP, Rail Gate, Ethanol gantry, MS/HSD Gantry. Guards were seen only at Rail Gate and Ethanol gantry during the time captured as per the Patrol report. | 6.10 | Quarterly Inspection | 1723 | PATNA DEPOT | Footage missing. Safety officer to ensure the readrer tags are placed in camera view OR security to visit the spot and tag the reader while on patrol | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131453 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131453 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131453 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131453 | AUD-2026-05-2000012355ACN-2026-05-4000131453 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-05-4000131454 | Closed | JHA RAJAN KUMAR | 2026-09-15 |  | 6.11 | Quarterly Inspection | 1723 | PATNA DEPOT | HPCL officers to verify the records periodically and LIC too should be informed and registers to be shown | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131454 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131454 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131454 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131454 | AUD-2026-05-2000012355ACN-2026-05-4000131454 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-05-4000131455 | Closed | JHA RAJAN KUMAR | 2026-09-15 |  | 6.12 | Quarterly Inspection | 1723 | PATNA DEPOT | Recording of contract workmen to be madatorialy done in register. The same to be checked by security supervisior and safety officer | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131455 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131455 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131455 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131455 | AUD-2026-05-2000012355ACN-2026-05-4000131455 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-05-4000131456 | Closed | JHA RAJAN KUMAR | 2026-09-15 |  | 6.13 | Quarterly Inspection | 1723 | PATNA DEPOT | Proper record to be maintained at location for CCTV footage. | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131456 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131456 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131456 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131456 | AUD-2026-05-2000012355ACN-2026-05-4000131456 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-05-4000131457 | Closed | JHA RAJAN KUMAR | 2026-09-15 | A number of Earth pits near Gate entry office, found without identification board. | 6.14 | Quarterly Inspection | 1723 | PATNA DEPOT | Pit nos to be mentioned | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131457 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131457 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131457 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131457 | AUD-2026-05-2000012355ACN-2026-05-4000131457 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
MONISH KUMAR | 2026-09-15 | JHA RAJAN KUMAR | 2026-09-15 | Closed in Audit no. AUD-2026-05-2000012310 | QUARTERY DEPOT INSPECTION | 2026-05-22 | AUD-2026-05-2000012355 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-05-4000131458 | Closed | JHA RAJAN KUMAR | 2026-09-15 |  | 6.15 | Quarterly Inspection | 1723 | PATNA DEPOT | Physical work to be ensured in maintenance and false record generation to be stopped immediately | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012355ACN-2026-05-4000131458 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012355ACN-2026-05-4000131458 | 2026-08-03 | 77.7538 | 379 | >20 | AUD-2026-05-2000012355 - ACN-2026-05-4000131458 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012355ACN-2026-05-4000131458 | AUD-2026-05-2000012355ACN-2026-05-4000131458 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152904 | Open |  |  | Housekeeping to be improved near Tank wagon gantry area. | 3.15 | Housekeeping & PPE usage checked | 1585 | MAHUL TERMINAL | To complete site clearance activity | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017701ACN-2026-09-4000152904 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152904 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152904 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152904 |  | AUD-2026-09-2000017701ACN-2026-09-4000152904 | 21 |  | 27 | 80 | 28 | 28 | 57
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152905 | Open |  |  | Earthpit condition reviewed and found OK. However, after revival of TT gantry, new earthpit to be constructed. | 3.16 | Earth pits / boundary / vegetation control checked | 1585 | MAHUL TERMINAL | To construct Earthpit and review. | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017701ACN-2026-09-4000152905 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152905 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152905 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152905 |  | AUD-2026-09-2000017701ACN-2026-09-4000152905 | 21 |  | 27 | 80 | 28 | 28 | 83
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152906 | Open |  |  | PCSA Audit carried out in Jan26. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1585 | MAHUL TERMINAL | 10 points pending compliance | SOD | Marketing | WZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017701ACN-2026-09-4000152906 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152906 | 2026-10-17 | 2.7538 | 486 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152906 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152906 |  | AUD-2026-09-2000017701ACN-2026-09-4000152906 | 21 |  | 27 | 80 | 28 | 28 | 70
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152907 | Open |  |  | No transporter meeting done in Q4. Location to organise | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1585 | MAHUL TERMINAL | Location to ensure one transporter meet per quarter | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017701ACN-2026-09-4000152907 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152907 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152907 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152907 |  | AUD-2026-09-2000017701ACN-2026-09-4000152907 | 21 |  | 27 | 80 | 28 | 28 | 57
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152908 | Open |  |  | Reviewed and advised the team to expedite the job | 4.2 | Maintenance activities reviewed | 1585 | MAHUL TERMINAL | All Tank repair job to complete within provided Timelines | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017701ACN-2026-09-4000152908 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152908 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152908 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152908 |  | AUD-2026-09-2000017701ACN-2026-09-4000152908 | 21 |  | 27 | 80 | 28 | 28 | 83
[5 empty] | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152909 | Open |  |  | RFD to be initiated for Miscellaeous Scrap and Scrap Tanks to be handed over to MR for further disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1585 | MAHUL TERMINAL | To initiate RFD Activities immediately. | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017701ACN-2026-09-4000152909 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152909 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152909 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152909 |  | AUD-2026-09-2000017701ACN-2026-09-4000152909 | 21 |  | 27 | 80 | 28 | 28 | 83
|  | MD KASHIF | 2026-09-15 | GeM Tender- GEM/2026/B/7869677 with due date 04th Sep,2026. PO expected to be placed by 20 Sep,2026.Technical evaluation u/p. Budget for replacement of camera has been assigned to location. Recommendation capital nature and hence being taken suitably as per Zone/HQ directives. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.31QUARTERLY INSPECTION | ACN-2026-06-4000137721 | Completed | MD KASHIF | 2026-09-15 | CCTV footage review: Camera quality is bery poor. | 6.31 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure Immediate replacment of old CCTVs with new ones. | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137721 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137721 | 2026-09-19 10:00 | 30.3372 | 317 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137721 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012744ACN-2026-06-4000137721 |  | AUD-2026-06-2000012744ACN-2026-06-4000137721 | 21 |  | 27 | 80 | 1 | 1 | 46
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152986 | Open |  |  | Review of major KPIs of stock loss , Scrap disposal , M&I , Projects discussed of tank conversion discussed . Advised to commissioned TK2 . Tank wagon gantry- Observed lot of scrap hoses were lying at the gantry. Hoses were found without cap. Other end of the Connected Hoses were on the ground needs to be hang. | 1.2 | Performance review conducted | 1630 | PARADEEP TERMINAL | 1.Stock loss - Stock loss in ethanol & MS is beyond AOP target . Location need to check the areas of losses & take action. 2. Scrap disposal - Advised to segrregate the scrap in the scrap yard . RFD to be made & disposed 3. Receiipt of PWD payment made outsideterminal of Rs.1 Cr to be taken 4. Housekeeping to be improved in operating area-Visitor Lobby .5.Scrap hoses needs to be shiftedand only usable hose to be kept at TW gantry. location to ensure that all the hoses must be capped all the time when not in use. Location advises to make a hose collar stand. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152986 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152986 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152986 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152986 |  | AUD-2026-09-2000017553ACN-2026-09-4000152986 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152987 | Open |  |  | Reviewed . Old Toll tax payments of transporters , route corrections , etc | 1.3 | Pending issues reviewed | 1630 | PARADEEP TERMINAL | Old cases of toll tax and route correction to be completed by 30.9.26 | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152987 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152987 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152987 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152987 |  | AUD-2026-09-2000017553ACN-2026-09-4000152987 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152988 | Open |  |  | 1. TTLF Gantry efficiency to be improved and Day End TLF Report: MFM vs BCU and inventory differences are observed, particularly MS, HSD and Ethanol. 2. All officers to be rotated and should know all jobs in terminal . Local Loading: should be avoided . 3. SOP for pipeline receipt to be made with OMC members and also the clear understanding for the coastal receipts .43. MFM K Factor: Significant factors noted, including Ethanol 0.965/1.068 and B5 1.068, with LP 21/22 values blank | 1.8 | Improvement plans discussed | 1630 | PARADEEP TERMINAL | 1. TTLF loading performance to meet SBU target .Reconcile bay-wise MFM/BCU/invoice/inventory differences and verify meter/totalizercalibration. 2. Officer rotations , particularly in ethanol handling Check preset configuration, totalizer accuracy and prover results 3. SOP with OMC for PLT receipt to avoid losses . 4.Validate calibration, approved K-factor changes and system master data. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152988 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152988 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152988 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152988 |  | AUD-2026-09-2000017553ACN-2026-09-4000152988 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152990 | Open |  |  | Lux level checked and found low level at TT gantry , Control room (290), security cabin , secondary road . | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1630 | PARADEEP TERMINAL | Installation of LED lights on existing HMT and additional light poles is in progress. Location advised to get the Lux level checkedfrom same party who has provided design | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152990 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152990 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152990 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152990 |  | AUD-2026-09-2000017553ACN-2026-09-4000152990 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152991 | Open |  |  | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1630 | PARADEEP TERMINAL | Location advised to inform security DGR owner to carry out inspection in night & have record of the same . Also advised to carry out mock drill in night | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152991 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152991 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152991 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152991 |  | AUD-2026-09-2000017553ACN-2026-09-4000152991 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152992 | Open |  |  | Checked and found okay but At the entrance one access control turnstile was not working, needs to be repaired. | 2.8 | Access control systems checked | 1630 | PARADEEP TERMINAL | one access control turnstile was not working, needs to be repaired. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152992 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152992 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152992 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152992 |  | AUD-2026-09-2000017553ACN-2026-09-4000152992 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152994 | Open |  |  | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1630 | PARADEEP TERMINAL | advised to procure the same urgently | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152994 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152994 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152994 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152994 |  | AUD-2026-09-2000017553ACN-2026-09-4000152994 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152995 | Open |  |  | Checked . Route deviation voilation & unauthorized stoppages found . ATF TTs to Ranchi , stoppage voilation found diversion from route | 3.3 | VTS deviations reviewed | 1630 | PARADEEP TERMINAL | Route correction in some cases & stoppages voilation (other than authorized) to be stopped | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152995 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152995 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152995 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152995 |  | AUD-2026-09-2000017553ACN-2026-09-4000152995 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152996 | Open |  |  | Checking each TTs of ethanol and Initial and Final Dips are being recorded . | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1630 | PARADEEP TERMINAL | Advised location to carry out analysis of all ethanol TTs stock loss variation during unloading by tank dips and check suspected TTs in calibration and make one record of all suppliers. Also action against deflauter TTs to be taken by suppliers and same TTs shallnot be operated in Industry .Action on TT needs to be updated on IEMS portal in coordination with HQO | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152996 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152996 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152996 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152996 |  | AUD-2026-09-2000017553ACN-2026-09-4000152996 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152997 | Open |  |  | TK 4 -HSD : Phy-2288, T-32'c / TAS - 2288.0, T-32.5( R-9390/OR-9382) TK 14 -MS : Phy - 5892.0,W-2.0, T-30.0/TAS - 5891.2, T-29.8, W- 2.0 cm (R-1183/OR-1183.2) | 3.7 | Inventory physical dip of minimum two tanks taken | 1630 | PARADEEP TERMINAL | Minor variation found in Ref.height of Tank 4 TO BE CORRECTED | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152997 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152997 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152997 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152997 |  | AUD-2026-09-2000017553ACN-2026-09-4000152997 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152998 | Open |  |  | daily reco sheet checked | 3.8 | Auto vs Manual reconciliation checked | 1630 | PARADEEP TERMINAL | Stock loss of Ethanol and MS is beyond the target , location required to pay full attention on Ethanol TT unloading and PLT receiptfrom IOC to cover up losses by month end .Locations should investigate root cause, reconcile records, validate calibration/K-factors and confirm corrective action with evidence.Location is advised to keep the daily Day end signed report | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152998 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152998 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152998 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152998 |  | AUD-2026-09-2000017553ACN-2026-09-4000152998 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152999 | Open |  |  | 1. SKO dye mixing equipement surplus after location made SKO free 2. RIM seal protection system one old panel is lying idle at first floor of planning room, to be removed and disposed | 3.9 | Abnormal variations / unused assets reviewed | 1630 | PARADEEP TERMINAL | 1. this facility to be offered to HQO for utilization at other locations 2. disposal to be done | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152999 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152999 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152999 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152999 |  | AUD-2026-09-2000017553ACN-2026-09-4000152999 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153001 | Open |  |  | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1630 | PARADEEP TERMINAL | yes | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153001 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153001 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153001 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153001 |  | AUD-2026-09-2000017553ACN-2026-09-4000153001 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153002 | Open |  |  | Compliance status reviewed . OISD compliances of 2 points AND 6 NOS. FOR SSA pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1630 | PARADEEP TERMINAL | advised to comply by 30.9.2026 | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153002 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153002 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153002 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153002 |  | AUD-2026-09-2000017553ACN-2026-09-4000153002 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153003 | Open |  |  | Transporters meeting done on 20.08.2026 | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1630 | PARADEEP TERMINAL | Transporter - safety during transit advised . Transporters required to provide safe route in rayagada route to avoid unsafe Ghat section. Toll tax payments | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153003 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153003 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153003 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153003 |  | AUD-2026-09-2000017553ACN-2026-09-4000153003 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153004 | Open |  |  | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1630 | PARADEEP TERMINAL | XX | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153004 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153004 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153004 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153004 |  | AUD-2026-09-2000017553ACN-2026-09-4000153004 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153005 | Open |  |  | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . Records of stariner / pressure gauge checked and found incomplete | 4.2 | Maintenance activities reviewed | 1630 | PARADEEP TERMINAL | Suggested ready schedule available at all the time | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153005 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153005 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153005 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153005 |  | AUD-2026-09-2000017553ACN-2026-09-4000153005 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153006 | Open |  |  | Reviewed . | 4.3 | Project progress reviewed | 1630 | PARADEEP TERMINAL | TK2 is ready and under hydrotesting . Location advised to speed up all jobs of tank conversion and commissioning of TK2 and completion of TK15&16 | SOD | Marketing | ECZ | 2026-12-30 |  | 6 |  | S3 | F2 | 2026-12-30 | AUD-2026-09-2000017553ACN-2026-09-4000153006 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153006 | 2026-08-20 17:50 | 60.0108 | 485 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153006 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153006 |  | AUD-2026-09-2000017553ACN-2026-09-4000153006 | 21 |  | 27 | 80 | 11 | 11 | 70
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153007 | Open |  |  | Scrap disposal of pending Pipe material & other misc. fixed assets items valuation done. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1630 | PARADEEP TERMINAL | RFD to be made & disposal to be done . Also some other fixed asset items not in usable condition like RIM SEAL panel in planning room , valves , found to be included in RFD | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153007 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153007 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153007 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153007 |  | AUD-2026-09-2000017553ACN-2026-09-4000153007 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-09-4000153008 | Open |  |  | MFM used only for IOC -marketing terminal PLT . However during refinery PLT, CTMS display not available | 5.1 | MFM based accounting at Pipeline and OMC location | 1630 | PARADEEP TERMINAL | Talk to IOC for taking feed of CTMS display to avoid losses | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153008 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153008 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153008 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153008 |  | AUD-2026-09-2000017553ACN-2026-09-4000153008 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153009 | Open |  |  | At far end of hydrant line header , pressure found to be 11 kg compare to 9-9.5 kg at fire engine shed . | 6.1 |  | 1630 | PARADEEP TERMINAL | Advised to check PTs and check the setting of jockey pumps to reduce far end pressure to 8.5-9 kg | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153009 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153009 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153009 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153009 |  | AUD-2026-09-2000017553ACN-2026-09-4000153009 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153010 | Open |  |  | one non-FLP panel of 50 KVA DGSET found in battery room. | 6.2 |  | 1630 | PARADEEP TERMINAL | Location either remove the panel or make it FLP | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153010 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153010 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153010 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153010 |  | AUD-2026-09-2000017553ACN-2026-09-4000153010 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153011 | Open |  |  | HSD Expressway ( 2 nos.) found to be idling most of the time | 6.3 |  | 1630 | PARADEEP TERMINAL | suggested that SKO loading arms and MFM can be used to provide MS loading points to utilize 2 bays fully | SOD | Marketing | ECZ | 2026-12-30 |  | 6 |  | S3 | F2 | 2026-12-30 | AUD-2026-09-2000017553ACN-2026-09-4000153011 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153011 | 2026-08-20 17:50 | 60.0108 | 485 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153011 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153011 |  | AUD-2026-09-2000017553ACN-2026-09-4000153011 | 21 |  | 27 | 80 | 11 | 11 | 70
[5 empty] | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153012 | Open |  |  | 1. Proper painting and Tagging of R1, R2 & R3 , KEY BOX to be done for identification and visibility. 2. Planning Room needs to be properly organised and also the acess needs to be review to avoid unwanted acess . | 6.4 |  | 1630 | PARADEEP TERMINAL | as per the Observation comments | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153012 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153012 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153012 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153012 |  | AUD-2026-09-2000017553ACN-2026-09-4000153012 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152396 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Interaction done with all present Officers and new joined officers . Department wise Training to new officer needs to be given . Itis observed that all offers needs to fixed their daily jobs clearly . Standard scheduled to be prepared for contract workmen also . | 1.1 | Interaction with all officers (1–1.5 hrs) | 1630 | PARADEEP TERMINAL | 1. Contract workmen schedule to be prepare weekly/monthly and same to be shared with contract supervisor for effective monitoring and fixing the role and responsibilty of the jobs allotted to them 2. Each department must prepare the departmentwise list of recordsunder them .A masterlist of record must be maintain with LIC . Learning diary to be maintain . | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000152396 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000152396 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000152396 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000152396 |  | AUD-2026-09-2000017451ACN-2026-09-4000152396 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152397 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Review of major KPIs of stock loss , Scrap disposal , M&I , Projects discussed of tank conversion discussed . Advised to commissioned TK2 . Tank wagon gantry- Observed lot of scrap hoses were lying at the gantry. Hoses were found without cap. Other end of the Connected Hoses were on the ground needs to be hang. | 1.2 | Performance review conducted | 1630 | PARADEEP TERMINAL | 1.Stock loss - Stock loss in ethanol & MS is beyond AOP target . Location need to check the areas of losses & take action. 2. Scrap disposal - Advised to segrregate the scrap in the scrap yard . RFD to be made & disposed 3. Receiipt of PWD payment made outsideterminal of Rs.1 Cr to be taken 4. Housekeeping to be improved in operating area-Visitor Lobby .5.Scrap hoses needs to be shiftedand only usable hose to be kept at TW gantry. location to ensure that all the hoses must be capped all the time when not in use. Location advises to make a hose collar stand. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000152397 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000152397 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000152397 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000152397 |  | AUD-2026-09-2000017451ACN-2026-09-4000152397 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152398 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Reviewed . Old Toll tax payments of transporters , route corrections , etc | 1.3 | Pending issues reviewed | 1630 | PARADEEP TERMINAL | Old cases of toll tax and route correction to be completed by 30.9.26 | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000152398 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000152398 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000152398 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000152398 |  | AUD-2026-09-2000017451ACN-2026-09-4000152398 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152399 | Open | KANNANTHARA SOORAJ | 2026-09-15 | 1. TTLF Gantry efficiency to be improved and Day End TLF Report: MFM vs BCU and inventory differences are observed, particularly MS, HSD and Ethanol. 2. All officers to be rotated and should know all jobs in terminal . Local Loading: should be avoided . 3. SOP for pipeline receipt to be made with OMC members and also the clear understanding for the coastal receipts .43. MFM K Factor: Significant factors noted, including Ethanol 0.965/1.068 and B5 1.068, with LP 21/22 values blank | 1.8 | Improvement plans discussed | 1630 | PARADEEP TERMINAL | 1. TTLF loading performance to meet SBU target .Reconcile bay-wise MFM/BCU/invoice/inventory differences and verify meter/totalizercalibration. 2. Officer rotations , particularly in ethanol handling Check preset configuration, totalizer accuracy and prover results 3. SOP with OMC for PLT receipt to avoid losses . 4.Validate calibration, approved K-factor changes and system master data. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000152399 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000152399 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000152399 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000152399 |  | AUD-2026-09-2000017451ACN-2026-09-4000152399 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153050 | Open | KANNANTHARA SOORAJ | 2026-09-15 | HVLR for MS and ethanol tank was checked and found okay . Nomenclature to be mentioned | 2.2 | Double contingency scenario simulated; observations recorded | 1630 | PARADEEP TERMINAL | Foam hoses to be positioned properly. Hydrant hoses boxes glass were found missing needs to be fixed. HVLR numbering with connectedmust be display | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153050 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153050 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153050 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153050 |  | AUD-2026-09-2000017451ACN-2026-09-4000153050 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153051 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Lux level checked and found low level at TT gantry , Control room (290), security cabin , secondary road . | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1630 | PARADEEP TERMINAL | Installation of LED lights on existing HMT and additional light poles is in progress. Location advised to get the Lux level checkedfrom same party who has provided design | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153051 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153051 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153051 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153051 |  | AUD-2026-09-2000017451ACN-2026-09-4000153051 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153052 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1630 | PARADEEP TERMINAL | Location advised to inform security DGR owner to carry out inspection in night & have record of the same . Also advised to carry out mock drill in night | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153052 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153052 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153052 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153052 |  | AUD-2026-09-2000017451ACN-2026-09-4000153052 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153053 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Checked and found okay but At the entrance one access control turnstile was not working, needs to be repaired. | 2.8 | Access control systems checked | 1630 | PARADEEP TERMINAL | one access control turnstile was not working, needs to be repaired. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153053 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153053 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153053 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153053 |  | AUD-2026-09-2000017451ACN-2026-09-4000153053 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153054 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Verified and found okay . AFFF-21 kl , ARFFF-9 KL | 2.9 | Foam inventory verified | 1630 | PARADEEP TERMINAL | Advised To put the Tank NO, Details, type of foam, Inlet/outlet valve valves numbers to be display. Tank colour coding needs to be followed. Tank numbers to be painted. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153054 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153054 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153054 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153054 |  | AUD-2026-09-2000017451ACN-2026-09-4000153054 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153055 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1630 | PARADEEP TERMINAL | advised to procure the same urgently | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153055 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153055 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153055 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153055 |  | AUD-2026-09-2000017451ACN-2026-09-4000153055 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153056 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Checked . Route deviation voilation & unauthorized stoppages found . ATF TTs to Ranchi , stoppage voilation found diversion from route | 3.3 | VTS deviations reviewed | 1630 | PARADEEP TERMINAL | Route correction in some cases & stoppages voilation (other than authorized) to be stopped | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153056 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153056 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153056 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153056 |  | AUD-2026-09-2000017451ACN-2026-09-4000153056 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153057 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Checking each TTs of ethanol and Initial and Final Dips are being recorded . | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1630 | PARADEEP TERMINAL | Advised location to carry out analysis of all ethanol TTs stock loss variation during unloading by tank dips and check suspected TTs in calibration and make one record of all suppliers. Also action against deflauter TTs to be taken by suppliers and same TTs shallnot be operated in Industry .Action on TT needs to be updated on IEMS portal in coordination with HQO | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153057 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153057 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153057 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153057 |  | AUD-2026-09-2000017451ACN-2026-09-4000153057 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153058 | Open | KANNANTHARA SOORAJ | 2026-09-15 | TK 4 -HSD : Phy-2288, T-32'c / TAS - 2288.0, T-32.5( R-9390/OR-9382) TK 14 -MS : Phy - 5892.0,W-2.0, T-30.0/TAS - 5891.2, T-29.8, W- 2.0 cm (R-1183/OR-1183.2) | 3.7 | Inventory physical dip of minimum two tanks taken | 1630 | PARADEEP TERMINAL | Minor variation found in Ref.height of Tank 4 TO BE CORRECTED | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153058 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153058 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153058 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153058 |  | AUD-2026-09-2000017451ACN-2026-09-4000153058 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153059 | Open | KANNANTHARA SOORAJ | 2026-09-15 | daily reco sheet checked | 3.8 | Auto vs Manual reconciliation checked | 1630 | PARADEEP TERMINAL | Stock loss of Ethanol and MS is beyond the target , location required to pay full attention on Ethanol TT unloading and PLT receiptfrom IOC to cover up losses by month end .Locations should investigate root cause, reconcile records, validate calibration/K-factors and confirm corrective action with evidence.Location is advised to keep the daily Day end signed report | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153059 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153059 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153059 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153059 |  | AUD-2026-09-2000017451ACN-2026-09-4000153059 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153060 | Open | KANNANTHARA SOORAJ | 2026-09-15 | 1. SKO dye mixing equipement surplus after location made SKO free 2. RIM seal protection system one old panel is lying idle at first floor of planning room, to be removed and disposed | 3.9 | Abnormal variations / unused assets reviewed | 1630 | PARADEEP TERMINAL | 1. this facility to be offered to HQO for utilization at other locations 2. disposal to be done | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153060 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153060 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153060 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153060 |  | AUD-2026-09-2000017451ACN-2026-09-4000153060 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153061 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Needs overall improvement - Paining need | 3.15 | Housekeeping & PPE usage checked | 1630 | PARADEEP TERMINAL | Housekeeping to be done . Painting at Immediately painting and cleaning of Visitor room, Planning room etc | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153061 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153061 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153061 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153061 |  | AUD-2026-09-2000017451ACN-2026-09-4000153061 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153062 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Railway siding vegitation on other side of track and also near ETP advised to remove | 3.16 | Earth pits / boundary / vegetation control checked | 1630 | PARADEEP TERMINAL | yes | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153062 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153062 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153062 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153062 |  | AUD-2026-09-2000017451ACN-2026-09-4000153062 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153063 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Compliance status reviewed . OISD compliances of 2 points AND 6 NOS. FOR SSA pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1630 | PARADEEP TERMINAL | advised to comply by 30.9.2026 | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153063 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153063 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153063 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153063 |  | AUD-2026-09-2000017451ACN-2026-09-4000153063 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153064 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Transporters meeting done on 20.08.2026 | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1630 | PARADEEP TERMINAL | Transporter - safety during transit advised . Transporters required to provide safe route in rayagada route to avoid unsafe Ghat section. Toll tax payments | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153064 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153064 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153064 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153064 |  | AUD-2026-09-2000017451ACN-2026-09-4000153064 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153065 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1630 | PARADEEP TERMINAL | XX | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153065 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153065 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153065 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153065 |  | AUD-2026-09-2000017451ACN-2026-09-4000153065 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153066 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . Records of stariner / pressure gauge checked and found incomplete | 4.2 | Maintenance activities reviewed | 1630 | PARADEEP TERMINAL | Suggested ready schedule available at all the time | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153066 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153066 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153066 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153066 |  | AUD-2026-09-2000017451ACN-2026-09-4000153066 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153067 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Reviewed . | 4.3 | Project progress reviewed | 1630 | PARADEEP TERMINAL | TK2 is ready and under hydrotesting . Location advised to speed up all jobs of tank conversion and commissioning of TK2 and completion of TK15&16 | SOD | Marketing | ECZ | 2026-12-30 |  | 6 |  | S3 | F2 | 2026-12-30 | AUD-2026-09-2000017451ACN-2026-09-4000153067 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153067 | 2026-08-20 17:50 | 60.0108 | 485 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153067 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153067 |  | AUD-2026-09-2000017451ACN-2026-09-4000153067 | 21 |  | 27 | 80 | 11 | 11 | 70
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153068 | Open | KANNANTHARA SOORAJ | 2026-09-15 | Scrap disposal of pending Pipe material & other misc. fixed assets items valuation done. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1630 | PARADEEP TERMINAL | RFD to be made & disposal to be done . Also some other fixed asset items not in usable condition like RIM SEAL panel in planning room , valves , found to be included in RFD | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153068 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153068 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153068 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153068 |  | AUD-2026-09-2000017451ACN-2026-09-4000153068 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-09-4000153069 | Open | KANNANTHARA SOORAJ | 2026-09-15 | MFM used only for IOC -marketing terminal PLT . However during refinery PLT, CTMS display not available | 5.1 | MFM based accounting at Pipeline and OMC location | 1630 | PARADEEP TERMINAL | Talk to IOC for taking feed of CTMS display to avoid losses | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153069 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153069 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153069 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153069 |  | AUD-2026-09-2000017451ACN-2026-09-4000153069 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153070 | Open | KANNANTHARA SOORAJ | 2026-09-15 | At far end of hydrant line header , pressure found to be 11 kg compare to 9-9.5 kg at fire engine shed . | 6.1 | FIRE HYDRANT LINE PRESSURE | 1630 | PARADEEP TERMINAL | Advised to check PTs and check the setting of jockey pumps to reduce far end pressure to 8.5-9 kg | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153070 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153070 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153070 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153070 |  | AUD-2026-09-2000017451ACN-2026-09-4000153070 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153071 | Open | KANNANTHARA SOORAJ | 2026-09-15 | one non-FLP panel of 50 KVA DGSET found in battery room. | 6.2 | Battery room of control room | 1630 | PARADEEP TERMINAL | Location either remove the panel or make it FLP | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153071 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153071 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153071 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153071 |  | AUD-2026-09-2000017451ACN-2026-09-4000153071 | 21 |  | 27 | 80 | 11 | 11 | 61
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153072 | Open | KANNANTHARA SOORAJ | 2026-09-15 | HSD Expressway ( 2 nos.) found to be idling most of the time | 6.3 | Gantry Infrastructure | 1630 | PARADEEP TERMINAL | suggested that SKO loading arms and MFM can be used to provide MS loading points to utilize 2 bays fully | SOD | Marketing | ECZ | 2026-12-30 |  | 6 |  | S3 | F2 | 2026-12-30 | AUD-2026-09-2000017451ACN-2026-09-4000153072 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153072 | 2026-08-20 17:50 | 60.0108 | 485 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153072 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153072 |  | AUD-2026-09-2000017451ACN-2026-09-4000153072 | 21 |  | 27 | 80 | 11 | 11 | 70
|  |  |  | OPEN | 1630_Q2_SENIOR_MANAGEMENT_INSPETION | 2026-08-20 | AUD-2026-09-2000017451 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153073 | Open | KANNANTHARA SOORAJ | 2026-09-15 | 1. Proper painting and Tagging of R1, R2 & R3 , KEY BOX to be done for identification and visibility. 2. Planning Room needs to be properly organised and also the acess needs to be review to avoid unwanted acess . | 6.4 | Gate entrance area | 1630 | PARADEEP TERMINAL | as per the Observation comments | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017451ACN-2026-09-4000153073 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017451ACN-2026-09-4000153073 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017451 - ACN-2026-09-4000153073 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017451ACN-2026-09-4000153073 |  | AUD-2026-09-2000017451ACN-2026-09-4000153073 | 21 |  | 27 | 80 | 11 | 11 | 61
[5 empty] | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152240 | Open |  |  | Closure of Project | 1.3 | Pending issues reviewed | 1551 | VASCO BLACK OIL TERMINAL | XX | SOD | Marketing | WZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017902ACN-2026-09-4000152240 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152240 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152240 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152240 |  | AUD-2026-09-2000017902ACN-2026-09-4000152240 | 21 |  | 27 | 80 | 31 | 31 | 57
|  |  |  | H1 Order processed | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152241 | Open | E PAULMURUGAN | 2026-09-16 | CCTV System available & maintained by ZIAVPL/ Discussed to procure locally for Vasco BOT | 2.6 | CCTV functioning checked | 1551 | VASCO BLACK OIL TERMINAL | Advised to procure locally and to submit proposal for budget | SOD | Marketing | WZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017902ACN-2026-09-4000152241 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152241 | 2026-09-04 | 45.7538 | 486 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152241 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152241 |  | AUD-2026-09-2000017902ACN-2026-09-4000152241 | 21 |  | 27 | 80 | 31 | 31 | 70
|  |  |  | Transporter rectified and shown the earthing made bet Chassis and body | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152242 | Open | E PAULMURUGAN | 2026-09-16 | YES. Checked randomly 2 TTs out of which one TT GA07F8288 chasis to Body earthing was missing | 3.1 | TT fittings & discipline checked | 1551 | VASCO BLACK OIL TERMINAL | Advised to rectify | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017902ACN-2026-09-4000152242 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152242 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152242 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152242 |  | AUD-2026-09-2000017902ACN-2026-09-4000152242 | 21 |  | 27 | 80 | 31 | 31 | 57
|  |  |  | All vegetations cleared | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152243 | Open | E PAULMURUGAN | 2026-09-16 | Transformer yard found with grass | 3.16 | Earth pits / boundary / vegetation control checked | 1551 | VASCO BLACK OIL TERMINAL | Advised to remove grass | SOD | Marketing | WZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017902ACN-2026-09-4000152243 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152243 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152243 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152243 |  | AUD-2026-09-2000017902ACN-2026-09-4000152243 | 21 |  | 27 | 80 | 31 | 31 | 57
|  |  |  | Being attended one by one | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152244 | Open | E PAULMURUGAN | 2026-09-16 | Pending points were discussed | 3.18 | OISD/MDSA/SSA compliance reviewed | 1551 | VASCO BLACK OIL TERMINAL | Advised to take action to close at the earliest | SOD | Marketing | WZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017902ACN-2026-09-4000152244 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152244 | 2026-09-04 | 45.7538 | 425 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152244 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152244 |  | AUD-2026-09-2000017902ACN-2026-09-4000152244 | 21 |  | 27 | 80 | 31 | 31 | 61
[5 empty] | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152245 | Open |  |  | YES | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1551 | VASCO BLACK OIL TERMINAL | Advised location to do painting walk way approach painting to Tanks | SOD | Marketing | WZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017902ACN-2026-09-4000152245 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152245 | 2026-09-04 | 45.7538 | 425 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152245 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152245 |  | AUD-2026-09-2000017902ACN-2026-09-4000152245 | 21 |  | 27 | 80 | 31 | 31 | 61
|  |  |  | Completed 96% | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152246 | Open | E PAULMURUGAN | 2026-09-16 | Yes | 4.3 | Project progress reviewed | 1551 | VASCO BLACK OIL TERMINAL | To close by Sep 2026 | SOD | Marketing | WZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017902ACN-2026-09-4000152246 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152246 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152246 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152246 |  | AUD-2026-09-2000017902ACN-2026-09-4000152246 | 21 |  | 27 | 80 | 31 | 31 | 57
[5 empty] | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152247 | Open |  |  | Yes at Vasco BOT | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1551 | VASCO BLACK OIL TERMINAL | To close by Dec 2026 | SOD | Marketing | WZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017902ACN-2026-09-4000152247 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152247 | 2026-09-04 | 45.7538 | 486 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152247 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152247 |  | AUD-2026-09-2000017902ACN-2026-09-4000152247 | 21 |  | 27 | 80 | 31 | 31 | 70
[5 empty] | GM INSPECTION_VASCO BOT_SEP26 | 2026-09-04 | AUD-2026-09-2000017902 | 2026-09-03 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152248 | Open |  |  | Tel Tale clockes were not working | 6 | Security alertness checked | 1551 | VASCO BLACK OIL TERMINAL | Advised location to take it up with eqipment supplier to put the system into back or Buy new system available in the market which ever is cost effective and easy to install painting walk way approach painting to Tanks | SOD | Marketing | WZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017902ACN-2026-09-4000152248 | GA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017902ACN-2026-09-4000152248 | 2026-09-04 | 45.7538 | 425 | >20 | AUD-2026-09-2000017902 - ACN-2026-09-4000152248 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017902ACN-2026-09-4000152248 |  | AUD-2026-09-2000017902ACN-2026-09-4000152248 | 21 |  | 27 | 80 | 31 | 31 | 61
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153083 | Open |  |  | MOVs & valves are in unused state for long time | 3.9 | Abnormal variations / unused assets reviewed | 1504 | MIRAJ TERMINAL | Location should declare such assets as surplus asset and confirm | SOD | Marketing | WZ | 2026-11-30 |  | 5 |  | S1 | F5 | 2026-11-30 | AUD-2026-09-2000017453ACN-2026-09-4000153083 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153083 | 2026-09-01 | 48.7538 | 455 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153083 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153083 |  | AUD-2026-09-2000017453ACN-2026-09-4000153083 | 21 |  | 27 | 80 | 0 | -1 | 65
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153085 | Open |  |  | Double hydrant provided in TT parking area was found without key to its hose box | 6.2 | Key for hose box of hydrant monitors | 1504 | MIRAJ TERMINAL | Location should ensure key to be provided to hose box | SOD | Marketing | WZ | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017453ACN-2026-09-4000153085 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153085 | 2026-09-01 | 48.7538 | 425 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153085 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153085 |  | AUD-2026-09-2000017453ACN-2026-09-4000153085 | 21 |  | 27 | 80 | 0 | -1 | 61
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153086 | Open |  |  | Loose soil is found at TT gantry | 6.3 | Housekeeping in TT gantry area | 1504 | MIRAJ TERMINAL | Location must remove such loose soil to avoid operational hazard during TT loading at gantry | SOD | Marketing | WZ | 2026-11-30 |  | 5 |  | S1 | F5 | 2026-11-30 | AUD-2026-09-2000017453ACN-2026-09-4000153086 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153086 | 2026-09-01 | 48.7538 | 455 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153086 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153086 |  | AUD-2026-09-2000017453ACN-2026-09-4000153086 | 21 |  | 27 | 80 | 0 | -1 | 65
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153087 | Open |  |  | Bottom loading hoses are found to be kept at it's specified stand at each & every bay. However few of the stands are seen to be loosely held from foundation/ground surface | 6.4 | Bottom loading hose in TT gantry bay area | 1504 | MIRAJ TERMINAL | Location should ensure proper grouting of all loading arms stands at each & every bay | SOD | Marketing | WZ | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017453ACN-2026-09-4000153087 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153087 | 2026-09-01 | 48.7538 | 425 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153087 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153087 |  | AUD-2026-09-2000017453ACN-2026-09-4000153087 | 21 |  | 27 | 80 | 0 | -1 | 61
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153088 | Open |  |  | Walkways & valve operating area structure are seen to be corroded | 6.5 | Gratings & structural painting | 1504 | MIRAJ TERMINAL | Location must carry out painting to the prescribed walkways, valve/monitor operating platforms | SOD | Marketing | WZ | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-09-2000017453ACN-2026-09-4000153088 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153088 | 2026-09-01 | 48.7538 | 486 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153088 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153088 |  | AUD-2026-09-2000017453ACN-2026-09-4000153088 | 21 |  | 27 | 80 | 0 | -1 | 70
[5 empty] | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153089 | Open |  |  | Earthing strip is provided under Ethanol unloading shed for Ethanol TTs. However it is seen to be of shorter length | 6.6 | Extending earthing strips | 1504 | MIRAJ TERMINAL | Location should extend the earthing strip enough for Ethanol TTs to provide earthing without any hindrance | SOD | Marketing | WZ | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017453ACN-2026-09-4000153089 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153089 | 2026-09-01 | 48.7538 | 425 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153089 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153089 |  | AUD-2026-09-2000017453ACN-2026-09-4000153089 | 21 |  | 27 | 80 | 0 | -1 | 61
|  | KANNANTHARA SOORAJ | 2026-09-16 |  | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152985 | Completed |  |  | Interaction done with all present Officers and new joined officers . Department wise Training to new officer needs to be given . Itis observed that all offers needs to fixed their daily jobs clearly . Standard scheduled to be prepared for contract workmen also . | 1.1 | Interaction with all officers (1–1.5 hrs) | 1630 | PARADEEP TERMINAL | 1. Contract workmen schedule to be prepare weekly/monthly and same to be shared with contract supervisor for effective monitoring and fixing the role and responsibilty of the jobs allotted to them 2. Each department must prepare the departmentwise list of recordsunder them .A masterlist of record must be maintain with LIC . Learning diary to be maintain . | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152985 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152985 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152985 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152985 |  | AUD-2026-09-2000017553ACN-2026-09-4000152985 | 21 |  | 27 | 80 | 11 | 11 | 61
|  | KANNANTHARA SOORAJ | 2026-09-16 |  | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152989 | Completed |  |  | HVLR for MS and ethanol tank was checked and found okay . Nomenclature to be mentioned | 2.2 | Double contingency scenario simulated; observations recorded | 1630 | PARADEEP TERMINAL | Foam hoses to be positioned properly. Hydrant hoses boxes glass were found missing needs to be fixed. HVLR numbering with connectedmust be display | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152989 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152989 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152989 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152989 |  | AUD-2026-09-2000017553ACN-2026-09-4000152989 | 21 |  | 27 | 80 | 11 | 11 | 61
|  | KANNANTHARA SOORAJ | 2026-09-16 |  | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152993 | Completed |  |  | Verified and found okay . AFFF-21 kl , ARFFF-9 KL | 2.9 | Foam inventory verified | 1630 | PARADEEP TERMINAL | Advised To put the Tank NO, Details, type of foam, Inlet/outlet valve valves numbers to be display. Tank colour coding needs to be followed. Tank numbers to be painted. | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000152993 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000152993 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000152993 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000152993 |  | AUD-2026-09-2000017553ACN-2026-09-4000152993 | 21 |  | 27 | 80 | 11 | 11 | 61
|  | KANNANTHARA SOORAJ | 2026-09-16 |  | PARADEEP Q2-25-26-SR. MGMT INSPECT VISIT | 2026-08-20 17:50 | AUD-2026-09-2000017553 | 2026-08-19 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153000 | Completed |  |  | Needs overall improvement - Paining need | 3.15 | Housekeeping & PPE usage checked | 1630 | PARADEEP TERMINAL | Housekeeping to be done . Painting at Immediately painting and cleaning of Visitor room, Planning room etc | SOD | Marketing | ECZ | 2026-10-30 |  | 6 |  | S3 | F2 | 2026-10-30 | AUD-2026-09-2000017553ACN-2026-09-4000153000 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017553ACN-2026-09-4000153000 | 2026-08-20 17:50 | 60.0108 | 424 | >20 | AUD-2026-09-2000017553 - ACN-2026-09-4000153000 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017553ACN-2026-09-4000153000 |  | AUD-2026-09-2000017553ACN-2026-09-4000153000 | 21 |  | 27 | 80 | 11 | 11 | 61
MANKAR PRAFULLA | 2026-09-16 | KUMAR NITISH | 2026-09-16 | "25 Additional lights & 10 new poles provided wherever Lux level was not meeting norms vide PO No 5300041844 dated 22.12.2025.. Repair of old FLP & high mast lights done. Lux requirement meeting at all valve operating platforms for all tanks & road area. Last Lux Survey Report attached. " | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145694 | Closed | KUMAR NITISH | 2026-09-16 | Checked and found adequate at the fire engine shed. Inadequate in tank farm area. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2027-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2027-03-31 | AUD-2026-06-2000012346ACN-2026-07-4000145694 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145694 | 2026-09-18 | 31.7538 | 380 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145694 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145694 | AUD-2026-06-2000012346ACN-2026-07-4000145694 | 21 | 21 | 27 | 80 | 5 | 5 | 83 | 55
MANKAR PRAFULLA | 2026-09-16 | KUMAR NITISH | 2026-09-16 | "Audit complaince being done in time bound manner. OISD: 8 out of 29 Points Pending; EDC: 31.03.2027 MDSA 25-26: 26 out of 42 Points Pending; EDC: 31.03.2027 SMI Q4: 3 out of 13 Points Pending; EDC: 31.03.2027 SSA: 8 out of 78 Points Pending; EDC: 31.03.2027" | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145699 | Closed | KUMAR NITISH | 2026-09-16 | As per SAP, audit compliance is 39% for all audits (PM - MDSA Audit -28%, PM - OISD- External Safety Audit - 69%, PM - SAFE100 SelfSafety Audit - 86%, PM - Senior Management Inspection - 0%, PM - SOD TANK AG EFR - 12%, PM-HLSA - 0%). Location is required to closed audit observation on priority in field as well as in SAP. Sr Management and HLSA audit compliance is to be accorded priority incompliance. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1546 | Mundra Terminal-MDPL | Points scheduled for closure in Jun'26 and over due points shall be closed. | SOD | Marketing | NWR | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2027-03-31 | AUD-2026-06-2000012346ACN-2026-07-4000145699 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000145699 | 2026-09-18 | 31.7538 | 380 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000145699 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000145699 | AUD-2026-06-2000012346ACN-2026-07-4000145699 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 55
MANKAR PRAFULLA | 2026-09-16 | KUMAR NITISH | 2026-09-16 | Fire Engine cooling line connected to under ground water collection pit. PO No 5400437413 | SR. MANAGEMENT INSPECTION Q1 26-27 MUNDR | 2026-05-21 13:00 | AUD-2026-06-2000012346 | 2026-05-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146504 | Closed | KUMAR NITISH | 2026-09-16 | The fire engine water cooling line is connected to the suction header. It should be of free-fall type. | 6.3 |  | 1546 | Mundra Terminal-MDPL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-15 | AUD-2026-06-2000012346ACN-2026-07-4000146504 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012346ACN-2026-07-4000146504 | 2026-09-18 | 31.7538 | 380 | >20 | AUD-2026-06-2000012346 - ACN-2026-07-4000146504 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012346ACN-2026-07-4000146504 | AUD-2026-06-2000012346ACN-2026-07-4000146504 | 21 | 21 | 27 | 80 | 5 | 5 | 41 | 55
MANKAR PRAFULLA | 2026-09-16 | KUMAR NITISH | 2026-09-16 | Same Audit Point covered in SMI Inspection Q1 FY 26-27. Compliance being done in same. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125474 | Closed | KUMAR NITISH | 2026-09-16 | Yes done and all CCTVs (except 2 Nos) are in working condition with 92 dys backup. | 2.6 | CCTV functioning checked | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-08-31 | AUD-2026-03-2000010720ACN-2026-03-4000125474 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125474 | 2026-09-18 | 31.7538 | 380 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125474 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010720ACN-2026-03-4000125474 | AUD-2026-03-2000010720ACN-2026-03-4000125474 | 21 | 21 | 26 | 80 | 5 | 5 | 35 | 55
|  | KUSHAGRA VASHISHTH | 2026-09-17 | Phone calls are being attended at location and issues if any are attended. Complied and closed. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144673 | Completed | KUSHAGRA VASHISHTH | 2026-09-17 | Meeting carried out with dealers of Jodhpur-A sales area. Dealers appreciated the efforts made by HPCL for ensuring that no outlet is dry even during product crisis period of Apr26 and May26. Meeting was conducted with 26 dealers on 25th June physically at conference hall of Jodhpur IRD. There were complain of not responding phone call by planning officer. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1278 | JODHPUR TERMINAL | Location to ensure that each of the dealers are attended | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144673 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144673 | 2026-09-25 20:45 | 23.8893 | 333 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144673 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000015346ACN-2026-07-4000144673 |  | AUD-2026-07-2000015346ACN-2026-07-4000144673 | 21 |  | 27 | 80 | 0 | 0 | 48
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | application was returned by pesso citing manpower issue. new application will be inciated on appointment of additional manpower | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-06-4000137536 | Closed | JOSVIN SUNNY | 2026-09-15 | The compliance status of MDSA, SSA pending points are reviewed. Location to comply at the earliest. Already location has submitted application for PESO license extension for night operations. Inspection by PESO official completed | 1.3 | Pending issues reviewed | 1892 | KOZHIKODE DEPOT | XX | SOD | Marketing | CZR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137536 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137536 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137536 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013060ACN-2026-06-4000137536 | AUD-2026-06-2000013060ACN-2026-06-4000137536 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | "1. Appropriation of the NPCB 2026 projects has been completed 2. replacemnt of the sleeper is done through railway 3. Letter given to the district authority for conducting level 3 drill 4. list of critical equipments are maintained 5.checks has been done regularly 6.proper monitoring of the electrical consuption is done" | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-06-4000137540 | Closed | JOSVIN SUNNY | 2026-09-15 | 1. Discussed about timely action for approved NPCB Projects 2. Replacement of wooden sleepers at railway siding 3. Level III drill 4. Maintenance of critical Equipments 5. Electrical systems maintenance | 1.8 | Improvement plans discussed | 1892 | KOZHIKODE DEPOT | 1. Submit Appropriation request for approved NPCB 2026 projects and take action for floating of tender 2. Replacement of sleepers to be handled with all safety measures and without interputing regualr wagon operations. 3. Plan for off site Level III drill in cooridnation with District administration. Involve MARG members. 4. List out all SCEs (Safety critical Equipments) and monitor for uptime. Any bypass is to be brought to the attention of Zone and efforts shall be to restore them to normalcy at the earliest possibletime. Also, maintenance of equipments viz. VFDs, UPS, BB, FAP etc.are carried out at regualr intervals. Verify comprehensive AMC with Automation Vendors for scheduled maintenance of above equipments. 5. Transformer oil filtration / BDV check along with other Elctrical maintenance as per OISD 137 to be handled as per Schedule. 6. Monitor Electrical units closley w.r.t MD and take steps for imporving the KWH/KL performance. | SOD | Marketing | CZR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137540 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137540 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137540 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137540 | AUD-2026-06-2000013060ACN-2026-06-4000137540 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | all scm points are closed and drills are conduted for all erdmp scenarios | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137541 | Closed | JOSVIN SUNNY | 2026-09-15 | 1. Location has conducted Level II mock drill involving F&B department and Mutual aid group on ... 2. All mock fire drills are single cotingency. Observation recorded and corrective actions taken. Safety committee conducted on 19-03-2026. 7 Recommendation were recorded . 4 pending to be complied. | 2.2 | Double contingency scenario simulated; observations recorded | 1892 | KOZHIKODE DEPOT | Four safety committee pending points to be complied by 15-06-2026. Location to review all scenarios considered in ERDMP and conduct drills for all ERDMP scenarios. | SOD | Marketing | CZR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137541 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137541 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137541 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137541 | AUD-2026-06-2000013060ACN-2026-06-4000137541 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | all points are closed | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137544 | Closed | JOSVIN SUNNY | 2026-09-15 |  | 2.8 | Access control systems checked | 1892 | KOZHIKODE DEPOT | Comply HLSA recommendations in time bound manner. Draw action plan as per the guidelines on HLSA from HQO | SOD | Marketing | CZR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-30 | AUD-2026-06-2000013060ACN-2026-06-4000137544 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137544 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137544 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137544 | AUD-2026-06-2000013060ACN-2026-06-4000137544 | 21 | 21 | 27 | 80 | 2 | -4 | 52 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | currently gaurds are not having hazardous endorsment, will check with contracor while deploying new gaurds. | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137545 | Closed | JOSVIN SUNNY | 2026-09-15 | Not available | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1892 | KOZHIKODE DEPOT | Security Gaurds with HVD HZA endorsement to be identified | SOD | Marketing | CZR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137545 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137545 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137545 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137545 | AUD-2026-06-2000013060ACN-2026-06-4000137545 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | Monthly and Quartely reco as per HQO circulars is done | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137547 | Closed | JOSVIN SUNNY | 2026-09-15 |  | 3.7 | Inventory physical dip of minimum two tanks taken | 1892 | KOZHIKODE DEPOT | Continue with auto reco. And take steps in case of manlfunctioining of any TFMS equipments. Monthly and Quartely reco shall be as per HQO circulars | SOD | Marketing | CZR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013060ACN-2026-06-4000137547 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137547 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137547 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137547 | AUD-2026-06-2000013060ACN-2026-06-4000137547 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | Proper unloading and accounting of wagon receipts is ensured. | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000137548 | Closed | JOSVIN SUNNY | 2026-09-15 | No abnormal varioations reported | 3.9 | Abnormal variations / unused assets reviewed | 1892 | KOZHIKODE DEPOT | Closley monitor Stock variations during wagon receipts. Proper unloading and accounting of wagon receipts to be ensured. | SOD | Marketing | CZR | 2026-12-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-30 | AUD-2026-06-2000013060ACN-2026-06-4000137548 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137548 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137548 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137548 | AUD-2026-06-2000013060ACN-2026-06-4000137548 | 21 | 21 | 27 | 80 | 2 | -4 | 70 | 55
HARINIVAS S | 2026-09-17 | JOSVIN SUNNY | 2026-09-15 | timely closure of work permits are ensured in sap | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138602 | Closed | JOSVIN SUNNY | 2026-09-15 | Permits checked and available. Timely closure of permits are being done. | 4.2 | Maintenance activities reviewed | 1892 | KOZHIKODE DEPOT | Ensure timely closure of work permits in SAP also. | SOD | Marketing | CZR | 2026-12-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-30 | AUD-2026-06-2000013060ACN-2026-06-4000138602 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000138602 | 2026-09-17 16:00 | 32.0872 | 381 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000138602 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000138602 | AUD-2026-06-2000013060ACN-2026-06-4000138602 | 21 | 21 | 27 | 80 | 2 | -4 | 70 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Complied | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146468 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Interacted with all officers of terminal. Reviewed NPCB project status of current year and Last year were viewed & discussed on operational issues of terminal | 1.1 | Interaction with all officers (1–1.5 hrs) | 1940 | KADAPA DEPOT | Location to Take up with RM's regarding Late Hold release | SOD | Marketing | SCR | 2026-06-10 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-10 | AUD-2026-07-2000016565ACN-2026-07-4000146468 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146468 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146468 | 532 | 8294 | 21 | 8294 | 131 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146468 | AUD-2026-07-2000016565ACN-2026-07-4000146468 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Cable laying and panel integration works completed, Termination works under progress. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146469 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | NPCB Status of Projects reviewed and advised location to close projects by 30.06.2026 | 1.3 | Pending issues reviewed | 1940 | KADAPA DEPOT | LT Supply from VDPL – Intergration works , TAS Revamp, Ethanol TT free exit & Fire engine panel replacement, and PCSA Compliance tobe completed | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000016565ACN-2026-07-4000146469 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146469 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146469 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146469 | AUD-2026-07-2000016565ACN-2026-07-4000146469 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | All pending recommendations are completed and closed. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146470 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Pending points and status of SSA, MDSA and T4S were reviewed | 1.4 | Earlier action points status checked | 1940 | KADAPA DEPOT | Advised location to close all the recommendations by 30.08.2026 | SOD | Marketing | SCR | 2026-08-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-30 | AUD-2026-07-2000016565ACN-2026-07-4000146470 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146470 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146470 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146470 | AUD-2026-07-2000016565ACN-2026-07-4000146470 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Alternate arrangement for Fire fighting facility. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146471 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Budget for HVLR of New Ethanol TK- 401A and Fire Extinguisher replacement were identified | 1.5 | HQO / Zonal support required identified | 1940 | KADAPA DEPOT | Advised DGM-HSE to arrange for HVLR and to put up proposal for FE Replacement | SOD | Marketing | SCR | 2026-08-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-30 | AUD-2026-07-2000016565ACN-2026-07-4000146471 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146471 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146471 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146471 | AUD-2026-07-2000016565ACN-2026-07-4000146471 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Complied | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146472 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Stock Loss Target to be Met, COLA/OLA traget to be Met.Closed Location Guntakal Idel Assests (Land and Staff Quarter) Proposal to be submitted, Updation of TT Inspection In SAP Target to be Met.Complinace sheet to be filed for all internal and external safety Audit, OCC Tickets timely closing - Less than 4 days, Pending toll claims to be cleared by month end | 1.8 | Improvement plans discussed | 1940 | KADAPA DEPOT | All the AOP parameters to be met as the target dates given | SOD | Marketing | SCR | 2026-08-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-30 | AUD-2026-07-2000016565ACN-2026-07-4000146472 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146472 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146472 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146472 | AUD-2026-07-2000016565ACN-2026-07-4000146472 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | All the observed shortcomings are covered in subsequent mock drills. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146473 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | As per DCIF the following Observation were recorded 1.Communication between teams to be improved 2.Standby personnel near WCFM in leakage spot was not ensured 3.Gully sucker should placed along NS Direction | 2.2 | Double contingency scenario simulated; observations recorded | 1940 | KADAPA DEPOT | Location to practice Mock drills for the shortcomings observed in the fire mock drill | SOD | Marketing | SCR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000016565ACN-2026-07-4000146473 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146473 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146473 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146473 | AUD-2026-07-2000016565ACN-2026-07-4000146473 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | All the missing items are procured in the emergency trolley. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146474 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Reviewed emergency trolley equipment &observed items like Non Spraking tool Kit, Tester and Mega phone Found Missing. | 2.5 | Emergency response preparedness reviewed | 1940 | KADAPA DEPOT | Location to ensure avaialblity of all items as per OISD STD 117 | SOD | Marketing | SCR | 2026-08-10 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-10 | AUD-2026-07-2000016565ACN-2026-07-4000146474 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146474 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146474 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146474 | AUD-2026-07-2000016565ACN-2026-07-4000146474 | 21 | 21 | 27 | 80 | 0 | 0 | 49 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | ALL the non Functional cctv camera made operational. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146475 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | CCTV fucntioning cheked and observed that 53 camera are working out of 60 no's. Following Observation were noted while reviewing cctv Recording -1. TT Parking area PTZ camera found non operational 2. blurness observed in 4 perimeter cameras 3. Bay 11 & 12 CCTV position to be reviewed and rectified 4. siding area 2 PTZ camera were non functional 5.CCTV not covered for Security Check at TT Parking | 2.6 | CCTV functioning checked | 1940 | KADAPA DEPOT | ALL the non Functional cctv camera to be rectified immedaitely and discrepancies to be attended immediately by 30.07.2026 | SOD | Marketing | SCR | 2026-07-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-30 | AUD-2026-07-2000016565ACN-2026-07-4000146475 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146475 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146475 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146475 | AUD-2026-07-2000016565ACN-2026-07-4000146475 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | LIC Master key sent to M/s.sterna for replacement. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146476 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | EM locks of 5 TTs checked TT nos. AP39WJ 1218, AP39TC 8346, AP39VC 0858,AP39UZ 6369, AP16TH9544 and found satisfactory . Observed LIC Master key is not functioning properly | 3.5 | EM Lock SOP compliance verified | 1940 | KADAPA DEPOT | Advised LIC Master key to sent back to M/s.sterna for replacement | SOD | Marketing | SCR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000016565ACN-2026-07-4000146476 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146476 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146476 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146476 | AUD-2026-07-2000016565ACN-2026-07-4000146476 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Location has taken up with TAS vendor and ensured that variations in tank temp are with in tolerance limit . | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146477 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Physical dip has been checked for TK 101A and TK 201A Tank 101A- Physical dip of 148.3 cms against TAS dip of 148.5. Water physicaldip observed 0.0 cms against TAS dip of 0.0 cms . Tank 201A- Physical dip of 1216.6 cms against TAS dip of 1216.7cms . Water physical dip observed 0.0 cms against TAS dip of 0.0 cms Variation : nil. Tank 101A tank physical temp 33.0 deg c against TAS temp of 35.0deg c . Tank 201A tank physical temp 37.0 deg C against TAS temp of 30.0 deg c. | 3.7 | Inventory physical dip of minimum two tanks taken | 1940 | KADAPA DEPOT | Location to take up with TAS vendor and ensure that variations in tank temp remain with in tolerance limit . | SOD | Marketing | SCR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000016565ACN-2026-07-4000146477 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146477 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146477 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146477 | AUD-2026-07-2000016565ACN-2026-07-4000146477 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Location is maintaining records. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146478 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Critical alarms are checked. Remarks are not entered while acknowleding the critical remarks mentioning the reason for critical alarm | 3.12 | Critical alarms checked & corrective actions reviewed | 1940 | KADAPA DEPOT | Location to enter remarks and maintain records with root cause of critical alarms | SOD | Marketing | SCR | 2026-06-10 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-10 | AUD-2026-07-2000016565ACN-2026-07-4000146478 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146478 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146478 | 532 | 8294 | 21 | 8294 | 131 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146478 | AUD-2026-07-2000016565ACN-2026-07-4000146478 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | All pending points are Complied. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146479 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | MDSA and SSA compliance reviewed. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1940 | KADAPA DEPOT | SSA 5 pending points and MDSA- 4 pending points to be complied by 30.08.2026 | SOD | Marketing | SCR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-08-30 | AUD-2026-07-2000016565ACN-2026-07-4000146479 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146479 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146479 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146479 | AUD-2026-07-2000016565ACN-2026-07-4000146479 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | LT Supply from VDPL – completed , TAS Revamp - work is in progress, Ethanol TT free exit & Fire engine panel replacement, and PCSA Compliance are completed. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146480 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | NPCB Status of Projects reviewed and advised location to close projects by 30.06.2026 | 4.3 | Project progress reviewed | 1940 | KADAPA DEPOT | LT Supply from VDPL – Intergration works , TAS Revamp, Ethanol TT free exit & Fire engine panel replacement, and PCSA Compliance tobe completed | SOD | Marketing | SCR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000016565ACN-2026-07-4000146480 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146480 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146480 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146480 | AUD-2026-07-2000016565ACN-2026-07-4000146480 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Work is in progress. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146481 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | RO and Terminal Misc Scrap was Observed | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1940 | KADAPA DEPOT | Location to Ensure Scrap Free by 31.12.2026 | SOD | Marketing | SCR | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-12-31 | AUD-2026-07-2000016565ACN-2026-07-4000146481 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146481 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146481 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146481 | AUD-2026-07-2000016565ACN-2026-07-4000146481 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Complied. | AUDIT UPLOAD IN SAP | 2026-06-05 19:00 | AUD-2026-07-2000016565 | 2026-06-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-07-4000146482 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Closure of SSA/ MDSA Points, Scrap Liquidation, M&I projects execution, Dormant Keys & Locks, CCTV Cameras | 5.1 | High priority areas requiring immediate action. | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-07-2000016565ACN-2026-07-4000146482 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016565ACN-2026-07-4000146482 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-07-2000016565 - ACN-2026-07-4000146482 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016565ACN-2026-07-4000146482 | AUD-2026-07-2000016565ACN-2026-07-4000146482 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | All Audits points complied | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123015 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Pending points and status of SSA & MDSA | 1.4 | Earlier action points status checked | 1940 | KADAPA DEPOT | Action to be taken on the pending SSA & MDSA Points. Self Safety audit- 8 points , MDSA- 10 points . Compliance of pending points to be completed as per the given target dates. | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010862ACN-2026-03-4000123015 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123015 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123015 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123015 | AUD-2026-03-2000010862ACN-2026-03-4000123015 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Emergency trolley regularly inspected & all equipment are available | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123021 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Reviewed emergency trolley equipment. Some of the items were not placed at respective places and not in the designated compartments. Interacted with officers & security personnel about their roles and resposibilities during emergencies. Emergency gate opened and checked. | 2.5 | Emergency response preparedness reviewed | 1940 | KADAPA DEPOT | Emergency trolley to be regularly inspected & all equipment to be placed at their designated compartments. Live fire traininng to be imparted to all contract workmen. | SOD | Marketing | SCR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000010862ACN-2026-03-4000123021 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123021 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123021 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123021 | AUD-2026-03-2000010862ACN-2026-03-4000123021 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | critical alarms records are being maintained | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123031 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Critical alarms are checked. Remarks are not entered while acknowleding the critical remarks mentioning the reason for critical alarm | 3.12 | Critical alarms checked & corrective actions reviewed | 1940 | KADAPA DEPOT | Location to enter remarks and maintain records with root cause of critical alarms | SOD | Marketing | SCR | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123031 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123031 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123031 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123031 | AUD-2026-03-2000010862ACN-2026-03-4000123031 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-18 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | all pending points are complied | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123035 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Nil OISD pending points. MDSA and SSA compliance reviewed. Pending points to be complied as per timelines | 3.18 | OISD/MDSA/SSA compliance reviewed | 1940 | KADAPA DEPOT | Action to be taken on the pending SSA & MDSA Points. Self Safety audit- 8 points , MDSA- 10 points | SOD | Marketing | SCR | 2027-05-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2027-05-31 | AUD-2026-03-2000010862ACN-2026-03-4000123035 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123035 | 2026-08-20 11:30 | 60.2747 | 382 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123035 | 532 | 8294 | 21 | 8294 | -223 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123035 | AUD-2026-03-2000010862ACN-2026-03-4000123035 | 21 | 21 | 26 | 80 | 0 | 0 | 91 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Pursuant to the review of key performance indicators, the ETP project identified for expedition has since been completed by 31.07.2026. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122609 | Closed | KUMAR RAJU | 2026-09-14 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed | 1.2 | Performance review conducted | 1712 | BARAUNI POL IRD | ETP project jobs to be expedited | SOD | Marketing | PZR | 2026-04-30 | THIRD PARTY ERRORS | 3 | PROCESS SAFETY | S3 | F1 | 2026-04-30 | AUD-2026-02-2000011302ACN-2026-03-4000122609 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122609 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122609 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122609 | AUD-2026-02-2000011302ACN-2026-03-4000122609 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The pending ETP project job identified during the review of outstanding issues has been completed by 31.07.2026. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122610 | Closed | KUMAR RAJU | 2026-09-14 | Reviewed | 1.3 | Pending issues reviewed | 1712 | BARAUNI POL IRD | ETP project jobs | SOD | Marketing | PZR | 2026-04-30 | THIRD PARTY ERRORS | 3 | PROCESS SAFETY | S3 | F1 | 2026-04-30 | AUD-2026-02-2000011302ACN-2026-03-4000122610 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122610 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122610 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122610 | AUD-2026-02-2000011302ACN-2026-03-4000122610 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The housekeeping improvement plan discussed during the review has been implemented. Housekeeping activities across the location arebeing carried out on a continuous basisq. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122611 | Closed | KUMAR RAJU | 2026-09-14 | Improvement plan on housekeeping front | 1.8 | Improvement plans discussed | 1712 | BARAUNI POL IRD | improvement in houskeeping area | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122611 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122611 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122611 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122611 | AUD-2026-02-2000011302ACN-2026-03-4000122611 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The location has procured the requisite equipment for conducting eyesight and colour-blindness tests. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122614 | Closed | KUMAR RAJU | 2026-09-14 | Location not having equipment for checking eyesight and colour blindness . | 2.16 | Eyesight / colour-blindness awareness checked | 1712 | BARAUNI POL IRD | advised to procure the same urgently | SOD | Marketing | PZR | 2026-04-30 | INADEQUATE SAFETY CULTURE | 3 | PROCESS SAFETY | S3 | F1 | 2026-04-30 | AUD-2026-02-2000011302ACN-2026-03-4000122614 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122614 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122614 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122614 | AUD-2026-02-2000011302ACN-2026-03-4000122614 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The non-functional focus lights in the tank valve areas have been repaired, restoring illumination to the prescribed levels. Lux levels on the affected primary roads have also been improved by rectifying the lighting fixtures. Corrective action has been completedat the location. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122613 | Closed | KUMAR RAJU | 2026-09-17 | Lux level found low in tank valve areas as focus light not working . Some of the primary road also lux level low | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1712 | BARAUNI POL IRD | location advised to take corrective action | SOD | Marketing | PZR | 2026-04-30 | INSUFFICIENT SUPERVISION | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-02-2000011302ACN-2026-03-4000122613 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122613 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122613 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000011302ACN-2026-03-4000122613 | AUD-2026-02-2000011302ACN-2026-03-4000122613 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Earth pits, boundary and vegetation control in the MFM area, ETP area and driver rest room were checked and found satisfactory during audit. As no adverse recommendation was made, the observation stands complied. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122618 | Closed | KUMAR RAJU | 2026-09-14 | Near MFM area , ETP area , driver rest room | 3.16 | Earth pits / boundary / vegetation control checked | 1712 | BARAUNI POL IRD | yes | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122618 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122618 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122618 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122618 | AUD-2026-02-2000011302ACN-2026-03-4000122618 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | All three pending OISD points have been complied with; compliance was completed on 31.07.2026 and confirmed accordingly. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122619 | Closed | KUMAR RAJU | 2026-09-14 | OISD pending point -3 nos. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1712 | BARAUNI POL IRD | advised to comply by 31.3.2026 | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122619 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122619 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122619 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000011302ACN-2026-03-4000122619 | AUD-2026-02-2000011302ACN-2026-03-4000122619 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Route correction is carried out promptly whenever a deviation is flagged through the Novex alert system. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122615 | Closed | KUMAR RAJU | 2026-09-14 | Checked . Route deviation voilation found | 3.3 | VTS deviations reviewed | 1712 | BARAUNI POL IRD | route correction in some cases | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 9 | PROCESS SAFETY | S3 | F3 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122615 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122615 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122615 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000011302ACN-2026-03-4000122615 | AUD-2026-02-2000011302ACN-2026-03-4000122615 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The quantity of unused 14-dia pipes lying along the PLT line has been assessed and the details communicated to HQO for further necessary action. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122616 | Closed | KUMAR RAJU | 2026-09-14 | PLT line unused pipes of 14 dia | 3.9 | Abnormal variations / unused assets reviewed | 1712 | BARAUNI POL IRD | Qtys of these pipes to be provided to HQO for shifting | SOD | Marketing | PZR | 2026-03-31 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S3 | F1 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122616 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122616 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122616 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122616 | AUD-2026-02-2000011302ACN-2026-03-4000122616 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Scattered scrap has been consolidated and disposed of by the location in February 2026 and disposal of retail-outlet scrap is beingcarried out on a regular basis. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122620 | Closed | KUMAR RAJU | 2026-09-14 | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1712 | BARAUNI POL IRD | Lot of scrap scattered to be put at one place and dispose . Retail scrap to be collected | SOD | Marketing | PZR | 2026-05-30 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-05-30 | AUD-2026-02-2000011302ACN-2026-03-4000122620 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122620 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122620 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122620 | AUD-2026-02-2000011302ACN-2026-03-4000122620 | 21 | 21 | 26 | 80 | 1 | 1 | 39 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | An M&I calendar has been established at the location for use from the beginning of each month and maintenance activities are being carried out and recorded as per the calendar, with records kept updated. Comprehensive inspection/cleaning of all pending tanks is currently in progress. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122621 | Closed | KUMAR RAJU | 2026-09-14 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . Tank insepction jobs of pending tanks to be completed | 4.2 | Maintenance activities reviewed | 1712 | BARAUNI POL IRD | All pending tanks compr. Inspection/ cleaningh to be done | SOD | Marketing | PZR | 2026-04-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S3 | F1 | 2026-04-30 | AUD-2026-02-2000011302ACN-2026-03-4000122621 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122621 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122621 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122621 | AUD-2026-02-2000011302ACN-2026-03-4000122621 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The ETP project has been completed on 31.07.2026. The Bottom Loading project is currently in progress and is targeted for completion by 30.09.2026. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122622 | Closed | KUMAR RAJU | 2026-09-14 | Reviewed for ETP & Bottom loading project | 4.3 | Project progress reviewed | 1712 | BARAUNI POL IRD | location advised to speed up all pending projects & time extension | SOD | Marketing | PZR | 2026-06-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-02-2000011302ACN-2026-03-4000122622 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122622 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122622 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122622 | AUD-2026-02-2000011302ACN-2026-03-4000122622 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | An RFD (Request for Disposal) for the pending scrap material was made and the scrap was subsequently disposed of by the location inFebruary 2026. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122623 | Closed | KUMAR RAJU | 2026-09-14 | scrap disposal of pending materail to be made | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1712 | BARAUNI POL IRD | RFD to be made within 10 days | SOD | Marketing | PZR | 2026-03-31 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122623 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122623 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122623 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122623 | AUD-2026-02-2000011302ACN-2026-03-4000122623 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | A feedback mechanism has been incorporated into all training sessions conducted at the location to assess and record the effectiveness of the training imparted. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122625 | Closed | KUMAR RAJU | 2026-09-14 | feedback system of training imparted | 6.2 | Training of workforce | 1712 | BARAUNI POL IRD | feedback system to be included in all training to check the effectiveness | SOD | Marketing | PZR | 2026-05-31 | INADEQUATE SAFETY CULTURE | 3 | PROCESS SAFETY | S3 | F1 | 2026-05-31 | AUD-2026-02-2000011302ACN-2026-03-4000122625 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122625 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122625 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122625 | AUD-2026-02-2000011302ACN-2026-03-4000122625 | 21 | 21 | 26 | 80 | 1 | 1 | 39 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The cost of patrolling and periodic maintenance & repair (M&R) has been computed and shared with BPCL and the payment has since been received. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122626 | Closed | KUMAR RAJU | 2026-09-14 | Patrolling and periodic M&R | 6.3 | PLT operations | 1712 | BARAUNI POL IRD | Patrolling and periodic M&R cost to be shared with BPCL | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122626 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122626 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122626 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122626 | AUD-2026-02-2000011302ACN-2026-03-4000122626 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Periodic maintenance & repair (M&R) of all safety equipment at the location has been carried out by the location as required. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122628 | Closed | KUMAR RAJU | 2026-09-14 | Periodic M&R of safety equipment | 6.6 | M&R of safety equipment | 1712 | BARAUNI POL IRD | This need to be done by location for all safety equipment | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122628 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122628 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122628 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000011302ACN-2026-03-4000122628 | AUD-2026-02-2000011302ACN-2026-03-4000122628 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Housekeeping and PPE usage in the driver rest room and PLT MFM area were checked and found satisfactory during the audit. As no recommendation was made, the point stands complied. | AUDIT UPLOAD IN SAP | 2026-01-21 19:00 | AUD-2026-02-2000011302 | 2026-01-20 15:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122617 | Closed | KUMAR RAJU | 2026-09-14 | Checked . Housekeeping near driver rest room , near PLT MFM area | 3.15 | Housekeeping & PPE usage checked | 1712 | BARAUNI POL IRD | yes | SOD | Marketing | PZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000011302ACN-2026-03-4000122617 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011302ACN-2026-03-4000122617 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-02-2000011302 - ACN-2026-03-4000122617 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011302ACN-2026-03-4000122617 | AUD-2026-02-2000011302ACN-2026-03-4000122617 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | Periodic M&R of all safety equipment has been carried out at the location as per the prescribed frequency. With regard to the siren, the required audible range of 3 km is being ensured. Personnel are being deputed up to the full 3 km range to verify and confirm the audibility of the siren. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-06-4000136944 | Closed | KUMAR RAJU | 2026-09-14 | Siren at the location was tested every week, however the audible range of 3kms is not being maintained. The location is sending person for confirmation till 2 kms only. | 6.1 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Person needs to be sent to 3 km range to confirm siren audibility | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136944 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136944 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136944 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136944 | AUD-2026-06-2000013057ACN-2026-06-4000136944 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Checking of empty Ethanol tank trucks (TTs) by two HPCL Officers prior to exit has been made mandatory and is being complied with. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-06-4000138504 | Closed | KUMAR RAJU | 2026-09-14 | Empty Ethanol TTs are not being checked by 2 HPCL Officers at time of exit. | 6.11 | Quarterly Inspection | 1712 | BARAUNI POL IRD | 2 HPCL officers to check the empty ethanol TTs going out from HPCL depot premises and LIC too should be informed and registers to be shown | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138504 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138504 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138504 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138504 | AUD-2026-06-2000013057ACN-2026-06-4000138504 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Location Officer provides the gate pass on time.. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-06-4000138505 | Closed | KUMAR RAJU | 2026-09-18 | Scrap going out from depot was not entered for 1/6/26. Location to ensure scrap is liquidated every quarter. | 6.12 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to ensure that timely entries are done for scrap material going out of depot. Location Officer to ptovide the gate pass ontime for entry | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138505 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138505 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138505 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138505 | AUD-2026-06-2000013057ACN-2026-06-4000138505 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Signage boards displaying the contact details have been updated at the location. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-06-4000138506 | Closed | KUMAR RAJU | 2026-09-14 | Signage boards ith contact details not updated | 6.13 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to ensure that correct boards to be updated. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138506 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138506 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138506 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138506 | AUD-2026-06-2000013057ACN-2026-06-4000138506 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The employee entry and exit register is now being updated on a daily basis with the entry and exit timings of all employees. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-06-4000138507 | Closed | KUMAR RAJU | 2026-09-14 | Employee entry and exit register not updated | 6.14 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Loaction to ensure updating register with enrty and exit time of the employees. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138507 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138507 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138507 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138507 | AUD-2026-06-2000013057ACN-2026-06-4000138507 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | It has been ensured that maintenance activities are physically carried out at site. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-06-4000138508 | Closed | KUMAR RAJU | 2026-09-18 |  | 6.15 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Physical work to be ensured in maintenance and false record generation to be stopped immediately | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138508 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138508 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138508 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138508 | AUD-2026-06-2000013057ACN-2026-06-4000138508 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | A foam drum has been provided near the No. 1 fire monitor and the Safety Officer has verified that the facility is now equipped with all the accessories necessary for fire-fighting during an emergency. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-06-4000138510 | Closed | KUMAR RAJU | 2026-09-14 | NO.1 monitor had no faom drum near the facilty | 6.17 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Safety officer to ensure the facility to be equiped with aal the accessories for fire fighing during an emergency. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138510 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138510 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138510 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138510 | AUD-2026-06-2000013057ACN-2026-06-4000138510 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Security staff have been instructed to check the cabins of all tank trucks prior to allowing entry into the depot premises for loading or unloading and this checking is now being carried out as a mandatory step at the gate. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-06-4000138512 | Closed | KUMAR RAJU | 2026-09-14 | Security staff is not performing cabin checking of the tankers entring in side the depot premises for loading or unloading. | 6.19 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to ensure that all the tanker cabins be checked by security staff before allowing entry inside the depot premies. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138512 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138512 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138512 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138512 | AUD-2026-06-2000013057ACN-2026-06-4000138512 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The armed guard's name has been updated in the register. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-06-4000136945 | Closed | KUMAR RAJU | 2026-09-14 | Armed guard name was not updated in the register. | 6.2 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Name to be updated in the register | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136945 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136945 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136945 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136945 | AUD-2026-06-2000013057ACN-2026-06-4000136945 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Strainer cleaning was found to be carried out satisfactorily, as confirmed through CCTV footage of 13.05.2026. The location is maintaining the prescribed cleaning schedule for all strainers and the observation stands complied. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-06-4000138513 | Closed | KUMAR RAJU | 2026-09-14 | Strainer cleaning was being done and visible in the CCTV footage for 13-5-26 | 6.20 | Quarterly Inspection | 1712 | BARAUNI POL IRD | OK. Location to manintian the cleaing schedule of all strainers. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138513 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138513 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138513 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138513 | AUD-2026-06-2000013057ACN-2026-06-4000138513 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The calibration activity was found to be satisfactorily witnessed by officers, as confirmed through CCTV footage. The location is maintaining this practice on an ongoing basis and no further action is required. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-06-4000138515 | Closed | KUMAR RAJU | 2026-09-14 | Caliberation shed CCTV footage was checked and it was found OK. Officer were witnessing the caliberation activity being done. | 6.22 | Quarterly Inspection | 1712 | BARAUNI POL IRD | OK Location officers to maintain the same. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138515 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138515 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138515 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138515 | AUD-2026-06-2000013057ACN-2026-06-4000138515 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The ethanol blending percentage is being maintained properly at the location. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-06-4000138516 | Closed | KUMAR RAJU | 2026-09-14 | Ethanol Blending was found to be 18% from the sample taken from gantry. | 6.23 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to improve the blending to 18.5 % | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138516 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138516 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138516 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138516 | AUD-2026-06-2000013057ACN-2026-06-4000138516 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The gantry personnel have been instructed to ensure regular recording and updating of the product density on the display board installed at the gantry. The same is now being carried out as part of the routine daily gantry operations. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24QUARTERLY INSPECTION | ACN-2026-06-4000138517 | Closed | KUMAR RAJU | 2026-09-14 | Density was not being recored on the board at the gantry | 6.24 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Gantry officer and Locatrion to ensure regualr updation of density on the Board installed on the gantry. | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138517 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138517 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138517 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138517 | AUD-2026-06-2000013057ACN-2026-06-4000138517 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The location has adopted the correct format for maintaining the density register and entries are being recorded accordingly. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25QUARTERLY INSPECTION | ACN-2026-06-4000138518 | Closed | KUMAR RAJU | 2026-09-18 | Density register being maintained is not as per the format. | 6.25 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to use correct format for recording the density. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138518 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138518 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138518 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138518 | AUD-2026-06-2000013057ACN-2026-06-4000138518 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The strainer cleaning register is now being updated and maintained properly. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27QUARTERLY INSPECTION | ACN-2026-06-4000138520 | Closed | KUMAR RAJU | 2026-09-14 | Strainer cleaning register was not being updated and maintained | 6.27 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Register to be updated and maintained propoerly and being reviewed by LIC. | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138520 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138520 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138520 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138520 | AUD-2026-06-2000013057ACN-2026-06-4000138520 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The Material Gate Pass register is being updated on a daily basis and the HPCL Location Officer is now regularly signing the register as required. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-06-4000136946 | Closed | KUMAR RAJU | 2026-09-14 | Material gate pass was not upto date. HPCL Officer sign was missing. | 6.3 | Quarterly Inspection | 1712 | BARAUNI POL IRD | HPCL Location Officer to sign the register and daily updation to be done. | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136946 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136946 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136946 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136946 | AUD-2026-06-2000013057ACN-2026-06-4000136946 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Regular, time-to-time training on the operation of fire extinguishers is being conducted for TT crew and hands-on training has already been provided to the identified helpers. Crew members are also being briefed on the location and usage of the VTS emergency/panic button for their safety. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.30QUARTERLY INSPECTION | ACN-2026-06-4000138522 | Closed | KUMAR RAJU | 2026-09-14 | Crew interaction: TT crew interacted with were found unaware of utility of emergency button of VTS unit. 4 TT helper were found notaware of how to operate Fire extinguishers. They were provided hands on training | 6.30 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Regular time to time crew to be trained on operating Fire extinguishers. And they need to be informed about the emergency / Panic button and its usage for their safety. | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138522 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138522 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138522 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138522 | AUD-2026-06-2000013057ACN-2026-06-4000138522 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The identified work permits (100000795381 and 100000795552) have been reviewed and closed after ensuring due acknowledgement by thework supervisor, completion of the JSA and signature of the LIC. Daily toolbox talks are now being conducted as per the job scope and prior to commencement of work. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.32QUARTERLY INSPECTION | ACN-2026-06-4000138524 | Closed | KUMAR RAJU | 2026-09-18 | Work permit 100000795381 / JSA was not acknowledged by the work supervisor , NO tool box talk available , NO signature of LIC. Permit No. 100000795552 : Tool box talk date was prior to the permit date. | 6.32 | Quarterly Inspection | 1712 | BARAUNI POL IRD | M&I officer to get the permits closed which needs to be duly signed by LIC for all permits. Daily Tool Box talks to be delivered asper the job scope. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138524 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138524 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138524 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138524 | AUD-2026-06-2000013057ACN-2026-06-4000138524 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The M&I Officer is now ensuring that the toolbox talk sheet is duly acknowledged (signed) by all workmen/labourers after each toolbox talk session. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.33QUARTERLY INSPECTION | ACN-2026-06-4000138525 | Closed | KUMAR RAJU | 2026-09-14 | Tool box talk sheet was not being acknowleged by the labourers. | 6.33 | Quarterly Inspection | 1712 | BARAUNI POL IRD | M&I officer to ensure that the workforce labour acknowleges the Tool box talk sheet. | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138525 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138525 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138525 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138525 | AUD-2026-06-2000013057ACN-2026-06-4000138525 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | LOTO (Lockout/Tagout) formalities have been streamlined and implemented at the location. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.34QUARTERLY INSPECTION | ACN-2026-06-4000138526 | Closed | KUMAR RAJU | 2026-09-18 | LOTO: has no permit no. only date was mentioned, No officer name was there. Keys was with the electrician and not with the permit issuer (HPCL Officer) LOTO could not be verified with any work permit. | 6.34 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Proper LOTO formalitites to be done and keys to be with HPCL officer. Location to ensure mentioning permit no, officer name on LOTO | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138526 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138526 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138526 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138526 | AUD-2026-06-2000013057ACN-2026-06-4000138526 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | PM (Preventive Maintenance) activity for the transformer was found satisfactory; the location is maintaining the same standard on an ongoing basis. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.35QUARTERLY INSPECTION | ACN-2026-06-4000138527 | Closed | KUMAR RAJU | 2026-09-14 | PM actitivity for transformer was found OK | 6.35 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Maintain the same | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138527 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138527 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138527 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138527 | AUD-2026-06-2000013057ACN-2026-06-4000138527 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The Safety Officer has sensitised the security staff and frisking of all personnel, including HPCL employees, is being carried out on a regular basis. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.37QUARTERLY INSPECTION | ACN-2026-06-4000138529 | Closed | KUMAR RAJU | 2026-09-14 | Security gurad did not carryout frisking fof one HPCL employee and was allowed to go inside the depot. | 6.37 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Safety offcier to ensure that the basic protocal and SOP to be followed. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138529 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138529 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138529 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138529 | AUD-2026-06-2000013057ACN-2026-06-4000138529 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Safety briefing is now being given to all visitors at the location at the time of entering the premises. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.38QUARTERLY INSPECTION | ACN-2026-06-4000138530 | Closed | KUMAR RAJU | 2026-09-14 | No brefing was given to us during our visit to the location while entring the premises. | 6.38 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Safety offcier to ensure that the basic protocal and SOP to be followed. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138530 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138530 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138530 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138530 | AUD-2026-06-2000013057ACN-2026-06-4000138530 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Security staff at R2 have been briefed on the expected cycle time for tanker and steps have been taken to ensure faster release of tank trucks after card punching, to minimise unnecessary halting. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.39QUARTERLY INSPECTION | ACN-2026-06-4000138531 | Closed | KUMAR RAJU | 2026-09-18 | Tankers going inside for loading are halting for too long after card punching.at R2 | 6.39 | Quarterly Inspection | 1712 | BARAUNI POL IRD | securtity staff to be briefed about cycle time and ensure faster release of TTs from R2 | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138531 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138531 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138531 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138531 | AUD-2026-06-2000013057ACN-2026-06-4000138531 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The In/Out entry register for contract workmen has been updated and is now being maintained on a daily basis. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-06-4000136947 | Closed | KUMAR RAJU | 2026-09-14 | In / Out entry registry for contract workman not update since 28-5-26 | 6.4 | Quarterly Inspection | 1712 | BARAUNI POL IRD | register to be updated daily or when ever there is any entry | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136947 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136947 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136947 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136947 | AUD-2026-06-2000013057ACN-2026-06-4000136947 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
CHANDRAKANTH JOSHI | 2026-09-18 | ROY TAVARES | 2026-09-15 | 3 non working CCTVs have been rectified during AMC Visit from 10-11 Sept 2026 | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138572 | Closed | ROY TAVARES | 2026-09-15 | CCTV Infrastructure: 3 cameras are not working out of 48 cameras. | 2.6 | CCTV functioning checked | 1797 | GULBARGA NEW IRD | The 3 non-working cameras are made to be functional at earliest. | SOD | Marketing | SWZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S4 | F2 | 2026-07-31 | AUD-2026-06-2000013300ACN-2026-06-4000138572 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138572 | 2026-08-19 18:00 | 61.0038 | 382 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138572 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138572 | AUD-2026-06-2000013300ACN-2026-06-4000138572 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 55
CHANDRAKANTH JOSHI | 2026-09-18 | ROY TAVARES | 2026-09-15 | non working CCTVs have been rectified during AMC Visit from 10-11 Sept 2026 | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122835 | Closed | ROY TAVARES | 2026-09-15 | 46 out of 48 CCTV Cameras are working. | 2.6 | CCTV functioning checked | 1797 | GULBARGA NEW IRD | 2 Non-working cameras are to be corrected. Response from SIS very poor | SOD | Marketing | SWZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 12 | ASSET INTEGRITY | S3 | F4 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122835 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122835 | 2026-08-19 18:00 | 61.0038 | 382 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122835 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122835 | AUD-2026-03-2000010764ACN-2026-03-4000122835 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Employees have been made aware of the need to declare the exact and accurate fire spot location during an emergency, to enable effective fire-fighting response and coordination among the team. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.41QUARTERLY INSPECTION | ACN-2026-06-4000138533 | Closed | KUMAR RAJU | 2026-09-14 | Fire Drill :Improper fire spot declaration . | 6.41 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Employees to be made aware that in case of fire emergency correct and accurate declaration to be made for effective fire fighting and team co-orrdination | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138533 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138533 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138533 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138533 | AUD-2026-06-2000013057ACN-2026-06-4000138533 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
CHANDRAKANTH JOSHI | 2026-09-18 | ROY TAVARES | 2026-09-15 | non working CCTVs have been rectified during AMC Visit from 10-11 Sept 2026 | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150407 | Closed | ROY TAVARES | 2026-09-15 | CCTV System Status: 3 cameras out of 48 are not operational. | 2.6 | CCTV functioning checked | 1797 | GULBARGA NEW IRD | The 3 non-working cameras are to be made functional at earliest. | SOD | Marketing | SWZ | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S4 | F2 | 2026-09-15 | AUD-2026-08-2000016952ACN-2026-08-4000150407 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150407 | 2026-08-19 18:00 | 61.0038 | 382 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150407 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016952ACN-2026-08-4000150407 | AUD-2026-08-2000016952ACN-2026-08-4000150407 | 21 | 21 | 27 | 80 | 5 | 5 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The foam system has been checked and repaired to ensure it is in working condition. The Location-in-Charge and Safety Officer are now ensuring that all fire-fighting facilities are periodically checked and kept ready for use during any emergency. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.42QUARTERLY INSPECTION | ACN-2026-06-4000138534 | Closed | KUMAR RAJU | 2026-09-14 | Fire Drill :Foam did not work | 6.42 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location LIC and safety officer to ensure that all facilities are checked and kept in working condiditon for any fire emergency | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138534 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138534 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138534 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138534 | AUD-2026-06-2000013057ACN-2026-06-4000138534 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | It has been ensured that LEL (Lower Explosive Limit) checking is carried out after every fire drill conducted at the location. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.46QUARTERLY INSPECTION | ACN-2026-06-4000138538 | Closed | KUMAR RAJU | 2026-09-14 | LEL was not checked. | 6.46 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Ensure LEL to be checked after fire drill | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138538 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138538 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138538 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138538 | AUD-2026-06-2000013057ACN-2026-06-4000138538 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The contact telephone numbers have been updated at the entry gate. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-06-4000136948 | Closed | KUMAR RAJU | 2026-09-14 | Updating of phones nos. such as RM, M&I, Location In charge needs to done at the entry gate. | 6.5 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to upodate the details | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136948 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136948 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136948 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136948 | AUD-2026-06-2000013057ACN-2026-06-4000136948 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The Point-type HCD (heat/combustible detector) of Dyke 1 was found functional; the location is maintaining the fire alarm system inworking condition. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.52QUARTERLY INSPECTION | ACN-2026-06-4000138542 | Closed | KUMAR RAJU | 2026-09-14 | Fire alarm system: Point type HCD of Dyke 1 checked. Found functional | 6.52 | Quarterly Inspection | 1712 | BARAUNI POL IRD | OK. To be maintained. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138542 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138542 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138542 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138542 | AUD-2026-06-2000013057ACN-2026-06-4000138542 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | As per the calibration chart, the level of TK-5 is 1342.0 cm. The location was re-verified and the actual level was found to be 1341.8 cm. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-06-4000138546 | Closed | KUMAR RAJU | 2026-09-18 | Tankfarm: Variation in Ref Ht of TK5 TAS 1340.6 Actual 1314.4 | 6.6 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Reason of Variation to be checked and corrected. Location to confrim back corrective action taken | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138546 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138546 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138546 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138546 | AUD-2026-06-2000013057ACN-2026-06-4000138546 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-17 | The In/Out entry register for contract workmen is now being updated on a daily basis. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-06-4000136949 | Closed | KUMAR RAJU | 2026-09-14 | In / Out entry registry for contract workman not update since 16-5-26 | 6.6 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Registers to be updated on daily basis | SOD | Marketing | PZR | 2026-07-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000136949 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000136949 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000136949 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000136949 | AUD-2026-06-2000013057ACN-2026-06-4000136949 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Use of correction pen in the Material Gate Pass register has been discontinued. The register is also being updated regularly. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-06-4000138500 | Closed | KUMAR RAJU | 2026-09-14 | In Material gate pass had correction pen marks. Register was updated till 18-5-26 only. | 6.7 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Correctionpen needs to be discontinued and any wrong entry to be strike off. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138500 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138500 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138500 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138500 | AUD-2026-06-2000013057ACN-2026-06-4000138500 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Proper night patrolling by security guards using RFID tokens is being ensured and the Safety Officer reviews compliance regularly. The Security Supervisor has been directed to review CCTV footage on a daily basis to confirm night patrol coverage. | BARAUNI IRD AUDIT Q1 | 2026-06-03 | AUD-2026-06-2000013057 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-06-4000138502 | Closed | KUMAR RAJU | 2026-09-14 | Tokens with RFID tag to be used security guards during Night patrol. CCTV footage does not show guards on patrol during 2:00 AM to 4:00 AM. | 6.9 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Saftey officer to ensure and review proper night patrol by the security guard. Security supervisor to review thw CCTV footage on daily basis. | SOD | Marketing | PZR | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000013057ACN-2026-06-4000138502 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013057ACN-2026-06-4000138502 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-06-2000013057 - ACN-2026-06-4000138502 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013057ACN-2026-06-4000138502 | AUD-2026-06-2000013057ACN-2026-06-4000138502 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The dislodged cable near the turnstile gate at the entry to the operating area, adjacent to the Admin Building, have been properly secured and the cable tray has been refixed and restored to its proper position. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-08-4000149489 | Closed | KUMAR RAJU | 2026-09-18 | A nos of cables found to have come out of cable tray , disturbing the position of cable trays on tray support, near the turnstile gate for entry to operating area near administrative building. | 6.1 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Cable trays to be fixed properly and cables to be secured in them | SOD | Marketing | PZR | 2026-09-20 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149489 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149489 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149489 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149489 | AUD-2026-08-2000017151ACN-2026-08-4000149489 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | All security personnel, including the Security Supervisor, have been briefed and made aware of the various facilities kept inside the security cabin and their intended use. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-08-4000149498 | Closed | KUMAR RAJU | 2026-09-14 | Security Supervisor found not aware of facilities kept inside Security cabin. | 6.10 | Quarterly Inspection | 1712 | BARAUNI POL IRD | All security to be made aware of different facilities kept inside security cabin and their work | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149498 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149498 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149498 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149498 | AUD-2026-08-2000017151ACN-2026-08-4000149498 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Security guards have been trained on the complete set of points to be covered during the safety briefing. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-08-4000149499 | Closed | KUMAR RAJU | 2026-09-14 | Security briefing was found not covering all points and security guard giving the briefing found not aware of what all to be covered in briefing. | 6.11 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Security to be trained on safety briefing | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149499 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149499 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149499 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149499 | AUD-2026-08-2000017151ACN-2026-08-4000149499 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The Location-in-Charge has directed security to record every entry and exit of officers, including in-between movements, rather than only the first entry and final exit. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-08-4000149700 | Closed | KUMAR RAJU | 2026-09-14 | Only during first time entry and final exit of officers, security is entering entry and exit times. However, whenever, officers areleaving office in between, the same is not recorded. | 6.12 | Quarterly Inspection | 1712 | BARAUNI POL IRD | LIC to ensure that security enters all entry / exit times religiously, without treating the work as ritual. | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149700 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149700 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149700 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149700 | AUD-2026-08-2000017151ACN-2026-08-4000149700 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The Location-in-Charge has directed security to record specific observations during CCTV monitoring rather than only the camera's functional status, and officers have also been assigned to periodically review CCTV footage to ensure effective oversight. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-08-4000149701 | Closed | KUMAR RAJU | 2026-09-14 | CCTV monitoring is not being done by mentioning the observations by security, rather mentioning whether the CCTVs are functioning or not. No officer monitors CCTV. | 6.13 | Quarterly Inspection | 1712 | BARAUNI POL IRD | LIC to ensure that security does effective CCTV monitoring and CCTVs are monitored by officers as well | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149701 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149701 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149701 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149701 | AUD-2026-08-2000017151ACN-2026-08-4000149701 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | This was an informational note on a planning meeting held with the supplier, transporters and DCTs regarding conversion of tank trucks from top loading to bottom loading. As no specific observation or recommendation was made, no corrective action is required. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-08-4000149710 | Closed | KUMAR RAJU | 2026-09-14 | A meeting was held with one of the suppliers of bottom loading TT fittings and transporters and DCTs on conversion of TTs from top loading to bottom loading for planning TT conversion | 6.22 | Quarterly Inspection | 1712 | BARAUNI POL IRD | No observation | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149710 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149710 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149710 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149710 | AUD-2026-08-2000017151ACN-2026-08-4000149710 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | A standard set of points covering the key Dos and Don'ts has been prepared for security personnel, and the briefing given at the time of depot entry has been improved. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-08-4000149711 | Closed | KUMAR RAJU | 2026-09-14 | Security Briefing at the time of Depot entry needs improvement. | 6.23 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Security to be given a standard point to talk upon and should be able to convey the important Dos and Don’ts. | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149711 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149711 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149711 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149711 | AUD-2026-08-2000017151ACN-2026-08-4000149711 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Security personnel have been instructed to record specific and detailed remarks in the CCTV register - including any irregularity observed and the effectiveness of the camera feed - instead of generic entries such as 'OK'. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24QUARTERLY INSPECTION | ACN-2026-08-4000149712 | Closed | KUMAR RAJU | 2026-09-14 | CCTV register had generic remarks such as “OK” in all the column. | 6.24 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Proper remarks with brief details to be mentioned in case of any irregularity observed while taking rounds mentioning the effectiveness of the camera feed. | SOD | Marketing | PZR | 2026-09-20 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149712 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149712 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149712 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149712 | AUD-2026-08-2000017151ACN-2026-08-4000149712 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The board displaying officer details at the Admin Building entry gate has been updated with the current details of the O&D Head andVigilance Officer. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25QUARTERLY INSPECTION | ACN-2026-08-4000149713 | Closed | KUMAR RAJU | 2026-09-14 | Boards having Officers details is Not updated at the Admin building entry gate. | 6.25 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to update the current details of O&D head, Vigilance and confirm. | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149713 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149713 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149713 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149713 | AUD-2026-08-2000017151ACN-2026-08-4000149713 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | A proper, standard density display board is being installed at the gantry. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26QUARTERLY INSPECTION | ACN-2026-08-4000149714 | Closed | KUMAR RAJU | 2026-09-18 | Improper density Board at the gantry. | 6.26 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Installation of proper and standard density display board to be done on the gantry. | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149714 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149714 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149714 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149714 | AUD-2026-08-2000017151ACN-2026-08-4000149714 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Installation of additional SOP Board at the gantry for the users is in progress. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27QUARTERLY INSPECTION | ACN-2026-08-4000149715 | Closed | KUMAR RAJU | 2026-09-18 | SOP on the gantry is not present. Installed at the fencing demarcating the gantry area. | 6.27 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to install the bilingual SOP Board on the gantry for the users to go through. | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149715 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149715 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149715 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149715 | AUD-2026-08-2000017151ACN-2026-08-4000149715 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Random checking of three tank trucks was carried out, and satisfactory results were observed for BR01GC1833 and WB76B1726. In the case of BR09GB7526 (new KGN transporter), dip variances of +2 mm, +3 mm, and +3 mm were observed in Chambers 2, 3, and 4, respectively. The observed variances are within the permissible limit of 0.1%. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.29QUARTERLY INSPECTION | ACN-2026-08-4000149716 | Closed | KUMAR RAJU | 2026-09-18 | Random checking of tank trucks.3 tankers were randomly checked: | 6.29 | Quarterly Inspection | 1712 | BARAUNI POL IRD | BR01GC1833: DCT 12KL at bay No 8 found to be OK/ WB76B1726: DCT 20KL at bays no. 6 found to be OK / BR09GB7526: Transporter NewKGN at bay No.2 1 chamber OK ,2nd 2mm + ,3rd 3mm + and 4th 3mm + and 4th OK | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149716 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149716 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149716 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149716 | AUD-2026-08-2000017151ACN-2026-08-4000149716 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The red-coloured water pump unit identified near the calibration tower has been inspected and found to be in working condition; it has therefore been retained for use rather than being disposed of. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-08-4000149491 | Closed | KUMAR RAJU | 2026-09-14 | A red coloured water pump unit, apparently not in working condition and disconnected from any pipeline or electricity connection found kept unattended in UG tankfarm near calibration tower. | 6.3 | Quarterly Inspection | 1712 | BARAUNI POL IRD | The pump is to be disposed off, if not usable or beyond economic repair | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149491 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149491 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149491 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149491 | AUD-2026-08-2000017151ACN-2026-08-4000149491 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Checking of empty Ethanol tank trucks by two HPCL Officers prior to exit from the depot premises has been made mandatory and is nowbeing complied with. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.31QUARTERLY INSPECTION | ACN-2026-08-4000149718 | Closed | KUMAR RAJU | 2026-09-14 | Empty Ethanol out tankers checking not being done by 2 HPCL officers. | 6.31 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Location to ensure that the empty TTs are checked by 2 HPCL officers before it exits depot premises. | SOD | Marketing | PZR | 2026-09-20 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149718 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149718 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149718 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149718 | AUD-2026-08-2000017151ACN-2026-08-4000149718 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Officers have been briefed to ensure all future work permits are issued with proper JSA and daily toolbox talks, and are duly signed off at closure. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.32QUARTERLY INSPECTION | ACN-2026-08-4000149719 | Closed | KUMAR RAJU | 2026-09-18 | Details on the work permit is not being captured properly. Found incomplete as it did not carry closing signatures, JSAs and Tool box sheet. For permits reviewed 180000109941/180000114687/180000114638/180000113557/180000116567 | 6.32 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Officers were briefed and Location to ensure the work permit is issued with proper JSA, Tool box talk for daily jobs. Ensuring signature at the closing of projects in the permits. | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149719 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149719 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149719 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149719 | AUD-2026-08-2000017151ACN-2026-08-4000149719 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The point was found satisfactory ('OK') during the inspection; as there is no adverse observation or recommendation, no corrective action is required. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.33QUARTERLY INSPECTION | ACN-2026-08-4000149720 | Closed | KUMAR RAJU | 2026-09-14 |  | 6.33 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Found OK | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149720 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149720 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149720 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149720 | AUD-2026-08-2000017151ACN-2026-08-4000149720 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Security guard rounds of the depot premises during the prescribed 2-hour time slot (12:00 midnight to 5:00 AM) were verified and found to be satisfactorily carried out ('OK'); no corrective action is required. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.34QUARTERLY INSPECTION | ACN-2026-08-4000149721 | Closed | KUMAR RAJU | 2026-09-14 |  | 6.34 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Found OK. Guards were doing rounds of the depot premises at the give time slot of 2hrs from 12:00 midnight to 5:00 AM in the morning. | SOD | Marketing | PZR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149721 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149721 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149721 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149721 | AUD-2026-08-2000017151ACN-2026-08-4000149721 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Wheel chokes have been provided at the calibration tower for use with tank trucks (TTs). | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-08-4000149492 | Closed | KUMAR RAJU | 2026-09-14 | There are no wheel chokes at calibration tower for TTs. | 6.4 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Wheel chokes to be provided | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149492 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149492 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149492 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149492 | AUD-2026-08-2000017151ACN-2026-08-4000149492 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The dyke drain of TK13 has been cleared of mud, dried leaves and other debris. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-08-4000149493 | Closed | KUMAR RAJU | 2026-09-14 | Dyke drain of Tk13 found full of mud, dried leaves, etc. | 6.5 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Proper housekeeping to be ensured | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149493 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149493 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149493 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149493 | AUD-2026-08-2000017151ACN-2026-08-4000149493 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | Vegetation obstructing the approaches to all three fire water tanks has been cleared, restoring clear and unobstructed access for emergency use. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-08-4000149494 | Closed | KUMAR RAJU | 2026-09-18 | Approaches to all three fire water tanks are not visible due to vegetation. | 6.6 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Proper approaches to be made | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149494 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149494 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149494 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149494 | AUD-2026-08-2000017151ACN-2026-08-4000149494 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
RAJENDRRA NIRAANJAN | 2026-09-18 | KUMAR RAJU | 2026-09-18 | The vegetation covering Fire Water Monitor No. 6 and its approach steel staircase has been cleared. | BARAUNI Q2 AUDIT | 2026-08-20 | AUD-2026-08-2000017151 | 2026-08-20 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-08-4000149496 | Closed | KUMAR RAJU | 2026-09-14 | Fire water monitor no 6 and its approach steel stair case found completely covered by green vegetation. | 6.8 | Quarterly Inspection | 1712 | BARAUNI POL IRD | Approaches to fire fighting facilities and fire fighting facilities to be maintained free of green vegetation | SOD | Marketing | PZR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-08-2000017151ACN-2026-08-4000149496 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017151ACN-2026-08-4000149496 | 2026-09-03 | 46.7538 | 382 | >20 | AUD-2026-08-2000017151 - ACN-2026-08-4000149496 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017151ACN-2026-08-4000149496 | AUD-2026-08-2000017151ACN-2026-08-4000149496 | 21 | 21 | 27 | 80 | 1 | 1 | 55 | 55
|  | M.RAJKUMAR | 2026-09-18 | All the VA applicable Cameras are made functional and VA violations are getting recorded | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122607 | Completed | M.RAJKUMAR | 2026-09-18 | VA alerts checked- No alerts active. 32 out of 37 VA cameras are functional. | 2.7 | VA alerts checked / analysed | 1856 | COIMBATORE DEPOT | AL | SOD | Marketing | SZ | 2026-02-28 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 6 | PROCESS SAFETY | S2 | F3 | 2026-02-28 | AUD-2026-03-2000010712ACN-2026-03-4000122607 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122607 | 2026-08-28 17:00 | 52.0455 | 180 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122607 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010712ACN-2026-03-4000122607 |  | AUD-2026-03-2000010712ACN-2026-03-4000122607 | 21 |  | 26 | 80 | 0 | 1 | 26
|  | M.RAJKUMAR | 2026-09-18 | All the VA applicable Cameras are made functional and VA violations are getting recorded | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142954 | Completed | M.RAJKUMAR | 2026-09-18 | VA alerts checked- No alerts active. 32 out of 37 VA cameras are functional. | 2.7 | VA alerts checked / analysed | 1856 | COIMBATORE DEPOT | Location to follw up with VA vendor and ensure all cameras are functional in VA. | SOD | Marketing | SZ | 2026-07-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142954 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142954 | 2026-08-28 17:00 | 52.0455 | 333 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142954 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015339ACN-2026-07-4000142954 |  | AUD-2026-07-2000015339ACN-2026-07-4000142954 | 21 |  | 27 | 80 | 0 | 1 | 48
|  | M.RAJKUMAR | 2026-09-18 | Internal Inspection of TK5, TK14 and TK15 completed and put back into service. TK16 Cleaning completed and put back into Operation. TK3 inspection and repair completed and put back into Operation. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122608 | Completed | M.RAJKUMAR | 2026-09-18 | All OISD points are complied. Pending MDSA/SSA points related to tank inpection is review and works are in progress | 3.18 | OISD/MDSA/SSA compliance reviewed | 1856 | COIMBATORE DEPOT | Location to expediate the closure of Pending MDSA/SSA point of Tank inspection. | SOD | Marketing | SZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | PROCESS SAFETY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000010712ACN-2026-03-4000122608 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122608 | 2026-08-28 17:00 | 52.0455 | 211 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122608 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010712ACN-2026-03-4000122608 |  | AUD-2026-03-2000010712ACN-2026-03-4000122608 | 21 |  | 26 | 80 | 0 | 1 | 31
BINU K | 2026-09-18 |  |  | Complied as suggested. | TIRUNELVELI_IRD_Q1_ZONAL HEAD INSPECTION | 2026-05-06 18:00 | AUD-2026-06-2000013162 | 2026-05-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138484 | Closed | BINU K | 2026-09-18 | Emergency Gate is not in use | 6.1 | Emergenccy Gate | 1879 | TIRUNELVELI DEPOT | Emergency gate Nomenclature to be removed as the gate is not in use | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 1 | EMERGENCY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013162ACN-2026-06-4000138484 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013162ACN-2026-06-4000138484 | 2026-05-08 | 164.7538 | 382 | >20 | AUD-2026-06-2000013162 - ACN-2026-06-4000138484 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013162ACN-2026-06-4000138484 | AUD-2026-06-2000013162ACN-2026-06-4000138484 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
BINU K | 2026-09-18 |  |  | Stept marked with yellow strips | TIRUNELVELI_IRD_Q1_ZONAL HEAD INSPECTION | 2026-05-06 18:00 | AUD-2026-06-2000013162 | 2026-05-05 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000138485 | Closed | BINU K | 2026-09-18 | Steps not marked with yellow strips | 6.2 | TWD Punp House | 1879 | TIRUNELVELI DEPOT | Yellow strip to be marked on the steps to identify difference in height | SOD | Marketing | SZ | 2026-07-30 | FAILURE TO FOLLOW PROCEDURES | 1 | EMERGENCY | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013162ACN-2026-06-4000138485 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013162ACN-2026-06-4000138485 | 2026-05-08 | 164.7538 | 382 | >20 | AUD-2026-06-2000013162 - ACN-2026-06-4000138485 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013162ACN-2026-06-4000138485 | AUD-2026-06-2000013162ACN-2026-06-4000138485 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152883 | Open |  |  | Carried out with all officers and LIC. 4 new Officers joined. They were welcomed. Expressed concern on delay in exit time of new officers. LIC was advised to stagger the timing in case of pet Coke loading as well as PLT from HRRL | 1.1 | Interaction with all officers (1–1.5 hrs) | 1224 | BARMER TERMINAL | It is advised to call at least two officers in late hrs so that they may extend for PLT receipt from and Pet Coke loading ex HRRL. This will reduce undue stress on officers due to regular extended hr job. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000152883 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152883 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152883 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152883 |  | AUD-2026-09-2000017855ACN-2026-09-4000152883 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152884 | Open |  |  | Location needs to collect list of all SOP from Bharatpur/Jodhpur Tml. Pls prepare SOP booklet for all kind of operations inside location. Get the booklet approved by GM O&D. Extract critical operating steps from these SOP booklets and display the same at prominent places inside and around Terminal | 1.3 | Pending issues reviewed | 1224 | BARMER TERMINAL | Pls ensure SOP booklet approval and SOP boards display as per circular. Location is also requested to share progress on this on fortnightly basis | SOD | Marketing | NWF | 2026-11-30 |  | 15 |  | S3 | F5 | 2026-11-30 | AUD-2026-09-2000017855ACN-2026-09-4000152884 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152884 | 2026-09-12 17:45 | 37.0143 | 455 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152884 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152884 |  | AUD-2026-09-2000017855ACN-2026-09-4000152884 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152885 | Open |  |  | 1. There are 46 points in PCSA conducted during 20th and 21st May 2026. Location needs to share target date of compliance and name of responsible officer for each of the points in PCSA. Location needs to apprise zone on monthly progress of PCSA. 2. Compliance ofERDMP team recommendations to be done. It is also to be reviewed by LIC and Zone on monthly basis | 1.4 | Earlier action points status checked | 1224 | BARMER TERMINAL | 1. There are 46 points in PCSA conducted during 20th and 21st May 2026. Location needs to share target date of compliance and name of responsible officer for each of the points in PCSA. Location needs to apprise zone on monthly progress of PCSA. 2. Compliance ofERDMP team recommendations to be done. It is also to be reviewed by LIC and Zone on monthly basis | SOD | Marketing | NWF | 2026-12-31 |  | 15 |  | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017855ACN-2026-09-4000152885 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152885 | 2026-09-12 17:45 | 37.0143 | 486 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152885 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152885 |  | AUD-2026-09-2000017855ACN-2026-09-4000152885 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152886 | Open |  |  | Location is engaging 21 labours at present. Out of 21 labours, 18 labours are reporting as on date. Pls engage maximum 13 labours and two contract engineers for all hired jobs except security service. If contract engineers are removed, you may engage two more contract labours. pls do not engage more than 15 hired persons without my consent. | 1.8 | Improvement plans discussed | 1224 | BARMER TERMINAL | Location is engaging 21 labours at present. Out of 21 labours, 18 labours are reporting as on date. Pls engage maximum 13 labours and two contract engineers for all hired jobs except security service. If contract engineers are removed, you may engage two more contract labours. pls do not engage more than 15 hired persons without my consent. Pls refer my email dt 18.09.2026 in this regard | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152886 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152886 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152886 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152886 |  | AUD-2026-09-2000017855ACN-2026-09-4000152886 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152887 | Open |  |  | Fire drill not done in last three months | 2.1 | Fire drill conducted in last 6 months (surprise) | 1224 | BARMER TERMINAL | Fire drill is to be conducted every month | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000152887 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152887 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152887 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152887 |  | AUD-2026-09-2000017855ACN-2026-09-4000152887 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152888 | Open |  |  | 1) Securities were found not alert. They didn't do frisking. 2) HHMD was out of order. 3) Safety briefing is not up to date. 4) Securities are not aware of idle shift (off shift drill). It needs to be conducted once in a quarter. 5) RTGP register is not okay.Any materials taken out for repairing jobs, pls make RTGP instead of OGP. Location is maintaining both online gate pass and hand made gate pass. Only online gate pass to be used. 6) Gate is not being sealed after the day end. Movement of vehicles is observed daynight also due to project Radiography requirements. This system is to be strengthened. 7) Lock number is not being mentioned in the register nor mentioned in invoice, It has to be recorded in TT register and invoice both. 8) Entry of all vehicles other than MS/HSD/Ethanol should also be mentioned in in/out gate pass. 9) Visitor Card System is currently not being followed. Pls ensure as perSOP. 10) FAN numbers are not getting recorded in TT register | 2.4 | Security alertness checked (night-halt / surprise checks) | 1224 | BARMER TERMINAL | 1. Pls give necessary training to all securities. Off shift drill to be conducted once in a quarter. 2. RTGP register is not okay.Any materials taken out for repairing jobs, pls make RTGP instead of OGP. Location is maintaining both online gate pass and hand made gate pass. Only online gate pass to be used. 3. Gate is not being sealed after the day end. Movement of vehicles is observed daynight also due to project Radiography requirements. This system is to be strengthened. Entry of all vehicles other than MS/HSD/Ethanol should also be mentioned in in/out gate pass. 4. Lock number is not being mentioned in the register nor mentioned in invoice, It has to be recorded in TT register and invoice both. 5. Visitor Card System is currently not being followed. Pls ensure as per SOP. 6. FAN numbers are not getting recorded in TT register. Pls do that | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152888 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152888 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152888 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152888 |  | AUD-2026-09-2000017855ACN-2026-09-4000152888 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152889 | Open |  |  | The same was reviewed. Since, most of the officers, contract workman and security guards are new, it needs continuous training. Since location is not having their own FW tank, FW pump and location is fully dependent on HRRL in case of emergency, hence it is suggested that location should make one local MOU (memorandum of understanding) with Fire and Safety department. This MOU should includeall critical person name, contact no. along with details of all fire fighting facilities which can be used for handling emergency at Terminal end. The MOU should be signed and kept on records. | 2.5 | Emergency response preparedness reviewed | 1224 | BARMER TERMINAL | 1) Location should engage nearby LPG plant officers for training on Fire and safety. 2) Location should conduct one more trainingthrough Fire and Safety department of HRRL. 3) Location should get training through VC from Mr. Neeraj Rajput on emergency preparedness and about Fire organisation chart. 4) Since location is not having their own FW tank, FW pump and location is fully dependenton HRRL in case of emergency, hence it is suggested that location should make one local MOU (memorandum of understanding) with Fireand Safety department. This MOU should include all critical person name, contact no. along with details of all fire fighting facilities which can be used for handling emergency at Terminal end. The MOU should be signed and kept on records. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152889 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152889 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152889 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152889 |  | AUD-2026-09-2000017855ACN-2026-09-4000152889 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152890 | Open |  |  | Access control system (C-Bac system) is yet to be made functional by E&P department. However, I have given training to security guards how to handle visitor, contract labours, TT crew. Pls ensure compliance | 2.8 | Access control systems checked | 1224 | BARMER TERMINAL | Pls get SOP prepared for visitor/contract labour/TT crew entry to location. Pls ensure to display the same in Hindi so that it can be understood by Security guards. Pls refer circular in SOD portal for issue of gate pass/ID card to contract labours/visitor | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152890 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152890 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152890 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152890 |  | AUD-2026-09-2000017855ACN-2026-09-4000152890 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152891 | Open |  |  | HVLR tested and found okay. There is leakage from HVLR. ESD/HCDs are yet to be installed. There is no RSFPS. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1224 | BARMER TERMINAL | 1) pls prepare one register. This register to be filled by each officer and contract staff for any issue observed in the field, equipment, assets etc. This is the period of handing over/taking over. Pls exmine each assets. Operate all equipment to its full capacity and observe for any issue. In case, any issue is there, pls inform in writing to E&P. 2) LIC should take Work permit authority. 3) Pls prepare schedule of preventive maintenance with respect to housekeeping job, maintenance job and electrical jobs. Pls share the schedule and frequency of job with zone. 4) Meeting with mutual aid members to be done. 5) Safety committee meeting should be done as per SOP. Members to be identified. Agenda to be prepared. Notice to be served. SCM report to be made. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152891 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152891 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152891 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152891 |  | AUD-2026-09-2000017855ACN-2026-09-4000152891 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152892 | Open |  |  | Handon training given by HRRL. They are under training period | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1224 | BARMER TERMINAL | Training to be given to all contract labours, security guards, TT crew and new officers as per OISD 154 module. Record to be maintained. The training report should contain, taregt group, identification of training needs by carrying out safety quiz, conducted training program with attendance sheet, photo etc, feedback of participant and evaluation of training program | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152892 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152892 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152892 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152892 |  | AUD-2026-09-2000017855ACN-2026-09-4000152892 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152893 | Open |  |  | Tank trucks were not loaded due to product constraint. Location is maintaining TT dip check register. It is not signed by officer. Secondly, location to avoid any top up of product in local or removal of product from tank truck after loading. If it is happening with one particular bay or one particular TT, the same needs to be attended by cross verification of same through calibration tower/mobile prover tank. Location is maintaining top up quantity both in litre as well as in litre. Pls mention one UOM (unit of measure) only. For any top up, LIC should be informed in writing. | 3.2 | Post-loading dip checks verified | 1224 | BARMER TERMINAL | TT dip checking to be done for 100% TTs and to be signed by officer in TT dip checking record. Top up qty should be signed by officer. It should be in one UOM. If it is happening with one particular bay or one particular TT, the same needs to be attended by cross verification of same through calibration tower/mobile prover tank. | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152893 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152893 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152893 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152893 |  | AUD-2026-09-2000017855ACN-2026-09-4000152893 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152894 | Open |  |  | Could not be checked. No loading took place | 3.3 | VTS deviations reviewed | 1224 | BARMER TERMINAL | Location needs to note down opening and closing dip of UG tank of ethanol before and after receipt of ethanol tanker. If there is shortage of more than 200 litre in any consignemnt, pls inform Zone. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000152894 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152894 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152894 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152894 |  | AUD-2026-09-2000017855ACN-2026-09-4000152894 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152895 | Open |  |  | EM locking system should be brought in operation as early as possible. KMX box to be installed. LAN connectivity to be given. It should start immediately | 3.5 | EM Lock SOP compliance verified | 1224 | BARMER TERMINAL | EM locking system should be brought in operation as early as possible. KMX box to be installed. LAN connectivity to be given. It should start immediately | SOD | Marketing | NWF | 2026-10-31 |  | 12 |  | S3 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152895 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152895 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152895 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152895 |  | AUD-2026-09-2000017855ACN-2026-09-4000152895 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152896 | Open |  |  | Could not be checked. No ethanol TT unloading | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1224 | BARMER TERMINAL | 1. Location needs to note down opening and closing dip of UG tank of ethanol before and after receipt of ethanol tanker. If there is shortage of more than 200 litre in any consignemnt, pls inform Zone. 2. Location needs to open dome cover of one ethanol TT per week and see thrugh inside all chambers. Whatever observation is made, pls record the same in register. 3. Location needs to calibrate at least one ethanol TT per month at calibration shed and make record of the same. | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152896 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152896 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152896 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152896 |  | AUD-2026-09-2000017855ACN-2026-09-4000152896 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152897 | Open |  |  | Dip of all tanks taken. The dips (Gross dip/water dip in cm) are: 1) HSD UG tank: 50.5/1.2 2) MS UG tank: 72.2/2.8 3) Ethanol: a) TK111 (AG): 124.5/0 b) TK112 (UG): 362.0/0 c) TK113 (UG): 300.4/0 Dip taken on 12th Sept closing hr. | 3.7 | Inventory physical dip of minimum two tanks taken | 1224 | BARMER TERMINAL | Pls share the gross dip/water dip and temp at which tanks reconciliation were done on 12th Sept closing. Differential volume (Dip at which tanks were reconciled - dip/temp mentioned by me) should be shared. Reason of abnormal variation to be given. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000152897 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152897 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152897 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152897 |  | AUD-2026-09-2000017855ACN-2026-09-4000152897 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152898 | Open |  |  | 1. Operation reco file was checked. Location should maintain daily print of operation reconciliation sheet. If the loss is more than 2.5 Kl in any product on any day, pls mention the reason of loss/gain >2.5 KL on operation reco sheet. 2. MFM of benzene and Toluene line at battery limit area, are to be calibrated. All other MFMs in gantry area are to be calibrated which are used for MS/HSD.. | 3.8 | Auto vs Manual reconciliation checked | 1224 | BARMER TERMINAL | 1. Operation reco file was checked. Location should maintain daily print of operation reconciliation sheet. If the loss is more than 2.5 Kl in any product on any day, pls mention the reason of loss/gain >2.5 KL in oper reco sheet 2. MFM of Benzene and Toluene line at battery limit area, are to be calibrated. All other MFMs in gantry area are to be calibrated which are used for MS/HSD.. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152898 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152898 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152898 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152898 |  | AUD-2026-09-2000017855ACN-2026-09-4000152898 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152899 | Open |  |  | There is loss of 32 KL in HSD for handling of very small volume. Stock loss is approx 1% which is in higher side. Location needs tocontrol stock loss in coming periods. Similarly locations needs to keep close watch on MS and ethanol loss | 3.9 | Abnormal variations / unused assets reviewed | 1224 | BARMER TERMINAL | Location needs to analyse receipt loss and dispatch loss separately. For every PLT of MS and HSD, gain loss to be calculated. If the loss qty is more than 1 Kl in any PLT, pls inform Zone in writing. | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000152899 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000152899 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000152899 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000152899 |  | AUD-2026-09-2000017855ACN-2026-09-4000152899 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153250 | Open |  |  | Make sheet of HRRL tank opening and closing gross dip/water dip/temp, HRRL side MFM opening and closing reading/temp, HPCL side MFMopening and closing reading/temp and UG/AG tank of Tml end opening and closing manual dip/temp, UG tank opening and closing TAS dip/temp. Make this table for both the products (MS/HSD) and share with us on monthly basis. This will help to check stability of MFM at HRRL and HPCL end. | 3.10 | TFMS/SAP reconciliation checked | 1224 | BARMER TERMINAL | Record to be maintained and to be shared with location on monthly basis. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000153250 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153250 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153250 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153250 |  | AUD-2026-09-2000017855ACN-2026-09-4000153250 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153251 | Open |  |  | Location needs to maintain totaliser reading for every TT before and after loading, product wise. Register to be maintained and signed. | 3.11 | MFM vs BCU totalizer comparison checked | 1224 | BARMER TERMINAL | Location needs to maintain totaliser reading for every TT before and after loading, product wise. Register to be maintained and signed. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000153251 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153251 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153251 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153251 |  | AUD-2026-09-2000017855ACN-2026-09-4000153251 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153252 | Open |  |  | Verify all MFM by mobile prover tank by 31st Oct 2026 | 3.13 | K-factor changes reviewed (if any) | 1224 | BARMER TERMINAL | Verify all MFM and Fixed prover tanks by 31.10.2026. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000153252 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153252 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153252 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153252 |  | AUD-2026-09-2000017855ACN-2026-09-4000153252 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153253 | Open |  |  | Location officer should wear PPE whenever they go to hazardous zone. New officer came without helmet at UG tank farm area. He needsto be trained. Mobile should not be used at hazardous zone. | 3.15 | Housekeeping & PPE usage checked | 1224 | BARMER TERMINAL | It needs to be strenthened and strictly implemented for all. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000153253 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153253 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153253 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153253 |  | AUD-2026-09-2000017855ACN-2026-09-4000153253 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153254 | Open |  |  | MOC to be made for new officers joined. | 3.17 | MOC status reviewed | 1224 | BARMER TERMINAL | MOC to be made for new officers joined. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017855ACN-2026-09-4000153254 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153254 | 2026-09-12 17:45 | 37.0143 | 394 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153254 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153254 |  | AUD-2026-09-2000017855ACN-2026-09-4000153254 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153255 | Open |  |  | A) tender should be floated for: 1) Standing order on Mechanical nature of jobs like structure welding, inch dia cutting, inch diawelding, 2) Standing order for civil nature of jobs like RCC/PCC/Brick masonery/plaster etc 3) Standing order for common supply items (stationery, printer cartridge, paint materials, consumables, plastic seal etc) which are repeated in nature. PX bills to be avoided. B) Location should prepare LPR and tender document for pipeline modifications, new MS/HSD pump house after conversion of one tank of Benzene and Toluene each. C) Location needs to take prior consent in writing for any nomination order or H1 orders. from GM O&D, Jaipur Zone. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1224 | BARMER TERMINAL | A) tender should be floated for: 1) Standing order on Mechanical nature of jobs like structure welding, inch dia cutting, inch diawelding, 2) Standing order for civil nature of jobs like RCC/PCC/Brick masonery/plaster etc 3) Standing order for common supply items (stationery, printer cartridge, paint materials, consumables, plastic seal etc) which are repeated in nature. PX bills to be avoided. B) Location should prepare LPR and tender document for pipeline modifications, new MS/HSD pump house after conversion of one tank of Benzene and Toluene each. C) Location needs to take prior consent in writing for any nomination order or H1 orders. from GM O&D, Jaipur Zone. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000153255 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153255 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153255 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153255 |  | AUD-2026-09-2000017855ACN-2026-09-4000153255 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153256 | Open |  |  | 1. Ladder support to be given at battery limit. 2. Pit hole to be filled at gantry area. 3. Marking to be made at TT parking areathrough E&P. 4. Attendance recording system to be installed 5. One more internet connection to be taken for smooth operation | 4.2 | Maintenance activities reviewed | 1224 | BARMER TERMINAL | 1. Ladder support to be given at battery limit. 2. Pit hole to be filled at gantry area. 3. Marking to be made at TT parking areathrough E&P. 4. Attendance recording system to be installed 5. One more internet connection to be taken for smooth operation | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000153256 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153256 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153256 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153256 |  | AUD-2026-09-2000017855ACN-2026-09-4000153256 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153257 | Open |  |  | E&P will be handing over the assets to location. Pls ask check list for all assets that will be handed over to Operation team. Pls ask the same from E&P in advance. Check each of the check list points. If there is any confusion in understanding of check list point, pls call zonal officer including undersign for any help. All assets are to be verified before final take over. If any issue is observed in any asset during take over period, the same to be informed in writing to E&P. Most of the assets will be in warranty period/one year observation period. pls collect the date of completion of each facilities. Examine all issues including civil nature, mechanical nature, electrical nature etc. Pls inform to E&P in writing for any deviations. | 4.3 | Project progress reviewed | 1224 | BARMER TERMINAL | E&P will be handing over the assets to location. Pls ask check list for all assets that will be handed over to Operation team. Pls ask the same from E&P in advance. Check each of the check list points. If there is any confusion in understanding of check list point, pls call zonal officer including undersign for any help. All assets are to be verified before final take over. If any issue is observed in any asset during take over period, the same to be informed in writing to E&P. Most of the assets will be in warranty period/one year observation period. pls collect the date of completion of each facilities. Examine all issues including civil nature, mechanical nature, electrical nature etc. Pls inform to E&P in writing for any deviations. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017855ACN-2026-09-4000153257 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153257 | 2026-09-12 17:45 | 37.0143 | 455 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153257 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153257 |  | AUD-2026-09-2000017855ACN-2026-09-4000153257 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO BARMER TML ON 11TH AND 12TH SEP | 2026-09-12 17:45 | AUD-2026-09-2000017855 | 2026-09-11 09:55 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153258 | Open |  |  | History card record was not found. Pls update record for all tanks, pumps in use, HVLR, DG etc. Even if cost of material is in the scope of vendor, pls mention the spare parts used and approx cost of spare parts in history card. | 6.1 | History card | 1224 | BARMER TERMINAL | History card record was not found. Pls update record for all tanks, pumps in use, HVLR, DG etc. Even if cost of material is in the scope of vendor, pls mention the spare parts used and approx cost of spare parts in history card. | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017855ACN-2026-09-4000153258 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017855ACN-2026-09-4000153258 | 2026-09-12 17:45 | 37.0143 | 425 | >20 | AUD-2026-09-2000017855 - ACN-2026-09-4000153258 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017855ACN-2026-09-4000153258 |  | AUD-2026-09-2000017855ACN-2026-09-4000153258 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153343 | Open |  |  | A total of 8 recommendations are open from Q4 and Q1 Audit. Location has been advised to close the same by 30.12.26 | 1.4 | Earlier action points status checked | 1334 | HPCL REWARI IRD | Balance points to be complied. Maximum target date for compliance is Sep'26 end. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017364ACN-2026-09-4000153343 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153343 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153343 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153343 |  | AUD-2026-09-2000017364ACN-2026-09-4000153343 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153345 | Open |  |  | Location is carrying out monthly monitoring of Lux levels in all operating areas. Last record of inspection done on 03.09.2026 and as per the record available, lux levels are well above the minimum required levels in all the areas. However, during night inspection done on 9th Sep'26, Lux levels were found less at Fire Engine#3, HSD pump at the extreme corner of product pump house, primary road in between TLF Gantry & the sealing shed and some sections of tertiary roads along the tank farm areas. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1334 | HPCL REWARI IRD | Lux levels to be improved at the identified spots in line with the requirement as per the OISD code. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017364ACN-2026-09-4000153345 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153345 | 2026-09-10 17:00 | 39.0455 | 424 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153345 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153345 |  | AUD-2026-09-2000017364ACN-2026-09-4000153345 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153346 | Open |  |  | During the Visit, Access control at main gate was checked and found that CBAC Systen was fully functional alongwith Biometric operational at Maingate & Entry to Licence area. However, biometric access system for the Control room was found non-functional. | 2.8 | Access control systems checked | 1334 | HPCL REWARI IRD | Bio-metric access control system for the control room to be made functional and till such time the system is restored, additional precautions to be taken to ensure none unauthorised access. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017364ACN-2026-09-4000153346 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153346 | 2026-09-10 17:00 | 39.0455 | 424 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153346 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153346 |  | AUD-2026-09-2000017364ACN-2026-09-4000153346 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153347 | Open |  |  | HVLR - Total 06 Nos of HVLR is available at the Location. HVLR No. 06 – Checked for its movement in all directions and found satisfactory. It was operated by an operator and his knowledge about the operating procedure for HVLR was found to be adequate. Its throw in jet mode was found to be adequate and the fog generation was as desired. RSFPS - Only one tank, TK-26, is equipped with anRSFPS. However, it is brought to notice that operation of the RSFPS cannot be carried out from the control room due to an issue with the software available. Pending point of previous inspection. HCD - Total 16 Nos of HCD available at the location. Out of which 07 nos are Open path and 09 Nos are Point type HCD. All HCD's are operatinal Open Path Type HCD No: 01 located at Pump House was checked with filter- local hooter got actuated along with hooter in the control room. Point type HCD No: 03 was tested & local as well as control room hooters performed their tast as required. OP HCD in the dyke of TK11 was also checked and local hooter operated instantaneously. However, there was a significant lag in operation of the control room hooter. ESD - Total 14 No of ESDsare available at the location. Functionality of ESD at Security Cabin was verified during the mock fire drill conducted on 9th Sep'26 and was found to be okay. ESD checking record is also being maintained by the location. However, break-glass switch of ESD04 nearsecurity cabin was not having glass. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1334 | HPCL REWARI IRD | Necessary corrective action to be taken. | SOD | Marketing | NZ | 2026-12-10 |  | 1 |  | S1 | F1 | 2026-12-10 | AUD-2026-09-2000017364ACN-2026-09-4000153347 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153347 | 2026-09-10 17:00 | 39.0455 | 465 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153347 | 532 | 8294 | 21 | 8294 | -51 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153347 |  | AUD-2026-09-2000017364ACN-2026-09-4000153347 | 21 |  | 27 | 80 | 1 | 1 | 67
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153348 | Open |  |  | A session was conducted with the TT crew to brief them on road safety. After the session, one DCP of TT no. HR38X5024 was operated and both the equipment and the TT driver operating it functioned as per requirement. However, the TT number was not marked on the DCP. TREM card was also available with all TT crew members. | 2.14 | TT crew fire extinguisher usage checked | 1334 | HPCL REWARI IRD | Location to ensure permanent incorporation of TT number on each DCP fire extinguisher owned by them. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017364ACN-2026-09-4000153348 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153348 | 2026-09-10 17:00 | 39.0455 | 424 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153348 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153348 |  | AUD-2026-09-2000017364ACN-2026-09-4000153348 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153349 | Open |  |  | Thorough checking TT No HR55AC1806 was done along with LIC and concerned officer to sensitize the need for proper inspection of TTsin line with the extant circular. 4 Nos NC issued | 3.1 | TT fittings & discipline checked | 1334 | HPCL REWARI IRD | Compliance of the observation made w.r.t. TT inspected to ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017364ACN-2026-09-4000153349 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153349 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153349 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153349 |  | AUD-2026-09-2000017364ACN-2026-09-4000153349 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153350 | Open |  |  | EM lock check record , 5% checkng is done on daily basis. Location to create record to ensure that 100% locks are checked on monthly basis | 3.5 | EM Lock SOP compliance verified | 1334 | HPCL REWARI IRD | Location to create record to ensure that 100% locks are checked on monthly basis | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017364ACN-2026-09-4000153350 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153350 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153350 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153350 |  | AUD-2026-09-2000017364ACN-2026-09-4000153350 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153351 | Open |  |  | Out of total 1304 instances of reconciliations during the period 9th Jun'26 to 9th Sep'26, none of the instances were with abnormalvariations. During the visit, following unused assets were found lying at the location: 1. One diesel driven Scorpio Jeep whichis having age of more than 10 yrs. and cannot be used due to restriction in NCR region. 2. One old fire engine with some of the parts already used for existing engines. 3. Product tanks# TK1 (MS-AG-590KL), TK2 (MS-AG-590KL) & TK17 (Slop Tank-AG-500KL) and TK7 (MS-UG-22KL)- kept redundant due to leakage identified during comprehensive inspection of the facility. 4. DG set of capacity 250KVA. | 3.9 | Abnormal variations / unused assets reviewed | 1334 | HPCL REWARI IRD | For idle/ unused assets, location is advised to: 1. Update their details in the surplus portal which can be spared for use elsewhere as per requirement. 2. Originate proposals for seeking funds to make these assets operational. 3. Originate RFDs for disposal if the asset doesn't fall under the above 2 criteria. | SOD | Marketing | NZ | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017364ACN-2026-09-4000153351 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153351 | 2026-09-10 17:00 | 39.0455 | 409 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153351 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153351 |  | AUD-2026-09-2000017364ACN-2026-09-4000153351 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153352 | Open |  |  | Avg. TFMS-SAP reconciliation % for the period Apr'26 to Aug'26 is 93.6%. | 3.1 | TFMS/SAP reconciliation checked | 1334 | HPCL REWARI IRD | Location is advised to improve the TFMS-SAP performance. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017364ACN-2026-09-4000153352 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153352 | 2026-09-10 17:00 | 39.0455 | 424 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153352 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153352 |  | AUD-2026-09-2000017364ACN-2026-09-4000153352 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153353 | Open |  |  | Housekeeping - Housekeeping of the location is found to be Satisfactory with some areas requiring minor upkeep which were discussedduring field round with location team, like rusting in TT gantry structure, pipelines and gratings. AC servicing required in Security Gaurd room. PPE - During visit it was observed that all Contract workers along with Officers are adhering to guidelines of PPE usage and adequate no of PPE's available at the location. List of PPE available at location is enclosed. | 3.15 | Housekeeping & PPE usage checked | 1334 | HPCL REWARI IRD | TT gantry structure, gratings and pipeline sinlge coat of painting to be done | SOD | Marketing | NZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-09-2000017364ACN-2026-09-4000153353 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153353 | 2026-09-10 17:00 | 39.0455 | 485 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153353 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153353 |  | AUD-2026-09-2000017364ACN-2026-09-4000153353 | 21 |  | 27 | 80 | 1 | 1 | 70
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153354 | Open |  |  | A total of 05 open MOCs are reflecting in the system. | 3.17 | MOC status reviewed | 1334 | HPCL REWARI IRD | Location to ensure timely closure of all the open MOCs. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017364ACN-2026-09-4000153354 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153354 | 2026-09-10 17:00 | 39.0455 | 394 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153354 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153354 |  | AUD-2026-09-2000017364ACN-2026-09-4000153354 | 21 |  | 27 | 80 | 1 | 1 | 57
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153355 | Open |  |  |  | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1334 | HPCL REWARI IRD | 1. Auto sampler in Bay 1 not working. To be rectified. 2. False ceiling in staff room to be repaired. 3. Maintenance officer to go thru OEM Manual for STP and know fully about operations. 4. Old defunct Insectr killer to be removed from staff room. 5. Emergency Gate lock key computer to be rectified.Tk 26 RIm seal Protection system to be made operational from control room. 6. 3 Nos fire engines have completed 12 years of service life. Location to seek Budget of Rs 1 crore from HQO for replacement of same. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017364ACN-2026-09-4000153355 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153355 | 2026-09-10 17:00 | 39.0455 | 486 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153355 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153355 |  | AUD-2026-09-2000017364ACN-2026-09-4000153355 | 21 |  | 27 | 80 | 1 | 1 | 70
[5 empty] | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153357 | Open |  |  | During discussion with location , location advised that there is suspected leakage in IOCL PLT Underground Pipelines. Location was advised to do pressure testing of line with product within 15 days and corrective action like clamps , sleeving with in one month | 6.1 | High priority areas requiring immediate action. | 1334 | HPCL REWARI IRD | Necessary corrective actions to be taken. | SOD | Marketing | NZ | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017364ACN-2026-09-4000153357 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153357 | 2026-09-10 17:00 | 39.0455 | 409 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153357 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153357 |  | AUD-2026-09-2000017364ACN-2026-09-4000153357 | 21 |  | 27 | 80 | 1 | 1 | 59
AILAVARAPU VENKATA KRISHNA MURTY | 2026-09-19 | DIWAKAR KAMLESH KUMAR | 2026-09-19 | Presently there is no clause available in Security Contract or Tender Terms which mentions security personnel to have HVD /HZA movement. However TT crews are available with TT during loading of TT and also in TT parking area where TT are kept in parking conditions when they arrive for next Load. Hence TT crews are available to handle any Emergency situations. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143379 | Closed | DIWAKAR KAMLESH KUMAR | 2026-09-19 | No Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 3708 | VISAKH NBOT | Location to explore the availability Trained security personnel with HVD/HZA endorsement | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143379 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143379 | 2026-09-18 17:30 | 31.0247 | 383 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143379 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143379 | AUD-2026-07-2000015047ACN-2026-07-4000143379 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 55
AILAVARAPU VENKATA KRISHNA MURTY | 2026-09-19 | DIWAKAR KAMLESH KUMAR | 2026-09-19 | Necessary corrective action has been done. New Light has been fixed and 3 Nos. of NMew High Mast Towers has been installed and commissioned.Now Lux level is in line with OISD requiremenmt. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125084 | Closed | DIWAKAR KAMLESH KUMAR | 2026-09-19 | Lux levels checked . TT Gantry - 77 , Product Pump House 120, Fire Pump House - 175, TK 208 manifold - 41, Secondary road near Bio diesel unloading gantry -3 , Admin - 320 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 3708 | VISAKH NBOT | Lux levels on roads is low . New HMT lighting works to be expedited. Lux level on platforms of manifold valves , ROSOV's, is low and not meeting requirements . Additional lights to be provided | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011315ACN-2026-03-4000125084 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125084 | 2026-09-18 17:30 | 31.0247 | 383 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125084 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125084 | AUD-2026-03-2000011315ACN-2026-03-4000125084 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 55
AILAVARAPU VENKATA KRISHNA MURTY | 2026-09-19 | DIWAKAR KAMLESH KUMAR | 2026-09-15 | Additional focused light and High Mast tower commssioned. Now lux level is matching OISD Guideline | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143374 | Closed | DIWAKAR KAMLESH KUMAR | 2026-09-15 | Lux levels checked and reading taken at PH-1, PH-2, PH-3, Main Operating platform-TTG1, Main Operating platform-TTG2, Main Operating platform-tank manifold dyke 1, Main Operating platform-tank manifold dyke 2, Main Operating platform-tank manifold dyke 3 and following values observed 180 ( vs 100), 110 vs 100, 136 vs 100, 160 vs 60, 77 vs 60, 17 vs 60, 5 vs 60 and 64 vs 60, respectively. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 3708 | VISAKH NBOT | Corretive action to be taken for correcting low lux level at Operating platform-tank manifold dyke 1 & Main Operating platform-tankmanifold dyke 2 | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143374 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143374 | 2026-09-18 17:30 | 31.0247 | 383 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143374 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143374 | AUD-2026-07-2000015047ACN-2026-07-4000143374 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 55
AILAVARAPU VENKATA KRISHNA MURTY | 2026-09-19 |  |  | 1. CCTV camera IP144: TT Parking, IP176: Compressor shed made functional. 2. CCTV IP172: camera is dirty cleaned, 3. Concertinacoil installed at 6 pole yard side. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143377 | Closed | DIWAKAR KAMLESH KUMAR | 2026-09-15 | CCTV functioning checked. 1. Three (2) CCTV offline/not working ( IP144: TT Parking, IP176: Compressor shed) out of total 60 CCTV. 2. CCTV IP172: camera is dirty need to be cleaned, Concertina coil is not there at 6 pole HT yard | 2.6 | CCTV functioning checked | 3708 | VISAKH NBOT | Corretive action to be taken for : 1. Three CCTV offline/not working ( IP144: TT Parking, IP176: Compressor shed) to be made functional 2. CCTV IP172: camera is dirty need to be cleaned, 3. Concertina coil to be rectified at 6 pole HT yard and other places wherever concertina coil is damaged. | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143377 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143377 | 2026-09-18 17:30 | 31.0247 | 383 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143377 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143377 | AUD-2026-07-2000015047ACN-2026-07-4000143377 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 55
|  | SAXENA UMESH CHANDRA | 2026-09-19 | BCU-MFM totaliser difference reports are being signed on daily basis. One sample report is attached in CAPA. Observation may therefore be closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152280 | Completed | SAXENA UMESH CHANDRA | 2026-09-19 | Location carryout daily checking of MFM and BCU difference with the day end report. Report verified. Location to ensure signing of report on daily basis without fail. | 3.11 | MFM vs BCU totalizer comparison checked | 1457 | INDORE DEPOT | Location to ensure signing of report on daily basis without fail. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152280 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152280 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152280 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152280 |  | AUD-2026-09-2000017752ACN-2026-09-4000152280 | 21 |  | 27 | 80 | 0 | -3 | 57
|  | SAXENA UMESH CHANDRA | 2026-09-19 | No local loading was done as both MS & HSD batches started exactly at the same time. The same was also confirmed with TAS vendor. Further, written statements from driver and helper were also taken and are enclosed. Audit observation may therefore be closed in view of no local loading. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152281 | Completed | SAXENA UMESH CHANDRA | 2026-09-19 | Local loading was done only for own use (DG Sets, Fire Engine and company vehicle). Local loading exception was observed for one ofthe TT (TT No: MP43ZD 7381) on 22.08.2026. Local loading report for each day is attached with the day end report and signed by the LIC and TAS officer. | 3.14 | Local loading checks (if applicable) | 1457 | INDORE DEPOT | Location to carry out root cause analysis/ further investigation for local loading of TT No: MP43ZD 7381. | SOD | Marketing | CEN | 2026-09-30 | THIRD PARTY ERRORS | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152281 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152281 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152281 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017752ACN-2026-09-4000152281 |  | AUD-2026-09-2000017752ACN-2026-09-4000152281 | 21 |  | 27 | 80 | 0 | -3 | 57
|  | SAXENA UMESH CHANDRA | 2026-09-19 | Only open point of Sr Mgmt Audit Q1 has been closed. Observation may therefore be closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152270 | Completed | SAXENA UMESH CHANDRA | 2026-09-19 | Yes, only one point related to MDSA is open that needs to be closed. | 1.4 | Earlier action points status checked | 1457 | INDORE DEPOT | Only one point related to MDSA is open that needs to be closed on priority. | SOD | Marketing | CEN | 2026-10-31 |  | 4 |  | S1 | F4 | 2026-10-31 | AUD-2026-09-2000017752ACN-2026-09-4000152270 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152270 | 2026-09-09 19:00 | 39.9622 | 425 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152270 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152270 |  | AUD-2026-09-2000017752ACN-2026-09-4000152270 | 21 |  | 27 | 80 | 0 | -3 | 61
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153116 | Open |  |  | Interacted with all officers. Concerns were raised with respect to delay in compliance of observation points. There are many pointswhich are repititive in every quarter. That means, location is not taking point seriously. Serious concern was raised by GM O&D to location officers. It was clearly informed that it is not the no. of points on which performance of location depends, rather, timelycompliance of observation points are indicative of good performance by location officers.performance of officer. Mr. Hemant Meena has worked on Electrical maintenance jobs. He has made list of electrical jobs. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1233 | BHARATPUR TERMINAL | Electrical maintenance PO needs to be revised. One electrician to be called in each shift. General shift electrician should not be paid on manpower basis. It should be on job basis. Hemant to develop LPR and tender document accordingly. Jobs related to maintenance, housekeeping which are done periodically in some fixed intervals (weekly, fortnightly, monthly, quarterly etc) are to be listedby officer. Pls ensure that jobs are carried out by contract workman. Supervisor needs to sign the PMS and officer needs to authenticate the same. If possible, pls get these jobs also converted into job basis PO. | SOD | Marketing | NWF | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017503ACN-2026-09-4000153116 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153116 | 2026-09-16 17:45 | 33.0143 | 486 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153116 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153116 |  | AUD-2026-09-2000017503ACN-2026-09-4000153116 | 21 |  | 27 | 80 | 2 | 1 | 70
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153117 | Open |  |  | 1. Lube disposal not done. 2. Discounted toll to be updated. It is till pending for few TTs. 3. Standing order to be prepared forrepaeted consumable items/supply items/service. 4. Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. 5. E-waste disposal is yet to be done. 6. Approx 8 MOVs are still not communicating | 1.3 | Pending issues reviewed | 1233 | BHARATPUR TERMINAL | 1. Lube disposal not done. 2. Discounted toll to be updated. It is till pending for few TTs. 3. Standing order to be prepared forrepaeted consumable items/supply items/service. PX voucher should be avoided for repeated service/supply items. 4. Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. 5. E-waste disposal is yet to bedone. 6. Approx 8 MOVs are still not communicating | SOD | Marketing | NWF | 2026-11-30 |  | 12 |  | S3 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153117 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153117 | 2026-09-16 17:45 | 33.0143 | 455 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153117 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153117 |  | AUD-2026-09-2000017503ACN-2026-09-4000153117 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153119 | Open |  |  | Foam supplier is not supplying 5.6 KL foam already ordered by location. It needs to be taken up by Zone. Central Foam tanks were found empty. This is serious. | 2.9 | Foam inventory verified | 1233 | BHARATPUR TERMINAL | Pls take zonal help for early supply of material. Pls treat this urgent and important. | SOD | Marketing | NWF | 2026-10-31 |  | 12 |  | S3 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153119 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153119 | 2026-09-16 17:45 | 33.0143 | 425 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153119 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153119 |  | AUD-2026-09-2000017503ACN-2026-09-4000153119 | 21 |  | 27 | 80 | 2 | 1 | 61
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153121 | Open |  |  | Branding of TT no. RJ02GB4727 is not good. | 3.1 | TT fittings & discipline checked | 1233 | BHARATPUR TERMINAL | Branding of all Tts to be verified and corrected. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153121 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153121 | 2026-09-16 17:45 | 33.0143 | 455 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153121 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153121 |  | AUD-2026-09-2000017503ACN-2026-09-4000153121 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153123 | Open |  |  | There are 44 stoppages of loaded Tts at 0.29 km from 0.76 Km From Bharatpur Terminal. This is the potential suspected points. Location should take action. | 3.3 | VTS deviations reviewed | 1233 | BHARATPUR TERMINAL | 1. Corrective action to be taken for all suspected points where multiple loaded Tts are stopping. 2. Training program to be delivered by Mr. Neetesh on VTS monitoring by DCT/transporter | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153123 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153123 | 2026-09-16 17:45 | 33.0143 | 425 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153123 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153123 |  | AUD-2026-09-2000017503ACN-2026-09-4000153123 | 21 |  | 27 | 80 | 2 | 1 | 61
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153128 | Open |  |  | 1. Fire water monitor no. 23 is blocked by tree. Trimming of branches to be done. 2. Pls carry out painting of MEFG pipeline of ETP. 3. SOP to be displayed for treated water pump. Shifting of water from ETP area to rain water harvesting area (sunken PH of TW) 4. ETP log book not maintained. 5. One Double Hydrant to be fitted near VRU. | 3.15 | Housekeeping & PPE usage checked | 1233 | BHARATPUR TERMINAL | 1. Fire water monitor no. 23 is blocked by tree. Trimming of branches to be done. 2. Pls carry out painting of MEFG pipeline of ETP. 3. SOP to be displayed for treated water pump. Shifting of water from ETP area to rain water harvesting area (sunken PH of TW) 4. ETP log book not maintained. 5. One Double Hydrant to be fitted near VRU. | SOD | Marketing | NWF | 2026-10-15 |  | 8 |  | S2 | F4 | 2026-10-15 | AUD-2026-09-2000017503ACN-2026-09-4000153128 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153128 | 2026-09-16 17:45 | 33.0143 | 409 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153128 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153128 |  | AUD-2026-09-2000017503ACN-2026-09-4000153128 | 21 |  | 27 | 80 | 2 | 1 | 59
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153132 | Open |  |  | 1. Location is having ample qty of spare 4 inch and 2 inch line. Location is requested to share the length of such spare pipes not in use. Location is also requested to share the details of spare ATF and SKO pumps. 2. 2 inch SS line connecting siding with OWS isnot in use. Pls remove these pipelines and keep in safe custody after safe cutting. 3. After removal of filers of ATF, it is also required to remove the branch ATF pipelines. This is behind TT gantry. After removal of these pipelines, B7 line is to be connected directly to main header. 4. Grass has grown very much in whole location. It needs to be cut on priority. 5. Pressure gauges directly fitted on pump suction and discharge pipe, are to be removed and to be mounted on angle bracket and to be connected to pump headers through hydrotested flexible hose. 6. Pumps were operated one by one in Product PH. Following pumps are not running or require maint. a. Ethanol pump no. 8 is to be repaired. b. Misalignment observed in MS pump no. 5, gap observed in rubber spider. c. Leakage observed in HSD pump no. 3 d. Press. gauge is not in working condition HSD pump no. 2 7. There are Eye wash system, Visual Identity boards at Scrap Yard. These should be installed after minor repair. 8. SS pipe (2 inch), kept near ETP, are touching ground. These should be shifted to PCC area. 9. SKO line and MS line coming from boundary wall near siding, upto TWPH are to be dismantled. MS line is filled with product. Product needs to be emptied using MOSRU (emergency vehicle). After removal of SKO and MS line, pls carry out complete housekeeping of old TWPH. There are many unwanted items like branch pipe, motor, vegetation etc on old TWPH. Pls clean that. Unwanted pipelines to be shifted as scrap line. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1233 | BHARATPUR TERMINAL | 1. Location is having ample qty of spare 4 inch and 2 inch line. Location is requested to share the length of such spare pipes not in use. Location is also requested to share the details of spare ATF and SKO pumps. 2. 2 inch SS line connecting siding with OWS isnot in use. Pls remove these pipelines and keep in safe custody after safe cutting. 3. After removal of filers of ATF, it is also required to remove the branch ATF pipelines. This is behind TT gantry. After removal of these pipelines, B7 line is to be connected directly to main header. 4. Grass has grown very much in whole location. It needs to be cut on priority. 5. Pressure gauges directly fitted on pump suction and discharge pipe, are to be removed and to be mounted on angle bracket and to be connected to pump headers through hydrotested flexible hose. 6. Pumps were operated one by one in Product PH. Following pumps are not running or require maint. a. Ethanol pump no. 8 is to be repaired. b. Misalignment observed in MS pump no. 5, gap observed in rubber spider. c. Leakage observed in HSD pump no. 3 d. Press. gauge is not in working condition HSD pump no. 2 7. There are Eye wash system, Visual Identity boards at Scrap Yard. These should be installed after minor repair. 8. SS pipe (2 inch), kept near ETP, are touching ground. These should be shifted to PCC area. 9. SKO line and MS line coming from boundary wall near siding, upto TWPH are to be dismantled. MS line is filled with product. Product needs to be emptied using MOSRU (emergency vehicle). After removal of SKO and MS line, pls carry out complete housekeeping of old TWPH. There are many unwanted items like branch pipe, motor, vegetation etc on old TWPH. Pls clean that. Unwanted pipelines to be shifted as scrap line. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153132 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153132 | 2026-09-16 17:45 | 33.0143 | 455 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153132 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153132 |  | AUD-2026-09-2000017503ACN-2026-09-4000153132 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153133 | Open |  |  | 1. VRU is not functional. To be repaired. Location informed that tender is already floated for VRU functionality. Location to sharemonthly progress to Zone on the same. 2. Paint condition of TK5 and TK6 (ethanol tanks) are dull. Though, no pitting/rusting observedon tank body and roof, there is peel off of paint on tank roof. Tanks were last painted on May 2018. It may be taken for painting. Gratings of few ladders in staircase was found pitted. | 4.2 | Maintenance activities reviewed | 1233 | BHARATPUR TERMINAL | 1. VRU is not functional. To be repaired. Location informed that tender is already floated for VRU functionality. Location to sharemonthly progress to Zone on the same. | SOD | Marketing | NWF | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017503ACN-2026-09-4000153133 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153133 | 2026-09-16 17:45 | 33.0143 | 486 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153133 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153133 |  | AUD-2026-09-2000017503ACN-2026-09-4000153133 | 21 |  | 27 | 80 | 2 | 1 | 70
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153134 | Open |  |  | 1. Bay 4 is to have mixed product loading. Location has assured to close this project by 30.11.2026. 2. Secondly, bay 3 (ATF bay) can be converted into full HSD. Pls explore this and convert this bay also. 3. RSFPS is not in working condition TK17. Purchase order is to be placed by CPO. Tendering already done. Pls keep minimum inventory in this tank. Get MOC approved after finalysing SOP. 4. Vapour duct at TWPH are not usable. This is made up of huge qty of GI sheet. Whole box can be used as canopy for ROSOV/MOV/DBBV. Pls do that. Spare qty can be sent to other Rajasthan locations for similar purpose 5. Show TWPH as Rain water harvesting area in PESO layout. | 4.3 | Project progress reviewed | 1233 | BHARATPUR TERMINAL | 1. Bay 4 to be converted into mixed bay by 30.11.2026. Bay 3 to be converted into express HSD bay. 2. RSFPS is not in working condition TK17. Purchase order is to be placed by CPO. Tendering already done. Pls keep minimum inventory in this tank. Get MOC approved after finalysing SOP. 3. Location to apply for additional budget in SAP. 4. Vapour duct at TWPH are not usable. This is made up of huge qty of GI sheet. Whole box can be used as canopy for ROSOV/MOV/DBBV. Pls do that. Spare qty can be sent to other Rajasthan locations for similar purpose 5. Show TWPH as Rain water harvesting area in PESO layout. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153134 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153134 | 2026-09-16 17:45 | 33.0143 | 455 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153134 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153134 |  | AUD-2026-09-2000017503ACN-2026-09-4000153134 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153135 | Open |  |  | It is observed that many costly materials are kept inside store. This includes, MFM, Radar, Pumps of different capacities etc. There are many wooden boxes/cartoon etc which are not attended. Pls make inventory of all costly materials and share with Zone | 4.4 | Quality of PM compliance reviewed | 1233 | BHARATPUR TERMINAL | 1. Segregation of usable and disposable materials inside store. Make inventory of usable and costly material in excel sheet. InformZone. Make RFD for all scrappable materials seen inside store and scrap yard. 2. One register at TT gantry to be maintained. This register should have entries of all issues at TT gantry. It may be related to maintenance, electrical issue, operational issue. Thismay be filled by contract staff in their language. TAS officer and M&I officer to review this register on weekly basis and LIC to review this register on monthly basis for compliance of job identified by gantry workman/officer 3. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FPpanel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. Itis advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. 4. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153135 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153135 | 2026-09-16 17:45 | 33.0143 | 455 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153135 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153135 |  | AUD-2026-09-2000017503ACN-2026-09-4000153135 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153136 | Open |  |  | 1. There are short length pipeline, branch pipe with multiple bends near ETP. These are not usable and should be segregated for scrap disposal. 2. Pls check all balance materials in siding area other than pipeline. It was observed that cable tray (laid on boundary wall), channel support, structure, lightig pole etc are still lying in siding area. These items are to be disposed through RFD. 3. RRKPL scrap to be removed from scrap yard. 4. I observed damaged plastic water tanks, old gate valve, Fire engine block and cam shaft, exhaust pipe, light tin materials, old fire ext. etc. These materials are of no use and should disposed. There are old almirah, old barrier gate. Pls check for its use. If not, pls dispose. 5. There are unused panels inside store. e-auction is already completed. Physical disposal is pending. Pls do that. 6. Inventory of surplus cables to be shared with Zone 7. There are approx 15 assets which are held for sale. RFDs of these assets are already approved. However, either physical disposal is pending or AMDA not made. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1233 | BHARATPUR TERMINAL | 1. There are short length pipeline, branch pipe with multiple bends near ETP. These are not usable and should be segregated for scrap disposal. 2. Pls check all balance materials in siding area other than pipeline. It was observed that cable tray (laid on boundary wall), channel support, structure, lightig pole etc are still lying in siding area. These items are to be disposed through RFD. 3. RRKPL scrap to be removed from scrap yard. 4. Observed damaged plastic water tanks, old gate valve, Fire engine block and cam shaft, exhaust pipe, light tin materials, old fire ext. etc. These materials are of no use and should disposed. There are old almirah,old barrier gate. Pls check for its use. If not, pls dispose. 5. There are unused panels inside store. e-auction is already completed. Physical disposal is pending. Pls do that. 6. Inventory of surplus cables to be shared with Zone. 7. Pls dispose the assets for which RFD is already approved. AMDA to be made after physical disposal of assets. There should be nil assets held for sale | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153136 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153136 | 2026-09-16 17:45 | 33.0143 | 425 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153136 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017503ACN-2026-09-4000153136 |  | AUD-2026-09-2000017503ACN-2026-09-4000153136 | 21 |  | 27 | 80 | 2 | 1 | 61
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | all pending points are complied | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-03-4000123042 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-12 | Closure of SSA/ MDSA Points, Scrap Liquidation, M&I projects execution, Dormant Keys & Locks, CCTV Cameras | 5.1 | High priority areas requiring immediate action. | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010862ACN-2026-03-4000123042 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123042 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123042 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123042 | AUD-2026-03-2000010862ACN-2026-03-4000123042 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 55
KAPIL DEV | 2026-09-21 | SINGH KUNAL | 2026-09-16 | All TT crew and contract workmen are being checked with Breath analyser before release inside terminal premises. Records are being maintained. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146309 | Closed | SINGH KUNAL | 2026-09-16 | Security guards and electricians in night shift to be checked with breath analyzer and records to be maintained. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146309 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146309 | 2026-09-10 21:00 | 38.8788 | 385 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146309 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146309 | AUD-2026-07-2000016503ACN-2026-07-4000146309 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 55
KAPIL DEV | 2026-09-21 | SINGH KUNAL | 2026-09-16 | Emergency contact list has been updated and contact numbers of Zonal officers | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146340 | Closed | SINGH KUNAL | 2026-09-16 | Emergency contact list did not display the contact numbers of zonal officers and HQO officers. | 6.16 |  | 1410 | VADODARA TERMINAL | Point to be complied | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146340 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146340 | 2026-09-10 21:00 | 38.8788 | 385 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146340 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146340 | AUD-2026-07-2000016503ACN-2026-07-4000146340 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 55
KAPIL DEV | 2026-09-21 | SINGH KUNAL | 2026-09-16 | SOP Board for display during ESD has been provided. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146341 | Closed | SINGH KUNAL | 2026-09-16 | No display board was available indicating the consequences or actions following ESD activation. | 6.17 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146341 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146341 | 2026-09-10 21:00 | 38.8788 | 385 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146341 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146341 | AUD-2026-07-2000016503ACN-2026-07-4000146341 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 55
SUJEET KUMAR | 2026-09-21 | SAXENA UMESH CHANDRA | 2026-09-19 | The same point is open in Q2 Senior Mgmt Audit conducted in Sept 2026. Hence the point may be closed here. | LOCATION VISIT AT INDORE IRD | 2026-06-05 19:30 | AUD-2026-06-2000012547 | 2026-06-04 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000135376 | Closed | SAXENA UMESH CHANDRA | 2026-09-19 | Yes, Location is advised to expedite closure of all 22 open MDSA Audit observation points in a time bound manner. Also, location toensure compliances at TT parking as per latest circular. | 1.6 | Expectations clearly communicated to officers | 1457 | INDORE DEPOT | Location is advised to expedite closure of all 22 open MDSA Audit observation points in a time bound manner. Also, location to ensure compliances at TT parking as per latest circular and confirm by 13.06.2026. | SOD | Marketing | CEN | 2026-12-31 | COMPLACENCY OR RISK NORMALIZATION | 8 | OCCUPATIONAL HEALTH | S2 | F4 | 2026-12-31 | AUD-2026-06-2000012547ACN-2026-06-4000135376 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012547ACN-2026-06-4000135376 | 2026-09-09 19:00 | 39.9622 | 385 | >20 | AUD-2026-06-2000012547 - ACN-2026-06-4000135376 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012547ACN-2026-06-4000135376 | AUD-2026-06-2000012547ACN-2026-06-4000135376 | 21 | 21 | 27 | 80 | 0 | -3 | 70 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Bi-weekly updation of compliance report is sent to zone. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150574 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Recent review recommendations were discussed, along with the pending audit observations . MDSA 2026-27 points were discussed in detail and action plan for compliance reviewed. Preparations for OISD audit reviewed | 1.4 | Earlier action points status checked | 1940 | KADAPA DEPOT | Bi-weekly updation of compliance report to be sent to zone. | SOD | Marketing | SCR | 2026-08-25 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-25 | AUD-2026-09-2000017202ACN-2026-09-4000150574 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150574 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150574 | 532 | 8294 | 21 | 8294 | 55 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150574 | AUD-2026-09-2000017202ACN-2026-09-4000150574 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150575 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Location Observed Lux Required Lux Status P.P.H. / Pump House 160 TT Gantry- 160 ROSOV / MOV Area 35 not meeting requirement Tank Farm Road 40 Main Road 9 (not meeting requirement) Security cabin 120 Substation 170 Control Room 410 , Admin building - 380 , TT parking Area -11 (not meeting reuirements) , ETP area 43 (not meeting requirement) | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1940 | KADAPA DEPOT | Lux levels to be improved at manifold area, main roads , ETP area , TT parking area to meet required Lux levels. | SOD | Marketing | SCR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-05 | AUD-2026-09-2000017202ACN-2026-09-4000150575 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150575 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150575 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150575 | AUD-2026-09-2000017202ACN-2026-09-4000150575 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Emergency trolley is available with all the required items. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150576 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | The Emergency Response Toolkit Trolley was inspected. Few items were found missing. Electrical gloves expiry date crossed. | 2.5 | Emergency response preparedness reviewed | 1940 | KADAPA DEPOT | To take corrective action for emergency trolley availability with all the required items. | SOD | Marketing | SCR | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017202ACN-2026-09-4000150576 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150576 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150576 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150576 | AUD-2026-09-2000017202ACN-2026-09-4000150576 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150577 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | CCTV fucntioning cheked and observed that 58 camera are working out of 60 no's. Following Observation were noted while reviewing cctv Recording -1. Siding perimeter camera not working,2.ETP Perimeter -03 - angle to be adjusted, 3.FPH camera hazy , lens to be cleaned, 4.Rly Siding perimeter 02 to be adjusted for angle, 5. Rly Siding perimeter 5 - image appearing inverted , Rly siding perimeter7 camera is hazzy, 8. Water tank behind camera not working 9. TTG Bay 07-08 angle to be adjusted | 2.6 | CCTV functioning checked | 1940 | KADAPA DEPOT | ALL the non Functional cctv camera to be rectified immedaitely and discrepancies to be attended immediately by 31.08.2026 | SOD | Marketing | SCR | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017202ACN-2026-09-4000150577 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150577 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150577 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150577 | AUD-2026-09-2000017202ACN-2026-09-4000150577 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150578 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Main Gate Turnstile is under repair | 2.8 | Access control systems checked | 1940 | KADAPA DEPOT | Main Gate Turnstile to be repaired and put back in operation | SOD | Marketing | SCR | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017202ACN-2026-09-4000150578 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150578 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150578 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150578 | AUD-2026-09-2000017202ACN-2026-09-4000150578 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
SUJEET KUMAR | 2026-09-21 | SAXENA UMESH CHANDRA | 2026-09-19 | Checked CCTV footage today i.e. on 19.09.2026 of the same camera and found recording of 19.06.2026 is available(screenshot is enclosed). Audit observation may therefore be considered as complied with and may be closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152275 | Closed | SAXENA UMESH CHANDRA | 2026-09-19 | All 70 CCTV cameras are working. Previous recording for several days in the month of June 2026 of Security Cabin was not available. | 2.6 | CCTV functioning checked | 1457 | INDORE DEPOT | Location to check and ascertain the root cause for not having recording of Security Cabin for several dates in the month of June 2026. | SOD | Marketing | CEN | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152275 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152275 | 2026-09-09 19:00 | 39.9622 | 385 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152275 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017752ACN-2026-09-4000152275 | AUD-2026-09-2000017752ACN-2026-09-4000152275 | 21 | 21 | 27 | 80 | 0 | -3 | 57 | 55
SUJEET KUMAR | 2026-09-21 | SAXENA UMESH CHANDRA | 2026-09-19 | At the time of the audit, a few CCTV cameras could not be configured due to incorrect IP addresses. However, all 70 CCTV cameras have since been successfully configured and are currently live. A screenshot of the VA dashboard showing the status of all cameras is enclosed as part of the CAPA. Observation may therefore be closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152276 | Closed | SAXENA UMESH CHANDRA | 2026-09-19 | VA implementation is under process and targeted to complete by 30.09.2026 | 2.7 | VA alerts checked / analysed | 1457 | INDORE DEPOT | Location to ensure implementation of VA in all respect by 30.09.2026. | SOD | Marketing | CEN | 2026-09-30 | THIRD PARTY ERRORS | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152276 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152276 | 2026-09-09 19:00 | 39.9622 | 385 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152276 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017752ACN-2026-09-4000152276 | AUD-2026-09-2000017752ACN-2026-09-4000152276 | 21 | 21 | 27 | 80 | 0 | -3 | 57 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150579 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | HVLR no. 5, TK-101B Rim Seal, TK-101B open path, TK-202 A open path , and TW Pump House Open-Type HCD were operated and found to befunctioning satisfactorily. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1940 | KADAPA DEPOT | Proper calllibration of HCD films of both 20% and 40% to be done. Initially throw of HVLR 5 was not coming properly, took time to start. Location to ensure timely operation. | SOD | Marketing | SCR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-09-05 | AUD-2026-09-2000017202ACN-2026-09-4000150579 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150579 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150579 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150579 | AUD-2026-09-2000017202ACN-2026-09-4000150579 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Master key sent back to M/s.sterna for replacement. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150580 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | EM Lock functionality of 5 TTs was checked using the Intelligent Key for TT nos AP39UZ9409,TN03AL3163,AP39UA7898,AP39WK9391,AP39VF4242 , Found OK. | 3.5 | EM Lock SOP compliance verified | 1940 | KADAPA DEPOT | LIC Master key to sent back to M/s.sterna for replacement, to follow up with vendor | SOD | Marketing | SCR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-05 | AUD-2026-09-2000017202ACN-2026-09-4000150580 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150580 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150580 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150580 | AUD-2026-09-2000017202ACN-2026-09-4000150580 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 55
KUMAR CHAKRABORTI ALOK | 2026-09-21 | PATHAK AHELI | 2026-09-19 | Complied as per recommendation | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141870 | Closed | PATHAK AHELI | 2026-09-19 | 1. Filenote for TFMS-SAP integration to be submitted before 10.06.2026. 2. Proposal for ATF loading at 2 Bays to be put up by 10.06.2026. 3. MS line hook up at MRPL to be expedited. 4. Proposal for additional 5000 KL MS tankage shall be initiated. 5. Proposal forRECD. | 1.8 | Improvement plans discussed | 1775 | BENGALURU TERMINAL | To expedite at the earliest | SOD | Marketing | SWZ | 2026-07-10 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141870 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141870 | 2026-09-24 17:00 | 25.0455 | 385 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141870 | 532 | 8294 | 21 | 8294 | 101 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141870 | AUD-2026-06-2000014499ACN-2026-06-4000141870 | 21 | 21 | 27 | 80 | 0 | 0 | 45 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Ensured that variations in tank dip and temp remains with in tolerance limit . | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150581 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Checked for TK101B TAS Readings : Dip Level : 106.3 cms , Water level : 0 ,Temp : 33°C . Actual Physical Dip Level : 106.39 cms , Water level : 0 ,Temp : 31.2°C | 3.7 | Inventory physical dip of minimum two tanks taken | 1940 | KADAPA DEPOT | Location to take up with TAS vendor and ensure that variations in tank dip and temp remain with in tolerance limit . | SOD | Marketing | SCR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-05 | AUD-2026-09-2000017202ACN-2026-09-4000150581 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150581 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150581 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150581 | AUD-2026-09-2000017202ACN-2026-09-4000150581 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 55
KUMAR CHAKRABORTI ALOK | 2026-09-21 | PATHAK AHELI | 2026-09-19 | Lux Level increased as per requirement | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141871 | Closed | PATHAK AHELI | 2026-09-19 | Checked lux levels in all areas of operation, Lux Levels in tank farm area and admin building not meeting requirement | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1775 | BENGALURU TERMINAL | Lux level at tank farm area & admin building to be enhanced to required level. | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-06-2000014499ACN-2026-06-4000141871 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141871 | 2026-09-24 17:00 | 25.0455 | 385 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141871 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141871 | AUD-2026-06-2000014499ACN-2026-06-4000141871 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | All the Pending audit observations are complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150582 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | MDSA, TAS, and SSA compliance status was reviewed. The location was advised to ensure 100% compliance with all pending observationswithin the stipulated target dates. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1940 | KADAPA DEPOT | Pending audit observations to be complied as per target dates | SOD | Marketing | SCR | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017202ACN-2026-09-4000150582 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150582 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150582 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150582 | AUD-2026-09-2000017202ACN-2026-09-4000150582 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
KUMAR CHAKRABORTI ALOK | 2026-09-21 | PATHAK AHELI | 2026-09-19 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141883 | Closed | PATHAK AHELI | 2026-09-19 | 1. Commissioning of Tank 30 (Ethanol/Gasohol) to be done on priority, PESO final approval & OISD pre-commissioning report to be expedited. 2. Road excavated for maintenance work to be put back to original condition prior to releasing GRN. Any civil/ fabrication jobs done, vendors to be asked to do site clearance before processing their bills | 4.3 | Project progress reviewed | 1775 | BENGALURU TERMINAL | To expedite at the earliest | SOD | Marketing | SWZ | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141883 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141883 | 2026-09-24 17:00 | 25.0455 | 385 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141883 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141883 | AUD-2026-06-2000014499ACN-2026-06-4000141883 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150583 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Full field round completed (gantry/tank farm/pump house/siding/control room/security/admin). FE1 coolant leakage, gland leakage,smoke from engine observed. For FE-2 and FE-5 the DP observed 12.9 which is higher than the given range of 10-11. While testing thesequence of fire pumps FE -4 started in place of FE-3, FE-4 gland leakage observed,For FE-2, smoke observed from alternator and wiring for panel damaged . LLOP & overspeed simulation could not be shown for all FEs. Insulation cladding for all FEs to be properly fixed. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-08-25 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-25 | AUD-2026-09-2000017202ACN-2026-09-4000150583 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150583 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150583 | 532 | 8294 | 21 | 8294 | 55 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150583 | AUD-2026-09-2000017202ACN-2026-09-4000150583 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | 3 ARS closed. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150584 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | 3 Carryover projects in Technically completed status to be closed. Current year projects appropriation to be done | 4.3 | Project progress reviewed | 1940 | KADAPA DEPOT | 3 ARS to be closed | SOD | Marketing | SCR | 2026-08-25 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-25 | AUD-2026-09-2000017202ACN-2026-09-4000150584 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150584 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150584 | 532 | 8294 | 21 | 8294 | 55 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150584 | AUD-2026-09-2000017202ACN-2026-09-4000150584 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150585 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Scrap generated from new ethanol tank construction works to be disposed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1940 | KADAPA DEPOT | RFD to be made and location to be scrap free by Q-III | SOD | Marketing | SCR | 2026-09-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-20 | AUD-2026-09-2000017202ACN-2026-09-4000150585 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150585 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150585 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150585 | AUD-2026-09-2000017202ACN-2026-09-4000150585 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Complied. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150587 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Near Miss Reporting to be improved. | 6.1 |  | 1940 | KADAPA DEPOT | Near Miss Reporting to be improved. | SOD | Marketing | SCR | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-09-2000017202ACN-2026-09-4000150587 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150587 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150587 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150587 | AUD-2026-09-2000017202ACN-2026-09-4000150587 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 55
SUJEET KUMAR | 2026-09-21 | SAXENA UMESH CHANDRA | 2026-09-19 | This observation relates to the closure of open MDSA points. The same observation has already been captured under Audit Point 1.6 of the same audit. Hence, this may be treated as a duplicate observation and closed accordingly. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152285 | Closed | SAXENA UMESH CHANDRA | 2026-09-19 | OISD - 0, SSA - 0 and MDSA - 03 pending against total observation point of 42. Targeted to complete it by Dec' 2026. The pending points are 1) Live Fire Training 2) QRA of Rly siding 3) SOP Updation | 3.18 | OISD/MDSA/SSA compliance reviewed | 1457 | INDORE DEPOT | Closure of 03 Open MDSA points to be expedited within set timeline. | SOD | Marketing | CEN | 2026-10-15 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S1 | F4 | 2026-10-15 | AUD-2026-09-2000017752ACN-2026-09-4000152285 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152285 | 2026-09-09 19:00 | 39.9622 | 385 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152285 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017752ACN-2026-09-4000152285 | AUD-2026-09-2000017752ACN-2026-09-4000152285 | 21 | 21 | 27 | 80 | 0 | -3 | 59 | 55
KUMAR CHAKRABORTI ALOK | 2026-09-21 | PATHAK AHELI | 2026-09-19 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141892 | Closed | PATHAK AHELI | 2026-09-19 | TT cycle time observed to be 130 minutes | 6.7 | Additional Observations | 1775 | BENGALURU TERMINAL | TT cylce time should be brought to 60 mins | SOD | Marketing | SWZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014499ACN-2026-06-4000141892 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141892 | 2026-09-24 17:00 | 25.0455 | 385 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141892 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141892 | AUD-2026-06-2000014499ACN-2026-06-4000141892 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 55
KUMAR CHAKRABORTI ALOK | 2026-09-21 | PATHAK AHELI | 2026-09-19 | Complied | BENGALURU-TML_FY26-Q1_SR.MGNT INSPECTION | 2026-06-24 18:00 | AUD-2026-06-2000014499 | 2026-06-24 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141893 | Closed | PATHAK AHELI | 2026-09-19 | 4 TT's observed parked within premises involving ITDG action (KA 01 AL 2468, KA 01 AQ 3724, WB 11 E 8498, AP 39 TE 5776) | 6.8 | Additional Observations | 1775 | BENGALURU TERMINAL | Timley action to be initiated. | SOD | Marketing | SWZ | 2026-07-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-06-2000014499ACN-2026-06-4000141893 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014499ACN-2026-06-4000141893 | 2026-09-24 17:00 | 25.0455 | 385 | >20 | AUD-2026-06-2000014499 - ACN-2026-06-4000141893 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000014499ACN-2026-06-4000141893 | AUD-2026-06-2000014499ACN-2026-06-4000141893 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 55
DANTHAMALLA SATISH KUMAR | 2026-09-21 | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Ethanol testing carried out strictly as per the prescribed procedure without any deviations. | AUDIT UPLOAD IN SAP | 2026-08-20 11:30 | AUD-2026-09-2000017202 | 2026-08-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150586 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-09-16 | Ethanol testing shall be carried out strictly as per the prescribed procedure without any deviations. | 6 |  | 1940 | KADAPA DEPOT | Ethanol testing shall be carried out strictly as per the prescribed procedure without any deviations. | SOD | Marketing | SCR | 2026-08-21 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-21 | AUD-2026-09-2000017202ACN-2026-09-4000150586 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017202ACN-2026-09-4000150586 | 2026-08-20 11:30 | 60.2747 | 385 | >20 | AUD-2026-09-2000017202 - ACN-2026-09-4000150586 | 532 | 8294 | 21 | 8294 | 59 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017202ACN-2026-09-4000150586 | AUD-2026-09-2000017202ACN-2026-09-4000150586 | 21 | 21 | 27 | 80 | 0 | 0 | 51 | 55
|  | JANA SUDEEP | 2026-09-22 | PO placed for medical check-up camp for TT crews vide PO No. 5200133095. Colour Blindness will be checked for all drivers in the planned healthcheckup camp planned on 24-25 Sep'26. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147383 | Completed | SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | Currently facility not avaialble . | 2.16 | Eyesight / colour-blindness awareness checked | 1146 | MEERUT DEPOT | During the medical check-up camp for drivers, colour blindness screening should be included as one of the mandatory examination parameters | SOD | Marketing | NUZ | 2026-08-30 | POOR COMMUNICATION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016227ACN-2026-08-4000147383 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147383 | 2026-09-25 19:00 | 23.9622 | 363 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147383 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016227ACN-2026-08-4000147383 |  | AUD-2026-08-2000016227ACN-2026-08-4000147383 | 21 |  | 27 | 80 | 0 | 0 | 52
KOSHLENDRA SINGH YADAV | 2026-09-22 | SINGH YASHDEEP | 2026-08-10 |  | LOCATION VISIT-SANGRUR_27-29.05.26 | 2026-05-29 | AUD-2026-07-2000016451 | 2026-05-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146511 | Closed |  |  | Adequate foam invetory is available for both AFFF & ARAFFF 1) ARAFFF SOP to be provided 2) Extra cable & pole from foam shed is to be removed. 3) Cross over to be provided in foam shed | 2.9 | Foam inventory verified | 1180 | SANGRUR DEPOT | Corrective action to be taken. | SOD | Marketing | NFZ | 2026-06-15 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-15 | AUD-2026-07-2000016451ACN-2026-07-4000146511 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016451ACN-2026-07-4000146511 | 2026-07-17 | 94.7538 | 386 | >20 | AUD-2026-07-2000016451 - ACN-2026-07-4000146511 | 532 | 8294 | 21 | 8294 | 126 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016451ACN-2026-07-4000146511 | AUD-2026-07-2000016451ACN-2026-07-4000146511 | 21 | 21 | 27 | 80 | 0 | 0 | 41 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | RFD 1008226 initiated by location. Bid published in MSTC portal for auctioning identified scrap materials. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147381 | Closed | JANA SUDEEP | 2026-09-22 | Stock loss , opex, cycle time, project closure, solar generation, RFDs to be monitored. | 1.8 | Improvement plans discussed | 1146 | MEERUT DEPOT | RFD to be initiate and esnure disposal. | SOD | Marketing | NUZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147381 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147381 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147381 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147381 | AUD-2026-08-2000016227ACN-2026-08-4000147381 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Location regullary follow up with AOT, by raising tickets and sending mail. OT service enginer provide report for all hardware issues in mail. HQO intervention required for resolution with permenent solution from AOT. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147384 | Closed | JANA SUDEEP | 2026-09-22 | Review of VTS deviation done for last 3 months. Locaction is taking action on VTS deviation basis mail received and taking action accordingly. Location has aware about limitation of VTS system and provide input to improve. | 3.3 | VTS deviations reviewed | 1146 | MEERUT DEPOT | Location to take up with AOT and HQO for VTS related issues | SOD | Marketing | NUZ | 2026-12-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147384 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147384 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147384 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147384 | AUD-2026-08-2000016227ACN-2026-08-4000147384 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Railway has confirm to share details of SCRAP disposal with OMC once auction in place. Railway Items are disposed to railway approved vendor only. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147385 | Closed | JANA SUDEEP | 2026-09-22 | For railway siding revamping project , Fix cost of scrap given by railway as per their measurement | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1146 | MEERUT DEPOT | The location shall take up the matter with the Railways for adjustment of the actual scrap value (as per MSTC invoice) during the execution of the Major Track Maintenance Project. | SOD | Marketing | NUZ | 2027-03-31 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2027-03-31 | AUD-2026-08-2000016227ACN-2026-08-4000147385 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147385 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147385 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147385 | AUD-2026-08-2000016227ACN-2026-08-4000147385 | 21 | 21 | 27 | 80 | 0 | 0 | 83 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Location have space constrain for new tankage, however as per discussion with zonal team, location can convert MS tank to Gasohol tanks and can receive Gasohole through rake. 50 m additional pipe line of 18" along with other pipeline fittings will be required forconverting MS tank into Gasohol tank. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147386 | Closed | JANA SUDEEP | 2026-09-22 | The location shall explore the feasibility of E25 unloading facility, along with the required conversion of MS and Ethanol tanks toGasohol service, using spare line of SKO unloading from Siding to pump house and new line from pump house to tank connection. In this case Depot have to convert all ethanol and Ms tank to Gasohol storage tanks. | 6.1 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147386 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147386 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147386 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147386 | AUD-2026-08-2000016227ACN-2026-08-4000147386 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Location sending regular mail to Leagal team for progress of case. Last mail sent: 19/08/26. (Previous mails: 4/7/26). Status from lawyer appointed by HPCL: "In writ petition no. 30081 of 2024, HPCL v State of U.P., the matter was last listed before the Hon'ble court on 18.02.2026. till date no counter affidavit has been filed on behalf of the Meerut Development authority or the State.The interim order dated 01.10.2024 is still operative." | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147389 | Closed | JANA SUDEEP | 2026-09-22 | The location shall coordinate with the Legal team and closely follow up on the MDA maintenance charges case in Alhabad High court for next hearing | 6.4 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-12-31 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147389 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147389 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147389 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147389 | AUD-2026-08-2000016227ACN-2026-08-4000147389 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Locaiton have conduted study for PLT receipt from pipeline and found that location required : additional pipe line of 220 m for each product, along with all fittings and valve, MFM for both products and integration required in TAS for receipt. Necessary integration with TAS to be performed. Also clearance from IOC required, As per IOC-Meerut, IOCL dont have provision of pumping in pipe line. also their tankage is insufficient to thier storage and they have coverage of 3 days only for thier requirement. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147390 | Closed | JANA SUDEEP | 2026-09-22 | The location shall explore the feasibility of receiving PLT from IOCL Meerut. If agreed by IOCL upon this proposal, a draft proposal shall be prepared in line with HQO approval | 6.5 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016227ACN-2026-08-4000147390 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147390 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147390 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147390 | AUD-2026-08-2000016227ACN-2026-08-4000147390 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | EM Lock replacement in progress: 82 locks changed till 31/08/26. Some new locks found not fit for use, location returned those locks to OEM Sterna Securities Pvt Ltd. (Failed in visual check). | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147391 | Closed | JANA SUDEEP | 2026-09-22 | A show cause notice has been issued to M/s Sterna regarding EM Lock tampering, and the same has been shared with the Zone. The location shall also prepare and circulate a brief note covering the issues related to EM Locks and the VTS system. Locaiton has already inform HQO through NCZ. | 6.6 | Additional Observations | 1146 | MEERUT DEPOT | Location to take up with OEM and transporter for replacement of lock with E-tag. | SOD | Marketing | NUZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147391 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147391 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147391 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147391 | AUD-2026-08-2000016227ACN-2026-08-4000147391 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Clear pathway available from RAF side and one of the in-gate of depot is dedicated for entry of emergency vehicle. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147392 | Closed | JANA SUDEEP | 2026-09-22 | The entrance area of depot to be handled so as trucks reporting /emergency vehicle/fire tender can report to depot with out any issue. | 6.8 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016227ACN-2026-08-4000147392 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147392 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147392 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147392 | AUD-2026-08-2000016227ACN-2026-08-4000147392 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Average contract demand for each month is reaching 80% of max demand. Location crossed maximum deamand only for one time in last 12months. Hence no change required in max contract demand. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147393 | Closed | JANA SUDEEP | 2026-09-22 | Location to review maximum contract demand and if required corrective action to be taken | 6.10 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016227ACN-2026-08-4000147393 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147393 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147393 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147393 | AUD-2026-08-2000016227ACN-2026-08-4000147393 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Location following-up with HQO HSE since 25.03.2025 for Board approval of ERDMP document. Approval not received from HQO HSE.Location sending regular Reminder to HSSE-HQO for the same. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147382 | Closed | JANA SUDEEP | 2026-09-22 | Done ,Location shared ERDMP with HQO however board approval copy of ERDMP not available with location . | 2.5 | Emergency response preparedness reviewed | 1146 | MEERUT DEPOT | The location shall take up the matter with HQO for obtaining Board approval of the ERDMP. | SOD | Marketing | NUZ | 2026-08-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-31 | AUD-2026-08-2000016227ACN-2026-08-4000147382 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147382 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147382 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147382 | AUD-2026-08-2000016227ACN-2026-08-4000147382 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | JANA SUDEEP | 2026-09-22 | Both IRR pending with Internal audit team: IR 2025006841 is resubmitted. All required document shared, action required from internal audit team. : current status: "Location Closure Recommended" IR 2025006823 : Current status appear as "Closure request checked & verified" | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147380 | Closed | SARANG MEHULKUMAR BHUPENDRABHAI | 2026-09-22 | 2 no of IRRs are pending for clouser. | 1.3 | Pending issues reviewed | 1146 | MEERUT DEPOT | Location to take up for clouser of pending IRR at the earliest | SOD | Marketing | NUZ | 2026-12-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147380 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147380 | 2026-09-25 19:00 | 23.9622 | 386 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147380 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016227ACN-2026-08-4000147380 | AUD-2026-08-2000016227ACN-2026-08-4000147380 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 56
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153017 | Open |  |  | 1. ESD 14 actuated. It worked well. 2. GI canopy to be made for MOV/ ROSOV for protection from rain. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1281 | AJMER TERMINAL | Bharatpur IRD is having ample qty of GI box inside their TWPH. This is presently not in use. Ajmer Tml may take some qty of GI boxes to cover ROSOV/MOV/DBBV etc. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153017 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153017 | 2026-09-09 17:45 | 40.0143 | 425 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153017 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153017 |  | AUD-2026-09-2000017605ACN-2026-09-4000153017 | 21 |  | 27 | 80 | 0 | 0 | 61
HARINIVAS S | 2026-06-12 | JOSVIN SUNNY | 2026-06-12 | not pretaining to location | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122296 | Closed | JOSVIN SUNNY | 2026-06-12 | Railway payment to IOC pending, TT allotment of 35 TTs from CPO. | 1.5 | HQO / Zonal support required identified | 1892 | KOZHIKODE DEPOT | Funds for railway payment, TT allotment from CPO. | SOD | Marketing | CZR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-02-28 | AUD-2026-02-2000010911ACN-2026-03-4000122296 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122296 | 2026-09-17 16:00 | 32.0872 | 284 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122296 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000010911ACN-2026-03-4000122296 | AUD-2026-02-2000010911ACN-2026-03-4000122296 | 21 | 21 | 26 | 80 | 2 | -4 | 26 | 41
[5 empty] | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151073 | Open |  |  | a. Carried out with all officers and LIC. New officer joined was greeted by me. b. There are 4 contract staffs working inside Admin Building. Two at planning room. Two are working as office boy. Apart from these 4 contract staffs, there is one cook who takes care of meal/tea etc. c. Driver of emergency vehicle can be utilised to maintaiun register in security gate (if he is educated). Thisis my suggestion. d. Jobs related to electrical, maintenance, housekeeping which are done periodically in some fixed intervals (weekly, fortnightly, monthly, quarterly etc) are to be listed by officer. the same to be shared with zone. Convert these jobs on manpower basis. A separate PO to be placed for getting these periodical jobs on job basis instead of manpower basis. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1242 | JAIPUR TERMINAL | 1. It is advised to remove one contract staff from office. One contract staff should be increased in housekeeping job. 2. Security guard is presently maintaining register and fill check list in system. Job of security guard is to carry out checks and do the patrolling in field. Updation of check list in computer/register should be carried out through contract staff in stead of DGR security gaurd. This will save cost. 3. We are not utilising 5 maintennace staffs, 4 electricians and 5 housekeeping staffs to their potential. There is no preventive maintenance schedule for getting the jobs from these working personnel. Currently, most of the jobs areof breakdown nature. Pls prepare schedule of jobs which are preventive in nature. Get the same signed by contractor and get the jobdone as per PMS. 4. Manpower basis jobs to be converted on job basis PO as mentioned in my observation | SOD | Marketing | NWF | [6 empty] | 2026-10-31 | AUD-2026-09-2000016770ACN-2026-09-4000151073 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151073 | 2026-09-30 | 19.7538 |  |  | AUD-2026-09-2000016770 - ACN-2026-09-4000151073 | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 |  | AUD-2026-09-2000016770ACN-2026-09-4000151073 |  | AUD-2026-09-2000016770ACN-2026-09-4000151073 |  |  | 27 | 80 | 0 | 0
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153022 | Open |  |  | 1. Secondary route creation is to be done in few cases like Kekri byepass. Pls ensure to get it done by SOs. 2. There were blocking of 57 Tts in June 26, 29 blocking in July 26 and 34 blocking in Aug 26. Mr. Ankur Khandelwal has to work on it. For any assistance, he should take support of Zonal officer including undersign. No. of blocking should be brought down below 10 TTs per month. 3. Identify 5 most suspected multiple loaded TT stoppage point. Issue letter to transporters/DCT. Take explanation in writing. Talk to TTcrew/transport manager. If any suspicion observed, pls inform to Security advisor and Police in writing with a copy to Zone. This needs to be done every month. | 3.3 | VTS deviations reviewed | 1281 | AJMER TERMINAL | 1. Secondary route creation is to be done in few cases like Kekri byepass, Pratappura byepass. Pls ensure to get it done by SOs. 2. There were blocking of 57 Tts in June 26, 29 blocking in July 26 and 34 blocking in Aug 26. Mr. Ankur Khandelwal has to work on it. For any assistance, he should take support of Zonal officer including undersign. No. of blocking should be brought down below 10 TTs per month. 3. Identify 5 most suspected multiple loaded TT stoppage point. Issue letter to transporters/DCT. Take explanation inwriting. Talk to TT crew/transport manager. If any suspicion observed, pls inform to Security advisor and Police in writing with a copy to Zone. This needs to be done every month. Share the findings with Zone every month. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153022 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153022 | 2026-09-09 17:45 | 40.0143 | 425 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153022 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153022 |  | AUD-2026-09-2000017605ACN-2026-09-4000153022 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153023 | Open |  |  | 1. Pls ensure payment for abused locks to M/s Sterna. Pls make file note for making payment from HPCL end. There are 34 abused locks for which M/s Sterna has asked payment. 2. It is also advised to check locks through intelligent key and submit check report every fortnight. | 3.5 | EM Lock SOP compliance verified | 1281 | AJMER TERMINAL | 1. Pls ensure payment for abused locks to M/s Sterna. Pls make file note for making payment from HPCL end. There are 34 abused locks for which M/s Sterna has asked payment. 2. It is also advised to check locks through intelligent key and submit check report every month. Locks of TT , which were identified as suspected by intelligent key, that particular TT should be checked closely for any ITDG violations (route deviation, stoppage violation, stopping at multiple loaded TT stopping points). Letter should be issued. Pls send locks of these Tts to 3rd party for checking. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017605ACN-2026-09-4000153023 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153023 | 2026-09-09 17:45 | 40.0143 | 455 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153023 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153023 |  | AUD-2026-09-2000017605ACN-2026-09-4000153023 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153025 | Open |  |  | TF-9 (Slope tank) TAS: 127.4/9.3/36 Manual: 127.1/9.1/36 | 3.7 | Inventory physical dip of minimum two tanks taken | 1281 | AJMER TERMINAL | Slop tank is having product similar to MS. The density is higher (almost 790). Product is clear. Location was advised to submit sample of this tank to Lab and get blending %. Pls mix the product with MS (after taking clearance from Lab) and liquidate the product.Pls share monthly progress report | SOD | Marketing | NWF | 2027-03-31 |  | 10 |  | S2 | F5 | 2027-03-31 | AUD-2026-09-2000017605ACN-2026-09-4000153025 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153025 | 2026-09-09 17:45 | 40.0143 | 576 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153025 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153025 |  | AUD-2026-09-2000017605ACN-2026-09-4000153025 | 21 |  | 27 | 80 | 0 | 0 | 83
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153027 | Open |  |  | a. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise. b. Location should also carry out cycle count of material on monthly basis. c. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informed toZone. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. d. There is loss of 28 kl in ethanol as on 31.08.2026. This is -0.1% against target of 0%. Pls check my email dt 25.08.2026 on ethanol loss control. Location has been implementing most of the suggestions given. Location should keep close watch on ethanol loss. | 3.9 | Abnormal variations / unused assets reviewed | 1281 | AJMER TERMINAL | a. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise. b. Location should also carry out cycle count of material on monthly basis. c. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informed toZone. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. d. There is loss of 28 kl in ethanol as on 31.08.2026. This is -0.1% against target of 0%. Pls check my email dt 25.08.2026 on ethanol loss control. Location has been implementing most of the suggestions given. Location should keep close watch on ethanol loss. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017605ACN-2026-09-4000153027 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153027 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153027 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153027 |  | AUD-2026-09-2000017605ACN-2026-09-4000153027 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153034 | Open |  |  | 1. Pls share details of all spare cable with rating and length of cable. 2. Cable dressing is required just outside S&D room. 3. MCC room: pls mention fuse rating and relay setting on the face of panel. 4. There should be one register at TT gantry. This register should have entries of all issues at TT gantry. It may be related to maintenance, electrical issue, operational issue. This may be filled by contract staff in their language. TAS officer and M&I officer to review this register on weekly basis and LIC to reviewthis register on monthly basis for compliance of job identified by gantry workman/officer 5. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. 6. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1281 | AJMER TERMINAL | 1. Pls share details of all spare cable with rating and length of cable. 2. Cable dressing is required just outside S&D room. 3. MCC room: pls mention fuse rating and relay setting on the face of panel. 4. There should be one register at TT gantry. This register should have entries of all issues at TT gantry. It may be related to maintenance, electrical issue, operational issue. This may be filled by contract staff in their language. TAS officer and M&I officer to review this register on weekly basis and LIC to reviewthis register on monthly basis for compliance of job identified by gantry workman/officer 5. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. 6. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017605ACN-2026-09-4000153034 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153034 | 2026-09-09 17:45 | 40.0143 | 455 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153034 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153034 |  | AUD-2026-09-2000017605ACN-2026-09-4000153034 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153035 | Open |  |  | 1. Painting of dyke wall is suggested. Pls float tender for the same. | 4.2 | Maintenance activities reviewed | 1281 | AJMER TERMINAL | 1. Painting of dyke wall is suggested. Pls float tender for the same. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017605ACN-2026-09-4000153035 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153035 | 2026-09-09 17:45 | 40.0143 | 455 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153035 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153035 |  | AUD-2026-09-2000017605ACN-2026-09-4000153035 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153036 | Open |  |  | 1. Bay 4 conversion is pending for a long time. Pls complete the project as early as possible. 2. There are 2 nos. of 3 inch MFM and one no. of 2 MFM. Pls check for its working codition. If not, pls get it repaired by OEM. 3. Installation of 400 KVA DG | 4.3 | Project progress reviewed | 1281 | AJMER TERMINAL | 1. Bay 4 conversion is pending for a long time. Pls complete the project as early as possible. 2. There are 2 nos. of 3 inch MFM and one no. of 2 MFM. Pls check for its working codition. If not, pls get it repaired by OEM. 3. Location to take up with CPO for early placement of PO and complete the job. | SOD | Marketing | NWF | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017605ACN-2026-09-4000153036 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153036 | 2026-09-09 17:45 | 40.0143 | 486 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153036 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153036 |  | AUD-2026-09-2000017605ACN-2026-09-4000153036 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153038 | Open |  |  | Following RTGPs were found open: 1. 11281-R-016544 dt 09.07.2022 for Dome Camera 2. 11281-R-024085 dt 29.05.2025, Mech. Seal There are pending RTGPs of very long period. Location is also supposed to carry out confirm dispatch after taking print of RTGP, otherwise, same will not show under open RTGP. | 6.2 | RTGP monitoring | 1281 | AJMER TERMINAL | Old RTGP to be closed. Confirm dispatch to be done after print of RTGP. | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153038 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153038 | 2026-09-09 17:45 | 40.0143 | 425 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153038 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153038 |  | AUD-2026-09-2000017605ACN-2026-09-4000153038 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153039 | Open |  |  | It is advised to monitor diesel consumption in fire engine and DG. Location can maintain monthly record as per the followings: i)Opening physical inv of HSD in DG tanks; ii) HSD given to DG tank in that month: iii) No. of hrs run by individual DG in zero load, no. of hrs run by individual DG in full load iv) Diesel consumption per hr as communicated by OEM for individual DG in no load and full load respectively. v) HSD consumed theoritically vi) Closing book stock of HSd in DG tank vii) Physical closing stock of HSD in DG tank | 6.3 | Additive stock monitoring | 1281 | AJMER TERMINAL | It is advised to monitor diesel consumption in fire engine and DG. Location can maintain monthly record as per the followings: i)Opening physical inv of HSD in DG tanks; ii) HSD given to DG tank in that month: iii) No. of hrs run by individual DG in zero load, no. of hrs run by individual DG in full load iv) Diesel consumption per hr as communicated by OEM for individual DG in no load and full load respectively. v) HSD consumed theoritically vi) Closing book stock of HSd in DG tank vii) Physical closing stock of HSD in DG tank | SOD | Marketing | NWF | 2026-10-15 |  | 10 |  | S2 | F5 | 2026-10-15 | AUD-2026-09-2000017605ACN-2026-09-4000153039 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153039 | 2026-09-09 17:45 | 40.0143 | 409 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153039 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153039 |  | AUD-2026-09-2000017605ACN-2026-09-4000153039 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153040 | Open |  |  | To be implemented for all toll plaza. | 6.4 | Discounted toll | 1281 | AJMER TERMINAL | To be implemented for all toll plaza. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017605ACN-2026-09-4000153040 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153040 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153040 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153040 |  | AUD-2026-09-2000017605ACN-2026-09-4000153040 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153041 | Open |  |  | Old Lubes are required to be liquidated | 6.5 | Liquidation of slow moving Lube | 1281 | AJMER TERMINAL | Old Lubes are required to be liquidated | SOD | Marketing | NWF | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017605ACN-2026-09-4000153041 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153041 | 2026-09-09 17:45 | 40.0143 | 486 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153041 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017605ACN-2026-09-4000153041 |  | AUD-2026-09-2000017605ACN-2026-09-4000153041 | 21 |  | 27 | 80 | 0 | 0 | 70
MANDAL PRATAPKUMAR | 2026-09-22 | NILABH | 2026-09-22 | Tree branches trimed through the boundary wall near the TT parking area. | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150280 | Closed | NILABH | 2026-09-22 | Tree branches were observed overhanging into the premises through the boundary wall near the TT parking area. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1305 | KANPUR TERMINAL | Tree branches to be suitably trimmed to maintain clear visibility near boundary wall to mitigate potential security risks. | SOD | Marketing | NCR | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150280 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150280 | 2026-08-26 17:00 | 54.0455 | 386 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150280 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017157ACN-2026-08-4000150280 | AUD-2026-08-2000017157ACN-2026-08-4000150280 | 21 | 21 | 27 | 80 | 4 | 4 | 57 | 56
MANDAL PRATAPKUMAR | 2026-09-22 | NILABH | 2026-09-22 | vegetation trimmed/cleared along the peripheral roads and boundary wall. | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150275 | Closed | NILABH | 2026-09-22 | Overgrown vegetation was observed across the premises during the ongoing rainy season particularly along the peripheral roads adjacent to the boundary wall. The excessive vegetation was obstructing clear visibility of the peripheral areas. | 3.16 | Earth pits / boundary / vegetation control checked | 1305 | KANPUR TERMINAL | The overgrown vegetation may be suitably trimmed/cleared on a regular basis to maintain clear visibility along the peripheral roadsand boundary wall. | SOD | Marketing | NCR | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150275 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150275 | 2026-08-26 17:00 | 54.0455 | 386 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150275 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017157ACN-2026-08-4000150275 | AUD-2026-08-2000017157ACN-2026-08-4000150275 | 21 | 21 | 27 | 80 | 4 | 4 | 57 | 56
SUDHIR KUMAR | 2026-09-22 | SHETTY ANURANJAN | 2026-09-22 | Processing and repeated in next audit | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125385 | Closed | SHETTY ANURANJAN | 2026-09-22 | Following action points are pending since 02.12.2025. 1. Fencing utilization in TT parking area. complied. 2. Guidelines for TTcrew in case of emergency. SOP board is to be displayed at prominent place in TT gantry. 3. Sewage treatment Plant is not in use. 4. Gravel and grass with designated path for crossing is to be maintained in one bay as an experiment. 5. Double Fire Hydrant between ETP and Hazardous Shed. 6. One of the ESD from gantry to be shifted to ETP area. 3 ESDs are sufficient in gantry. 7. All SOPboards to be displayed in Hindi and not English for workers' understanding. 8. ESD 1 (E1) to be shifted to near tank 4 9. Commuication issue of 12 MOV's in TAS. | 1.4 | Earlier action points status checked | 1242 | JAIPUR TERMINAL | Time bound action plan is to be maintained | SOD | Marketing | NWF | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011022ACN-2026-03-4000125385 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125385 | 2026-09-30 | 19.7538 | 386 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125385 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125385 | AUD-2026-03-2000011022ACN-2026-03-4000125385 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 56
SUDHIR KUMAR | 2026-09-22 | SHETTY ANURANJAN | 2026-09-22 | PO placed and Fire Engine taken up for overhauling | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125402 | Closed | SHETTY ANURANJAN | 2026-09-22 | Fire engine no. 5 is giving unusual sound. Though, it is in running condition, it needs to be repaired urgently. | 6.1 | Fire engine | 1242 | JAIPUR TERMINAL | Pls ensure timely action | SOD | Marketing | NWF | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 12 | ASSET INTEGRITY | S3 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125402 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125402 | 2026-09-30 | 19.7538 | 386 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125402 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125402 | AUD-2026-03-2000011022ACN-2026-03-4000125402 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 56
SUDHIR KUMAR | 2026-09-22 | SHETTY ANURANJAN | 2026-09-22 | Processing and rpeeated in next audit | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125403 | Closed | SHETTY ANURANJAN | 2026-09-22 | 10 MOVs out of total 51 MOVs are not communicating. All ROSOVs are communicating. HSD pump and MS pump, one each, are in local. Allpumps should be in remote mode. | 6.3 | mov repair and communication | 1242 | JAIPUR TERMINAL | MOV to be repaired. Pumps should be kept in remote mode. | SOD | Marketing | NWF | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011022ACN-2026-03-4000125403 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125403 | 2026-09-30 | 19.7538 | 386 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125403 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125403 | AUD-2026-03-2000011022ACN-2026-03-4000125403 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 56
SUDHIR KUMAR | 2026-09-22 | SHETTY ANURANJAN | 2026-09-22 | Lubes have been verified by Jaipur Lubes RO and advised that the same has to be disposed, follow ups are being taken up for disposal with Jaipur Lubes RO | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125410 | Closed | SHETTY ANURANJAN | 2026-09-22 | Old Lubes are required to be liquidated | 6.11 | Liquidation of slow moving Lube | 1242 | JAIPUR TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is already done by Mr. darpan. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-04-30 | POOR COMMUNICATION | 8 | ENVIRONMENTAL | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011022ACN-2026-03-4000125410 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125410 | 2026-09-30 | 19.7538 | 386 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125410 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011022ACN-2026-03-4000125410 | AUD-2026-03-2000011022ACN-2026-03-4000125410 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 56
NIDAMARTHI NAGA KIRAN | 2026-09-22 | SATYENDRA CHOURASIA | 2026-09-17 | Bag checking are now being carried out before DFMD. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147048 | Closed | SATYENDRA CHOURASIA | 2026-09-17 | Bag checking shall be carried out before DFMD. | 6.2 |  | 1919 | SECUNDERABAD TERMINAL | Bag checking shall be carried out before DFMD. | SOD | Marketing | SCR | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147048 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147048 | 2026-08-06 19:00 | 73.9622 | 386 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147048 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147048 | AUD-2026-08-2000016364ACN-2026-08-4000147048 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Grss cutting and housekeeping is being done. Because of frequent rain, grass cutting is being done regularly to prevent the growth. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150221 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Earthpit of 75KVA DG was checked and following readings found. Electrode - 1.24 ohm Grid - 0.28 ohm, Excessive vegetation has grown around tanks farm area and pump house. Vegetation along boundary wall also found excessie. |  | Earth pits / boundary / vegetation control checked | 1308 | SITARGANJ DEPOT | Location to ensure that grass cutting is done on regular basis and no excessive vegetation growth is observed inside depot premises. | SOD | Marketing | NUZ | 2026-09-10 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-10 | AUD-2026-08-2000016859ACN-2026-08-4000150221 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150221 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150221 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150221 | AUD-2026-08-2000016859ACN-2026-08-4000150221 | 21 | 21 | 27 | 80 | 0 | 0 | 54 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | FE, Hydrant line and safety equipments are maintained and AMC carried out. Working of FE checked and is as per logic in FDS. (For total no. of fire engine running at a time and fail to start logic for standby engine) | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149847 | Closed | CHOUDHARY JAYESH | 2026-09-22 | To focus on the individual area along with stringet monitoring and applicable clauses, over and above depot regular duties. | 1.6 | Expectations clearly communicated to officers | 1308 | SITARGANJ DEPOT | HSE to focus on important issues such as FE, Hydrant line and safety equipments - regular maintenance, AMC, and working as per logic. | SOD | Marketing | NUZ | 2026-09-07 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000149847 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149847 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149847 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000149847 | AUD-2026-08-2000016859ACN-2026-08-4000149847 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | "1. FE logic checked for running of Main and standby engine. As per FDS, at any point of time, the total no. fire engine that can run is the total no. of main fire engine designated. Also, in case of fail to start of main fire engine, the standby will run. The same is tested in field and complied. 2. Location is in discussion with Roorkee and concerned sales officer for necessry realignment." | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000149848 | Closed | CHOUDHARY JAYESH | 2026-09-22 | 1. Improvement in Fire and safety equipments 2. Catering of additional outlets from location. | 1.8 | Improvement plans discussed | 1308 | SITARGANJ DEPOT | 1. FEs to work as per logic and FDS - to take up with TAS vendor and to ensure it. 2. Exercise is needed to create ullage at Bareily. If possible after consultation with IMM to implement. | SOD | Marketing | NUZ | 2026-09-07 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000149848 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000149848 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000149848 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000149848 | AUD-2026-08-2000016859ACN-2026-08-4000149848 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Security has been trained for notifying alerts to all. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150207 | Closed | CHOUDHARY JAYESH | 2026-09-22 | HCD test carried out at Pump House for 20% hydrocarbon film. Indication and hooter automatically came at controll room. Alarm message received from Planning. No alert message received from security | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1308 | SITARGANJ DEPOT | HCD alarms to be notified to all depot employees by security / planning office / control room. Presently, security is not notifyingthe alerts to all. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150207 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150207 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150207 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150207 | AUD-2026-08-2000016859ACN-2026-08-4000150207 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Foam generation checked and working satisfactorily. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150208 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Officer operated monitors near gantry. Foam application was not adequate. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1308 | SITARGANJ DEPOT | Foam generation to be checked and to be ensured for 3% foam generation. | SOD | Marketing | NUZ | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-08-2000016859ACN-2026-08-4000150208 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150208 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150208 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150208 | AUD-2026-08-2000016859ACN-2026-08-4000150208 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | TT crews are carrying file having all the documents and being checked by security. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESSTT C | ACN-2026-08-4000150209 | Closed | CHOUDHARY JAYESH | 2026-09-22 | TT UP85CT6026 upon inspection, was not having hazardous endorsement availablewith him. The copy of same was available with security. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1308 | SITARGANJ DEPOT | Location to ensure that all the TT crews are carrying file wherein all the truck and crew documets are made available. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150209 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150209 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150209 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150209 | AUD-2026-08-2000016859ACN-2026-08-4000150209 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Fire extenguisher of trucks are regularly carried out and ensuring timely servicing and having certificate/sticker. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150210 | Closed | CHOUDHARY JAYESH | 2026-09-22 | TT crew of TT UP78GN0294 operated the extenguisher at gantry. | 2.14 | TT crew fire extinguisher usage checked | 1308 | SITARGANJ DEPOT | Location to ensure fire exteguishers of trucks are monthly serviced and certificate is available with them. | SOD | Marketing | NUZ | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-08-2000016859ACN-2026-08-4000150210 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150210 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150210 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150210 | AUD-2026-08-2000016859ACN-2026-08-4000150210 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | TT crews are carrying file having all the documents and being checked by security. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150211 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Dicussed at TT gantry with drivers. TREM card was not availble with TT UP78GN0294. | 2.15 | TT crew roadside emergency procedures checked | 1308 | SITARGANJ DEPOT | Location to ensure that all the TT crews are carrying file wherein all the truck and crew documets are made available. Security to check and ensure nil deviation. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150211 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150211 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150211 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150211 | AUD-2026-08-2000016859ACN-2026-08-4000150211 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Security guard is checking the documents and IDs af TT/ TT Crew. The TT crew are wearing ID cards. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150201 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Doc of TT UP85CT6026 was checked and it was found that necessary documents were not available with the crew. Also ID card/pass was not available at driver. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1308 | SITARGANJ DEPOT | Location to ensure security guards at main gate checks all the incoming trucks for all documents and IDs. | SOD | Marketing | NUZ | 2026-08-28 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-28 | AUD-2026-08-2000016859ACN-2026-08-4000150201 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150201 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150201 | 532 | 8294 | 21 | 8294 | 52 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150201 | AUD-2026-08-2000016859ACN-2026-08-4000150201 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Security imparted traininig for emergency preparedness. Emergency contact list displayed at Security cabin. Emergency contacts are being communicated in mock drills. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150202 | Closed | CHOUDHARY JAYESH | 2026-09-22 | During fire drill, general security alertness and prepardness reviewed. | 2.5 | Emergency response preparedness reviewed | 1308 | SITARGANJ DEPOT | Training to be imparted to security for emergency preparedness. Security to inform the all important persons as per list available with security. No. list to be kept displayed at Security. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150202 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150202 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150202 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150202 | AUD-2026-08-2000016859ACN-2026-08-4000150202 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | CCTV training imparted for reviewing backup on regular basis. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150203 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Yes functioning. CCTV coverage not available at main gate frisking area. | 2.6 | CCTV functioning checked | 1308 | SITARGANJ DEPOT | CCTV training to be imparted to all officers so that backup can be reviewed on regular basis. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150203 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150203 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150203 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150203 | AUD-2026-08-2000016859ACN-2026-08-4000150203 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Being reviewd and closed regularly. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150204 | Closed | CHOUDHARY JAYESH | 2026-09-22 | VA alerts checked | 2.7 | VA alerts checked / analysed | 1308 | SITARGANJ DEPOT | Regularly to be reviewed and closed. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150204 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150204 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150204 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150204 | AUD-2026-08-2000016859ACN-2026-08-4000150204 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | PR initiated and approved. Being send to CPO for floating tender. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150206 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Foam inventory vs requirement reviewed. 6KL available against 4.75KL requirement. | 2.9 | Foam inventory verified | 1308 | SITARGANJ DEPOT | Location to initiate procurement for replenishment. | SOD | Marketing | NUZ | 2026-09-10 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-10 | AUD-2026-08-2000016859ACN-2026-08-4000150206 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150206 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150206 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150206 | AUD-2026-08-2000016859ACN-2026-08-4000150206 | 21 | 21 | 27 | 80 | 0 | 0 | 54 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Training imparted to security for notifying critical alarms. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150218 | Closed | CHOUDHARY JAYESH | 2026-09-22 | HCD alarm checked. Working fine. However, no message came from securty regarding the same. | 3.12 | Critical alarms checked & corrective actions reviewed | 1308 | SITARGANJ DEPOT | Training to be imparted to security to notify regarding critical alarms in dpot premises. | SOD | Marketing | NUZ | 2026-09-07 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000150218 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150218 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150218 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150218 | AUD-2026-08-2000016859ACN-2026-08-4000150218 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | K factor report is printed and reviewed on daily vasis | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150219 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Dialy K factor report to be generated and printed. | 3.13 | K-factor changes reviewed (if any) | 1308 | SITARGANJ DEPOT | Location to print the K factor report on daily basis and the same to be reviewed on daily basis. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150219 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150219 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150219 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150219 | AUD-2026-08-2000016859ACN-2026-08-4000150219 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Grss cutting and housekeeping is being done. Because of frequent rain, grass cutting is being done regularly to prevent the growth. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150220 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Housekeeping and PPE usage checked. | 3.15 | Housekeeping & PPE usage checked | 1308 | SITARGANJ DEPOT | Location to ensure grass cutting is done and housekeeping is maintained. | SOD | Marketing | NUZ | 2026-09-10 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-10 | AUD-2026-08-2000016859ACN-2026-08-4000150220 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150220 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150220 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150220 | AUD-2026-08-2000016859ACN-2026-08-4000150220 | 21 | 21 | 27 | 80 | 0 | 0 | 54 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | MOC initiated and approved for change of manpower. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150222 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Location has not initiated MOC post joining of new officer. | 3.17 | MOC status reviewed | 1308 | SITARGANJ DEPOT | Location to initiate applicable MOC | SOD | Marketing | NUZ | 2026-08-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-31 | AUD-2026-08-2000016859ACN-2026-08-4000150222 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150222 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150222 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150222 | AUD-2026-08-2000016859ACN-2026-08-4000150222 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | Regular training imparted to TT crew for emergncy response. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-08-4000150224 | Closed | CHOUDHARY JAYESH | 2026-09-22 | Interacted with UP78GN0294 and UK04CC4848. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1308 | SITARGANJ DEPOT | Location to impart training for emergency response prepardness to TT crew. | SOD | Marketing | NUZ | 2026-09-07 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-07 | AUD-2026-08-2000016859ACN-2026-08-4000150224 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150224 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150224 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150224 | AUD-2026-08-2000016859ACN-2026-08-4000150224 | 21 | 21 | 27 | 80 | 0 | 0 | 53 | 56
ADITYA ASHUTOSH | 2026-09-23 | CHOUDHARY JAYESH | 2026-09-22 | TAS MFM readings being reviewed on daily basis by LIC. | SR MANAGEMENT INSPECTION Q2 SITARGANJ | 2026-08-26 17:00 | AUD-2026-08-2000016859 | 2026-08-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150214 | Closed | CHOUDHARY JAYESH | 2026-09-22 | TT dip checked for UP85CT6026. Following variation were observd - 1. Comp. 1 : 0 2. Comp. 2 : 0 3. Comp. 3 : 0 4. Comp. 4 : 0 | 3.2 | Post-loading dip checks verified | 1308 | SITARGANJ DEPOT | For 2 no. of trucks, TAS MFM reading to be reviewed on daily basis. | SOD | Marketing | NUZ | 2026-08-29 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-08-29 | AUD-2026-08-2000016859ACN-2026-08-4000150214 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016859ACN-2026-08-4000150214 | 2026-08-26 17:00 | 54.0455 | 387 | >20 | AUD-2026-08-2000016859 - ACN-2026-08-4000150214 | 532 | 8294 | 21 | 8294 | 51 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016859ACN-2026-08-4000150214 | AUD-2026-08-2000016859ACN-2026-08-4000150214 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
BANTHIYA RITESH DEELIP | 2026-09-23 | PANWAR VIPIN SINGH | 2026-09-21 | Recalibration done for TT on 19th Sep 2026 in presence of W&M. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147912 | Closed | PANWAR VIPIN SINGH | 2026-09-21 | Checked for 3 TT's. Dip Rod variation of 3 mm observed in TT No. MP35 HA 0528. Location is advised to get it verified thru W&M. | 3.2 | Post-loading dip checks verified | 1436 | SAGAR DEPOT | Dip Rod length to be verified thru W&M Dept. | SOD | Marketing | CEN | 2026-08-20 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-20 | AUD-2026-08-2000016370ACN-2026-08-4000147912 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147912 | 2026-08-07 19:00 | 72.9622 | 387 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147912 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016370ACN-2026-08-4000147912 | AUD-2026-08-2000016370ACN-2026-08-4000147912 | 21 | 21 | 27 | 80 | 4 | 2 | 51 | 56
POTHALA VENKATA RAO | 2026-09-23 | M.RAJKUMAR | 2026-09-18 | All the officers had set their KPIs as per the AOP/Metrics provided by HQO and all are working towards for meeting the set KPIs. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000141849 | Closed | M.RAJKUMAR | 2026-09-18 | Performance review was discussed with Officers. Everyone had submitted the G&Ts as per timelines. During discussions, it was emphasised that SOD HQO deliverables like Opex monitoring, MEB Control, MIS Submission, Cycle Time Reduction, QC Index, Auto Reco Performance, Self-Audits, ESA Compliance, HLSA Compliance, Re-validation of all SOP's at location, Improving Tank Turns, Tank Inspection should be the prime focus during the current year. | 1.2 | Performance review conducted | 1856 | COIMBATORE DEPOT | Officers to maintain focus on the metrics | SOD | Marketing | SZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015339ACN-2026-07-4000141849 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000141849 | 2026-08-28 17:00 | 52.0455 | 387 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000141849 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000141849 | AUD-2026-07-2000015339ACN-2026-07-4000141849 | 21 | 21 | 27 | 80 | 0 | 1 | 57 | 56
POTHALA VENKATA RAO | 2026-09-23 | M.RAJKUMAR | 2026-09-18 | Faded Boards replaced and Earth pits date has been changed. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000142961 | Closed | M.RAJKUMAR | 2026-09-18 | Upkeep of Boards | 6.3 | Additional Observations | 1856 | COIMBATORE DEPOT | Faded boards to be replaced and Earth pit stickers to be | SOD | Marketing | SZ | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142961 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142961 | 2026-08-28 17:00 | 52.0455 | 387 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142961 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142961 | AUD-2026-07-2000015339ACN-2026-07-4000142961 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 56
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153176 | Open |  |  | Surprise night inspections are not being conducted at the location. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153176 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153176 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153176 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153176 |  | AUD-2026-09-2000017755ACN-2026-09-4000153176 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153177 | Open |  |  | Location to monitor coastal performance, ensure daily reconcilation and signed sheet along with remarks shall be kept at location. | 1.8 | Improvement plans discussed | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153177 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153177 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153177 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153177 |  | AUD-2026-09-2000017755ACN-2026-09-4000153177 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153178 | Open |  |  | Date of drill: 10.07.2026 Contingency type: Single Full system Shutdown: Yes Location of emergency: 1. Fire in Dry grass from ongoing welding works near TK Nature of emergency: 1. Fire in Dry grass from ongoing welding works near TK Area of improvement: 1.Visitor entering at main gate during the emergency should be instructed to be at Assembly point. 2. Safety checks are to be carried out during emergency also. 3. Level of Emergencies to be demonstrated (from level-I to Level II) at site during the emergencies. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1546 | Mundra Terminal-MDPL | Location being double contingency, double contingency fire scenerio shall be considered. | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153178 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153178 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153178 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153178 |  | AUD-2026-09-2000017755ACN-2026-09-4000153178 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153179 | Open |  |  | Night inspections are not being carried out. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153179 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153179 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153179 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153179 |  | AUD-2026-09-2000017755ACN-2026-09-4000153179 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153180 | Open |  |  | 51 out of 55 cameras are currently operational. Backup is available for 92 days. | 2.6 | CCTV functioning checked | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153180 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153180 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153180 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153180 |  | AUD-2026-09-2000017755ACN-2026-09-4000153180 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153181 | Open |  |  | Water: Required – 16,623 KL; Available – 12,251 KL. MOC taken. | 2.10 | Fire water levels verified | 1546 | Mundra Terminal-MDPL | Location shall replenish water level earliest. | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153181 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153181 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153181 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153181 |  | AUD-2026-09-2000017755ACN-2026-09-4000153181 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153182 | Open |  |  | 1. OPD 03, OPD 05 & OPD 09 was checked. No local alarm/hooter activated for OPD -09. Alarm generated against 28% LEL in OPD 03 was 38% and in OPD 09 was 40%. 2. Dyke-2 dyke valve indicator was working properly. Alarm was generated in both the control room and field. 3. HVLR No. 12 was operated by contract workmen. Performance was satisfactory. HVLR No. 13 could not be operated due power failure. 4. RSFPS for TK13 was checked. Air supply to pneumatic valve was kept close for all modules. Module operated satisfactory post valve opening. Field hooter was not audible. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153182 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153182 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153182 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153182 |  | AUD-2026-09-2000017755ACN-2026-09-4000153182 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153183 | Open |  |  | Location officer were asked to operate the HVLRs, sprinkler system, and MEFG in the field. He demonstrated adequate knowledge of the operating procedures. Nozzle U49 and M55 were found choked for tank TK07 sprinkler. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153183 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153183 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153183 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153183 |  | AUD-2026-09-2000017755ACN-2026-09-4000153183 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153184 | Open |  |  | TK-05 Reference Height: As per record: 1471.4 cm, Actual in field: 1471.4 cm Product Dip: TAS Dip: 1039.1 cm, Physical Dip: 1040 cm Water Dip: TAS: 6.7 cm Physical: 20 cm Temp: TAS: 31.2 Physical: 31 TK-13 Reference Height: As per record: 1475.0 cm, Actual in field: 1475.0 cm Product Dip: TAS Dip: 1071.3 cm, Physical Dip: 1072.1 cm Water Dip: TAS: 14.3 cm,Physical: 14.3 cm Temp: TAS: 29.7 Physical: 29.5 | 3.7 | Inventory physical dip of minimum two tanks taken | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153184 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153184 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153184 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153184 |  | AUD-2026-09-2000017755ACN-2026-09-4000153184 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153185 | Open |  |  | Auto reconciliation is being carried out based on daily end-of-day TAS dips. Signed records with proper reason for abnormal gain/loss is not recorded. | 3.8 | Auto vs Manual reconciliation checked | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153185 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153185 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153185 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153185 |  | AUD-2026-09-2000017755ACN-2026-09-4000153185 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153186 | Open |  |  | Comments are being recorded for abnormal variations. The location has updated surplus/idle assets on the surplus portal. | 3.9 | Abnormal variations / unused assets reviewed | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153186 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153186 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153186 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153186 |  | AUD-2026-09-2000017755ACN-2026-09-4000153186 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153187 | Open |  |  | Review of project done. TK 01 and 04 is required to be commissioned on priority. | 4.3 | Project progress reviewed | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153187 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153187 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153187 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153187 |  | AUD-2026-09-2000017755ACN-2026-09-4000153187 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153188 | Open |  |  | Disposal of MS scrap should be expedited. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153188 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153188 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153188 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153188 |  | AUD-2026-09-2000017755ACN-2026-09-4000153188 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153189 | Open |  |  | Location to check and provide FLP smoke detector in lab sample room | 6.1 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153189 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153189 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153189 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153189 |  | AUD-2026-09-2000017755ACN-2026-09-4000153189 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153190 | Open |  |  | Plaster is coming out from drain wall around admin building same is required to be repaired. | 6.2 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153190 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153190 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153190 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153190 |  | AUD-2026-09-2000017755ACN-2026-09-4000153190 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153191 | Open |  |  | Earthing layout is not updated for foam tank shed | 6.3 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153191 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153191 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153191 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153191 |  | AUD-2026-09-2000017755ACN-2026-09-4000153191 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153192 | Open |  |  | Road is found damaged near TK- 02 | 6.4 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153192 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153192 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153192 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153192 |  | AUD-2026-09-2000017755ACN-2026-09-4000153192 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153193 | Open |  |  | One hose in HB 22 found damaged and leaking. | 6.5 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153193 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153193 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153193 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153193 |  | AUD-2026-09-2000017755ACN-2026-09-4000153193 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153194 | Open |  |  | VA checked for camera no 37 near TK04 for No helmet. No alarm generated for same | 6.6 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153194 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153194 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153194 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153194 |  | AUD-2026-09-2000017755ACN-2026-09-4000153194 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153195 | Open |  |  | Glands size found improper for new actuator installed at location. Gaps were found to be filled with sealing material. | 6.7 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017755ACN-2026-09-4000153195 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153195 | 2026-09-18 | 31.7538 | 424 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153195 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153195 |  | AUD-2026-09-2000017755ACN-2026-09-4000153195 | 21 |  | 27 | 80 | 5 | 5 | 61
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153196 | Open |  |  | PA system near- mother tank foam storage was not able to connect to security main gate. | 6.8 |  | 1546 | Mundra Terminal-MDPL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153196 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153196 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153196 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153196 |  | AUD-2026-09-2000017755ACN-2026-09-4000153196 | 21 |  | 27 | 80 | 5 | 5 | 57
[5 empty] | SR. MANAGEMENT INS MUNDRA Q2 26-27 | 2026-09-18 | AUD-2026-09-2000017755 | 2026-09-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153197 | Open |  |  | Presence of HSD is observed in ETP. | 6.9 |  | 1546 | Mundra Terminal-MDPL | Product shall be recovered from ETP | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017755ACN-2026-09-4000153197 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017755ACN-2026-09-4000153197 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017755 - ACN-2026-09-4000153197 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017755ACN-2026-09-4000153197 |  | AUD-2026-09-2000017755ACN-2026-09-4000153197 | 21 |  | 27 | 80 | 5 | 5 | 57
BINU K | 2026-09-24 | J. NAVANEETH RAMJI | 2026-08-03 | In view of the permanent closure of the installation, the above recommendation is no longer applicable and may kindly be treated as closed | TVL IRD- SR MGMT INSPECTION | 2026-03-19 | AUD-2026-03-2000011226 | 2026-03-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124678 | Closed | J. NAVANEETH RAMJI | 2026-08-03 | Railway revised LLF to be paid for which E proposal submitted for getting approval from Marketing contracts committee | 1.3 | Pending issues reviewed | 1879 | TIRUNELVELI DEPOT | Location to expedite the payment process in consulation with SZ legal, HQO and railways. | SOD | Marketing | SZ | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011226ACN-2026-03-4000124678 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011226ACN-2026-03-4000124678 | 2026-05-08 | 164.7538 | 388 | >20 | AUD-2026-03-2000011226 - ACN-2026-03-4000124678 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011226ACN-2026-03-4000124678 | AUD-2026-03-2000011226ACN-2026-03-4000124678 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 56
|  | CHANGMAI RAHUL | 2026-09-24 | All the TAS items laying in Gantry were shifted to scrapyard and the healthy equipments to designated store room at the admin building. Additionally, planning to segreggate the space of MCC room to make one part as storage area. | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152323 | Completed | CHANGMAI RAHUL | 2026-09-24 | Items are not seggregated and lying everywhere | 6.3 | Proper store Room for extra items | 1708 | DIMAPUR DEPOT | Separate room to be maintained and items are to be stacked properly. | SOD | Marketing | GZR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017853ACN-2026-09-4000152323 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152323 | 2026-09-12 | 37.7538 | 394 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152323 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152323 |  | AUD-2026-09-2000017853ACN-2026-09-4000152323 | 21 |  | 27 | 80 | 7 | 7 | 57
|  | MD KASHIF | 2026-09-24 | Lux level study has been conducted internally by the location and areas not meeting the lux level. Action for restoration are underway. | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125707 | Completed | MD KASHIF | 2026-09-24 | Lux level is low behind TT gantry , secondary roads | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1742 | BOKARO DEPOT | Advised location to carry out Lux study and check the areas having low lux level | SOD | Marketing | PZR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125707 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125707 | 2026-09-19 10:00 | 30.3372 | 241 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125707 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010870ACN-2026-03-4000125707 |  | AUD-2026-03-2000010870ACN-2026-03-4000125707 | 21 |  | 26 | 80 | 1 | 1 | 35
|  | MD KASHIF | 2026-09-24 | Acrylic sheets have been provided as barrier for direct access with the panel door. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-06-4000136342 | Completed | MD KASHIF | 2026-09-24 | Electrical system: MCC: No insulation sheets between panel doors and cable connections with busbars found. | 6.1 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer to immediately place insulation sheets. Location to ensure compliance | SOD | Marketing | PZR | 2026-07-15 | COMPLACENCY OR RISK NORMALIZATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000136342 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000136342 | 2026-09-19 10:00 | 30.3372 | 317 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000136342 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-06-2000012744ACN-2026-06-4000136342 |  | AUD-2026-06-2000012744ACN-2026-06-4000136342 | 21 |  | 27 | 80 | 1 | 1 | 46
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153260 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Location advised to provide cost estimate for the ATF facilities and also advised to closed the DS Tank convesion Project | 1.3 | Pending issues reviewed | 1527 | RAIPUR DEPOT | ATF Facilities to be developed to Depot | SOD | Marketing | ECZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017609ACN-2026-09-4000153260 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153260 | 2026-08-28 18:28 | 51.9844 | 486 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153260 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153260 |  | AUD-2026-09-2000017609ACN-2026-09-4000153260 | 21 |  | 27 | 80 | 0 | 0 | 70
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153261 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Pending IA audit report reply | 1.4 | Earlier action points status checked | 1527 | RAIPUR DEPOT | IA report reply discussed & to be sent | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153261 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153261 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153261 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153261 |  | AUD-2026-09-2000017609ACN-2026-09-4000153261 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | Practical training demostrate on workman and field officer on 24 Sept 26 | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153263 | Open | KAMLESH SAHU | 2026-09-25 | HVLR Operated found ok | 2.2 | Double contingency scenario simulated; observations recorded | 1527 | RAIPUR DEPOT | Needs more training to the officers | SOD | Marketing | ECZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153263 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153263 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153263 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153263 |  | AUD-2026-09-2000017609ACN-2026-09-4000153263 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153268 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Lot of old scrap and absolute equipments , automation fitting , guigages , project material is found scattered and also some projectjobs found incomplete. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1527 | RAIPUR DEPOT | All project surplus material to be segregated . Also pending project jobs to be completed and budget for same to be sought from projects or HQO | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153268 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153268 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153268 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153268 |  | AUD-2026-09-2000017609ACN-2026-09-4000153268 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153269 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . | 4.2 | Maintenance activities reviewed | 1527 | RAIPUR DEPOT | fire engines , mechanical seal to be provided as heavy water leakge found in 1-2 engines | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153269 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153269 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153269 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153269 |  | AUD-2026-09-2000017609ACN-2026-09-4000153269 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153271 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Lot of scrap material , particularly project items and old depot scrap to be identified | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1527 | RAIPUR DEPOT | RFD of all these material to be made | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153271 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153271 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153271 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153271 |  | AUD-2026-09-2000017609ACN-2026-09-4000153271 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | OPEN | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153273 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Needs to organise the material in the store | 6.2 | Engg Stores | 1527 | RAIPUR DEPOT | Unwanted and absolute items must be segreegated and disposal activity must be done | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153273 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153273 | 2026-08-28 18:28 | 51.9844 | 394 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153273 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017609ACN-2026-09-4000153273 |  | AUD-2026-09-2000017609ACN-2026-09-4000153273 | 21 |  | 27 | 80 | 0 | 0 | 57
|  |  |  | Data sought by HQO has submitted for further processing. Response awaited from HQO | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153276 | Open | KAMLESH SAHU | 2026-10-02 | Reviewed the major KPIs of stock loss , scrap disposal , M&I , Projects discussed for last year . MEB budget requirement for this depot also was discussed for taking up with HQO | 1.2 | Performance review conducted | 1528 | RAIPUR IRD-II | Addl. 2.5 Crore Budgetis required for new depot | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153276 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153276 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153276 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153276 |  | AUD-2026-09-2000017611ACN-2026-09-4000153276 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | Cost estimation and Budget proposal for OISD pending point submitted to HQO. Also, pending jobs for parking area related to fire fighting development is under process and expected to completed by Oct-26. Also Proposal for parking area land & boundary wall development has submitted | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153277 | Open | KAMLESH SAHU | 2026-10-02 | All pending OISD points , pending parking area jobs discussed . Location was advised to provide revised cost estimate of pending parking area jobs and OISD Complience | 1.3 | Pending issues reviewed | 1528 | RAIPUR IRD-II | Details of panding parking area and cost estimate for NPCB Revised budget required for OISD to be provided | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153277 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153277 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153277 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153277 |  | AUD-2026-09-2000017611ACN-2026-09-4000153277 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | Data sought by HQO has submitted for further processing. Response awaited from HQO | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153279 | Open | KAMLESH SAHU | 2026-10-02 | Additional MEB is required for New IRD | 1.5 | HQO / Zonal support required identified | 1528 | RAIPUR IRD-II | Follow up with HQO for additional budget as per prorata | SOD | Marketing | ECZ | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153279 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153279 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153279 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153279 |  | AUD-2026-09-2000017611ACN-2026-09-4000153279 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | Light post has provided in front of gantry. Back side work is under process | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153282 | Open | KAMLESH SAHU | 2026-10-02 | As per OISD AUDIT lux level was found inadquate in parking area , DG area , ETP Panel room, transf room , VCB area , primary roads | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1528 | RAIPUR IRD-II | Location is advised to put the Light post as availble in the yard and put the additional lights to meet the lux level | SOD | Marketing | ECZ | 2026-12-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017611ACN-2026-09-4000153282 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153282 | 2026-08-28 18:00 | 52.0038 | 486 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153282 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153282 |  | AUD-2026-09-2000017611ACN-2026-09-4000153282 | 21 |  | 27 | 80 | 3 | 3 | 70
|  |  |  | Budget allocation request with supporting document has sent to HQO. PR Prepration is under process | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153284 | Open | KAMLESH SAHU | 2026-10-02 | VA system not yet activated at new depot | 2.7 | VA alerts checked / analysed | 1528 | RAIPUR IRD-II | to be followed up with DI team / HQO | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153284 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153284 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153284 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153284 |  | AUD-2026-09-2000017611ACN-2026-09-4000153284 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | File note 137203 created on 25 sept 26 has been initiated. | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153287 | Open | KAMLESH SAHU | 2026-10-02 | Raipur IRD II Tank 101 – 770.0/w-1.4/731.5/27.5 (TAS – 770.0/w-1.5 / 736.2/27.5 ) Tank 202 – 1676.6/ w-1.6/807.5/29.5 (TAS – 1677.3/W-1.8/807.6/28.66) | 3.7 | Inventory physical dip of minimum two tanks taken | 1528 | RAIPUR IRD-II | Location to ensure TFMS-SAP integration for Raipur IRD II by Sept 26 | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153287 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153287 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153287 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153287 |  | AUD-2026-09-2000017611ACN-2026-09-4000153287 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153289 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | 7 such instances found between Apr - July 26 is on account of annual proving by W&M | 3.13 | K-factor changes reviewed (if any) | 1528 | RAIPUR IRD-II | Location to ensure stabilisation of TT gantry & Dip elimination FN by Jan 27. | SOD | Marketing | ECZ | 2027-01-31 |  | 4 |  | S2 | F2 | 2027-01-31 | AUD-2026-09-2000017611ACN-2026-09-4000153289 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153289 | 2026-08-28 18:00 | 52.0038 | 517 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153289 | 532 | 8294 | 21 | 8294 | -103 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153289 |  | AUD-2026-09-2000017611ACN-2026-09-4000153289 | 21 |  | 27 | 80 | 3 | 3 | 74
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153290 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Compliance status reviewed . OISD compliances of 28 points reviewed and found that 7 complied & budget is required for other points | 3.18 | OISD/MDSA/SSA compliance reviewed | 1528 | RAIPUR IRD-II | Location advised to submit revised budget request for complinace of all pending points by 30.09.2026 | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153290 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153290 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153290 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153290 |  | AUD-2026-09-2000017611ACN-2026-09-4000153290 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153291 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Lot of project material is found scattered in the yards beside the MCC room and also behind the DG Set . | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1528 | RAIPUR IRD-II | All project surplus material to be segregated . Also pending project jobs to be completed and budget for same to be sought from projects or HQO | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153291 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153291 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153291 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153291 |  | AUD-2026-09-2000017611ACN-2026-09-4000153291 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153292 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Reviewed . Location officers advised to have M&I calander in the beginning of the month and carry out activities as per calander and all records to be updated . | 4.2 | Maintenance activities reviewed | 1528 | RAIPUR IRD-II | Advised to maintain the quick reference plan . | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153292 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153292 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153292 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153292 |  | AUD-2026-09-2000017611ACN-2026-09-4000153292 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153293 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Parking area pending project jobs , pending project activities inside depot to be completed | 4.3 | Project progress reviewed | 1528 | RAIPUR IRD-II | Parking area fire fighting facility pending project activities to be completed . budget details to be provided . | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153293 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153293 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153293 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153293 |  | AUD-2026-09-2000017611ACN-2026-09-4000153293 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153294 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Lot of scrap material , particularly project items and old depot scrap to be identified | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1528 | RAIPUR IRD-II | RFD of all these material to be made | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153294 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153294 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153294 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153294 |  | AUD-2026-09-2000017611ACN-2026-09-4000153294 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153295 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Visitor room & TT crew waiting area is not available in new depot | 6.1 | Visitor room & TT crew shed | 1528 | RAIPUR IRD-II | same need to be identified and budget request to be given | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153295 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153295 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153295 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153295 |  | AUD-2026-09-2000017611ACN-2026-09-4000153295 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153296 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | Same is shifted but are of insufficient capacity . | 6.2 | Car /scooter parking shed for employees | 1528 | RAIPUR IRD-II | Parking shed required for min. 10 cars and 30 2 wheelers . Budget requirement to be given | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153296 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153296 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153296 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153296 |  | AUD-2026-09-2000017611ACN-2026-09-4000153296 | 21 |  | 27 | 80 | 3 | 3 | 57
|  |  |  | PENDING | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153298 | Open | KHADE RAKESH GANPATRAO | 2026-09-24 | No STP provided for office or driver amenity , which is must requirement for any Industry | 6.4 | STP | 1528 | RAIPUR IRD-II | Budget request to be given | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153298 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153298 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153298 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153298 |  | AUD-2026-09-2000017611ACN-2026-09-4000153298 | 21 |  | 27 | 80 | 3 | 3 | 57
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Same observation upcoming Senior managemnet inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122537 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | TAS Audit: 20 points pending to be complied. TAS upgradation project is going on. | 1.3 | Pending issues reviewed | 1233 | BHARATPUR TERMINAL | All 20 pending points to be complied by 31st March 2026. | SOD | Marketing | NWF | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122537 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122537 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122537 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122537 | AUD-2026-03-2000011210ACN-2026-03-4000122537 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Same observation upcoming Senior managemnet inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122538 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | 1. Self safety Audit, Set 2025: 5 points pending 2. Comprehensive audit, 23rd Sept to 27th Sept 2025: 23 points pending 3. T4S audit: 15 points pending | 1.4 | Earlier action points status checked | 1233 | BHARATPUR TERMINAL | Except two points of comprehensive audit (1. Storm water drain and 2. Sample room in Hazardous area for pipeline location), all pending points to be closed by 31.03.2026 | SOD | Marketing | NWF | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122538 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122538 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122538 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122538 | AUD-2026-03-2000011210ACN-2026-03-4000122538 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Proposal has been sent and approved, | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122539 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Bay 4 is required to be converted into mixed bay. At present, it is HSD +SKO. As location is not handling SKO at present, it is advised to convert this bay into MS +HSD. In line blending facility of ethanol to be added in this bay. Pls prepare cost estimate and send the proposal for conversion. Zone will assist in getting fund approval. | 1.5 | HQO / Zonal support required identified | 1233 | BHARATPUR TERMINAL | Pls ensure to send cost estimate by 9th March and hence proposal by 15.03.2026 | SOD | Marketing | NWF | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | PROCESS SAFETY | S1 | F3 | 2026-03-15 | AUD-2026-03-2000011210ACN-2026-03-4000122539 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122539 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122539 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011210ACN-2026-03-4000122539 | AUD-2026-03-2000011210ACN-2026-03-4000122539 | 21 | 21 | 26 | 80 | 2 | 1 | 28 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Location has planned for in-tank blending | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122540 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Location to prepare proposal for inline Biodiesel loading | 1.8 | Improvement plans discussed | 1233 | BHARATPUR TERMINAL | Propsal to be made with cost estimate | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | PROCESS SAFETY | S1 | F3 | 2026-04-30 | AUD-2026-03-2000011210ACN-2026-03-4000122540 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122540 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122540 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011210ACN-2026-03-4000122540 | AUD-2026-03-2000011210ACN-2026-03-4000122540 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | observation upcoming Senior managemnet inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122702 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | 8 Projects are there which are ongoing. Status of all 8 projects were reviewed. | 4.3 | Project progress reviewed | 1233 | BHARATPUR TERMINAL | All these projects are to be closed by March end. | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122702 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122702 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122702 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122702 | AUD-2026-03-2000011210ACN-2026-03-4000122702 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation in upcoming Senior managment inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122710 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Discounted toll to be implemented | 6.9 | Discounted toll | 1233 | BHARATPUR TERMINAL | There is Gazette notification. Email shared with location on discounted toll concept. Pls implement | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122710 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122710 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122710 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122710 | AUD-2026-03-2000011210ACN-2026-03-4000122710 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Monthly SPPI is being done | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122709 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.8 | Additive stock monitoring | 1233 | BHARATPUR TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122709 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122709 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122709 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011210ACN-2026-03-4000122709 | AUD-2026-03-2000011210ACN-2026-03-4000122709 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming senior managment inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122705 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Bio diesel one PO is there. Complete quantity has to be consumed by March 26. One 70 kl UG tank to be converted into B7 HSD in tankblending. One 70 kl UG tank to be converted in Biodiesel & 1 SKO tank (600 kl) to be converted into B7 HSD. | 6.4 | Consumption of Bio Diesel quantity | 1233 | BHARATPUR TERMINAL | Pls consume omplete bio diesel allocated qty for Bharatpur IRD | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122705 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122705 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122705 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122705 | AUD-2026-03-2000011210ACN-2026-03-4000122705 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming senior managment inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122704 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Location has placed PO on MOV spare supplier. Pls ensure that all MOVs are communicating remotely. | 6.3 | mov repair and communication | 1233 | BHARATPUR TERMINAL | Pls ensure timely action | SOD | Marketing | NWF | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-03-31 | AUD-2026-03-2000011210ACN-2026-03-4000122704 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122704 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122704 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011210ACN-2026-03-4000122704 | AUD-2026-03-2000011210ACN-2026-03-4000122704 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation recorded in upcoming senior management inspection | AUDIT UPLOAD IN SAP | 2026-01-20 | AUD-2026-03-2000011210 | 2026-01-19 | Released | I1802 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122711 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Old Lubes are required to be liquidated | 6.1 | Liquidation of slow moving Lube | 1233 | BHARATPUR TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is required. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-30 | AUD-2026-03-2000011210ACN-2026-03-4000122711 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011210ACN-2026-03-4000122711 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-03-2000011210 - ACN-2026-03-4000122711 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011210ACN-2026-03-4000122711 | AUD-2026-03-2000011210ACN-2026-03-4000122711 | 21 | 21 | 26 | 80 | 2 | 1 | 35 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming OISD | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128572 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | TAS audit was conducted on 27.09.2025. Out of 28 recomm., 12 recomm are still pending to be complied. 9 points of Comp. audit (23rdto 27th Sept 2025), 5 points of T4S audit and 4 points of SSA to be complied | 1.3 | Pending issues reviewed | 1233 | BHARATPUR TERMINAL | All points are required to be complied by 15th May 2026 | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128572 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128572 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128572 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128572 | AUD-2026-04-2000010749ACN-2026-04-4000128572 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Proposal has been apporved and work in progress | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128573 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Bay 4 is required to be converted into mixed bay. At present, it can be used to load HSD only. Location to revert with action plan with budget requirement | 1.4 | Earlier action points status checked | 1233 | BHARATPUR TERMINAL | Except two points of comprehensive audit (1. Storm water drain and 2. Sample room in Hazardous area for pipeline location), all pending points to be closed by 31.03.2026 | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128573 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128573 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128573 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128573 | AUD-2026-04-2000010749ACN-2026-04-4000128573 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128575 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | TFMS SAP integration file note approval to be renewed. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1233 | BHARATPUR TERMINAL | Pls prepare action plan and record data as per format mentioned in circular of year 2022. Circular shared with location | SOD | Marketing | NWF | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-31 | AUD-2026-04-2000010749ACN-2026-04-4000128575 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128575 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128575 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128575 | AUD-2026-04-2000010749ACN-2026-04-4000128575 | 21 | 21 | 27 | 80 | 2 | 1 | 52 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128583 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | 1. RIM seal of TK17 was checked. RSFPS of TK17 couldn’t be operated from control room as well as push button. There is no communication. This RSFPS didn't work during my last visit also. Location informed that they need to replace the card of RSFPS. Location was suggested to replace the same on immediate basis. 2. 5 HVLRs operated out of 7 HVLRs. All worked well. 3. Foam pourer of all tanks were operated. Foam was coming late in few tanks. Otherwise, it worked well. 4. Double hydrant hose was operated. Hydrant hose coupling got dismantled. Hydrant hose was getting disconnected from male coupling. Locking system to be checked and rectified. 5. HCD was not functional at VRU and dyke-2. 6. Dyke valve position indicator was operated. It worked well. Local hooter sounded. Baseplate to be welded on top of valve handle in one of the dykes shown to location personnel. 7. Earthing disconnected from one of Ttunder loading. Loading stopped. 8. One MEFG operated. It worked well. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1233 | BHARATPUR TERMINAL | RIM seal to be attended immediately. HCD to be rectified. | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128583 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128583 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128583 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128583 | AUD-2026-04-2000010749ACN-2026-04-4000128583 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128582 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Not okay. Both tanks in CFS were almost empty. Location informed that foam is available with them. Location should top up foam tanks. | 2.9 | Foam inventory verified | 1233 | BHARATPUR TERMINAL | This kind of situation is not desirable. Foam should always be available in CFS tank to replenish foam in daughter tank of HVLR in case of an emergency | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 16 | PROCESS SAFETY | S4 | F4 | 2026-04-30 | AUD-2026-04-2000010749ACN-2026-04-4000128582 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128582 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128582 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | HIGH |  | AUD-2026-04-2000010749ACN-2026-04-4000128582 | AUD-2026-04-2000010749ACN-2026-04-4000128582 | 21 | 21 | 27 | 80 | 2 | 1 | 35 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128750 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Old Lubes are required to be liquidated | 6.1 | Liquidation of slow moving Lube | 1233 | BHARATPUR TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is required. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128750 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128750 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128750 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000010749ACN-2026-04-4000128750 | AUD-2026-04-2000010749ACN-2026-04-4000128750 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128593 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Location has received materials of MOV except one actuator. Pls ensure that all MOVs are communicating remotely. | 6.3 | mov repair and communication | 1233 | BHARATPUR TERMINAL | Pls ensure timely action | SOD | Marketing | NWF | 2026-05-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-05-15 | AUD-2026-04-2000010749ACN-2026-04-4000128593 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128593 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128593 | 532 | 8294 | 21 | 8294 | 157 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128593 | AUD-2026-04-2000010749ACN-2026-04-4000128593 | 21 | 21 | 27 | 80 | 2 | 1 | 37 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128594 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Bio diesel one PO is there. Location is ready with in tank blending. Location informed that vendor is not ready to supply bio diesel because of increase in cost. Location has been advised to keep follow ups. | 6.4 | Consumption of Bio Diesel quantity | 1233 | BHARATPUR TERMINAL | Pls consume omplete bio diesel allocated qty for Bharatpur IRD | SOD | Marketing | NWF | 2026-05-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-05-31 | AUD-2026-04-2000010749ACN-2026-04-4000128594 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128594 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128594 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128594 | AUD-2026-04-2000010749ACN-2026-04-4000128594 | 21 | 21 | 27 | 80 | 2 | 1 | 39 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation noted in upcoming Senior management inspection | VISIT OF BHARATPUR TML IN Q1 2026-27 | 2026-04-18 15:00 | AUD-2026-04-2000010749 | 2026-04-16 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128599 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Discounted toll to be implemented | 6.9 | Discounted toll | 1233 | BHARATPUR TERMINAL | There is Gazette notification. Email shared with location on discounted toll concept. Pls implement | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-04-2000010749ACN-2026-04-4000128599 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010749ACN-2026-04-4000128599 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-04-2000010749 - ACN-2026-04-4000128599 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-04-2000010749ACN-2026-04-4000128599 | AUD-2026-04-2000010749ACN-2026-04-4000128599 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation recorded in upcoming SMI | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138486 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | TAS audit was conducted on 27.09.2025. Out of 28 recomm., 9 recomm are still pending to be complied. Target date of compliance of 9TAS audit points is 15.07.2026. Comp. audit (23rd to 27th Sept 2025) 5 points are still balance to be complied. This needs to be complied by 31.07.206. 2 points of T4S audit and 2 points of SSA to be complied by 31.07.2026 | 1.3 | Pending issues reviewed | 1233 | BHARATPUR TERMINAL | All points are required to be complied by 31.07.2026 | SOD | Marketing | NWF | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-06-2000013164ACN-2026-06-4000138486 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138486 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138486 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138486 | AUD-2026-06-2000013164ACN-2026-06-4000138486 | 21 | 21 | 27 | 80 | 2 | 1 | 48 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation recorded in upcoming SMI | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138488 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | TFMS SAP integration file note approval to be renewed. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1233 | BHARATPUR TERMINAL | This point is repeated. Location is stablizing with Tas upgradation. Pls ensure time bound action plan and complete the file note approval by 31.08.2026 | SOD | Marketing | NWF | 2026-08-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-31 | AUD-2026-06-2000013164ACN-2026-06-4000138488 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138488 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138488 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138488 | AUD-2026-06-2000013164ACN-2026-06-4000138488 | 21 | 21 | 27 | 80 | 2 | 1 | 52 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation recorded in upcoming SMI | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138493 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | 1. RIM seal of TK17 was checked. RSFPS of TK17 couldn’t be operated from control room as well as push button. There is no communication. This RSFPS didn't work during my last two visits also.Location need to take immediate action 2.ESD was operated near ETP. it worked well. 3. 3 HVLRs were operated. It worked well. 4. Public address sytem was checked. It was found working | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1233 | BHARATPUR TERMINAL | RIM seal to be attended immediately. HCD to be rectified. | SOD | Marketing | NWF | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-06-2000013164ACN-2026-06-4000138493 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138493 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138493 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013164ACN-2026-06-4000138493 | AUD-2026-06-2000013164ACN-2026-06-4000138493 | 21 | 21 | 27 | 80 | 2 | 1 | 57 | 56
MEENA HEMANT KUMAR | 2026-09-24 |  |  | Observation recorded in upcoming SMI | VISIT TO BHARATPUR TML ON 12TH AND 13TH | 2026-06-13 | AUD-2026-06-2000013164 | 2026-06-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138492 | Closed | MEENA HEMANT KUMAR | 2026-09-24 | Not okay. Both tanks in CFS were almost empty. It was also found that few foam barrels deployed in the field are half filled | 2.9 | Foam inventory verified | 1233 | BHARATPUR TERMINAL | This kind of situation is not desirable. This is a repeated point. Foam should always be available in CFS tank to replenish foam indaughter tank of HVLR in case of an emergency | SOD | Marketing | NWF | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 16 | PROCESS SAFETY | S4 | F4 | 2026-06-30 | AUD-2026-06-2000013164ACN-2026-06-4000138492 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013164ACN-2026-06-4000138492 | 2026-09-16 17:45 | 33.0143 | 388 | >20 | AUD-2026-06-2000013164 - ACN-2026-06-4000138492 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | HIGH |  | AUD-2026-06-2000013164ACN-2026-06-4000138492 | AUD-2026-06-2000013164ACN-2026-06-4000138492 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 56
KUSHAGRA VASHISHTH | 2026-09-24 |  |  | New Security tendor floated with armed gaurd deployment in all shifts included in the scope of job/Tender condition. Gem bib published on 18.09.26 as confirmed by IFS. (GEM/2026/B/8053893) | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000144658 | Closed | KUSHAGRA VASHISHTH | 2026-09-24 | Three HLSA audit points not complied: 1. Biometric control access to be provided for admin building entry. 2. Armed security guard to be provided at location 3. Tie Up with hospitals for ambulance which can reach within 10 minutes | 1.3 | Pending issues reviewed | 1278 | JODHPUR TERMINAL | Pls ensure compliance of all pending HLSA points | SOD | Marketing | NWF | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-07-2000015346ACN-2026-07-4000144658 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144658 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144658 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144658 | AUD-2026-07-2000015346ACN-2026-07-4000144658 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUSHAGRA VASHISHTH | 2026-09-24 |  |  | New Security tendor floated with armed gaurd deployment in all shifts included in the scope of job/Tender condition. Gem bib published on 18.09.26 as confirmed by IFS. (GEM/2026/B/8053893) | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144672 | Closed | KUSHAGRA VASHISHTH | 2026-09-24 | HLSA Audit - 3 points pending out of 6. Comprehensive Audit (Nov 25): Nil pending point, T4S audit: Nil point pending, Sr. Mgmt Audit: all points complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1278 | JODHPUR TERMINAL | All points to be complied by 30.09.2026. | SOD | Marketing | NWF | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-07-2000015346ACN-2026-07-4000144672 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144672 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144672 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144672 | AUD-2026-07-2000015346ACN-2026-07-4000144672 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | MOC taken for Shri Kushagra Vashishth (Recent Transfer) | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144671 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | MOC for new officer Mr Kushagra not taken | 3.17 | MOC status reviewed | 1278 | JODHPUR TERMINAL | Location to initiate MOC | SOD | Marketing | NWF | 2026-07-31 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144671 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144671 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144671 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144671 | AUD-2026-07-2000015346ACN-2026-07-4000144671 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | All rusted earthing strips have been checked/replaced, GI paint applied wherever feasible, and strip sizes verified for compliance with OISD-244. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144670 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Checked three Earth Pits: 1. Earth Pit no. 107: Painting required on 4'' pipe. 2. Earth pit no. 36: 2'' pipe installed instead of4'' pipe. 3. Earth pit no. 28: Not clean. | 3.16 | Earth pits / boundary / vegetation control checked | 1278 | JODHPUR TERMINAL | Location to check and replce all rusted earth strips, apply GI paint whereever possible. Earthing strip size also needs to be checked and modified in line with OISD 244. | SOD | Marketing | NWF | 2026-08-05 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-05 | AUD-2026-07-2000015346ACN-2026-07-4000144670 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144670 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144670 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144670 | AUD-2026-07-2000015346ACN-2026-07-4000144670 | 21 | 21 | 27 | 80 | 0 | 0 | 49 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | Dedicated person assigned for gantry wash .Now Only one person engaged in planning room .Housekeeping job are being done on regularbasis . | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144669 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Housekeeping needs to be improved. Sheds, gantry area- loading arms, pipelines, drains to be cleaned. Location to utilize the contract manpower judiciously and deploy more manpower for housekeeping by reducing manpower from office jobs. | 3.15 | Housekeeping & PPE usage checked | 1278 | JODHPUR TERMINAL | One workment to be stationed at TT Gantry only for housekeeping/cleaning of all equipment, pipeline and structures by soap water solution on daily basis. Location needs to ensure that each area viz. gantry, UG Tank farm, AG tank farm, pipelines and drains are clean and free from any vegetations. Pls do not engage two contract person in planning room. One contract person of planning room to beshifted for housekeeping job. | SOD | Marketing | NWF | 2026-07-31 | COMPLACENCY OR RISK NORMALIZATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144669 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144669 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144669 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144669 | AUD-2026-07-2000015346ACN-2026-07-4000144669 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | VTS violations, particularly speed violations, are being further reduced through enhanced monitoring and corrective action. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144667 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Total TT blocking have reduced from 37 (May26) to 19 (June26), although location has reduced no. of Route and Stoppage violations, need to work for further reduction. Response of transport handling officer is not good. He should give timely reply of email | 3.3 | VTS deviations reviewed | 1278 | JODHPUR TERMINAL | Location need to reduce the VTS violations further especially speed violations. | SOD | Marketing | NWF | 2026-08-31 | INSUFFICIENT SUPERVISION | 15 | PROCESS SAFETY | S3 | F5 | 2026-08-31 | AUD-2026-07-2000015346ACN-2026-07-4000144667 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144667 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144667 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144667 | AUD-2026-07-2000015346ACN-2026-07-4000144667 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | All transport TTs have been verified for correct calibration, and necessary corrective action has been taken. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000144666 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Checked for 2 TTs. Following variations observed compartment wise: 1. RJ19GJ2215: +1 mm/+2 mm/+5 mm/+1 mm 2. RJ19GH9484: +2 mm/+1mm/+6 mm/+5mm | 3.2 | Post-loading dip checks verified | 1278 | JODHPUR TERMINAL | Variation is more in transport TTs. Location needs to verify all transport TTs for correct calibration. | SOD | Marketing | NWF | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-07-2000015346ACN-2026-07-4000144666 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144666 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144666 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144666 | AUD-2026-07-2000015346ACN-2026-07-4000144666 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | Training has been imparted for new joinees and contract engineers. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144665 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | New officer operated HVLR-06 well. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1278 | JODHPUR TERMINAL | Training to be enhanced to new joinees and contract engineers. | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144665 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144665 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144665 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144665 | AUD-2026-07-2000015346ACN-2026-07-4000144665 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-07 | Mock drill entries incorporated in fire engine log book. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144664 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | A. HVLR-06 operated. It worked fine. B. ESD was checked. It worked well. C. HCD -3 (point type), HCD-7 (path type) were tested. Found working. Local hooter sounded. D. Dyke Wall point indicator of dyke-6 near TK-29 checked and found working. E. ESD checked at Gantry. Found working. F. HSD pump forced stopped from Gantry. Found working. G. Earthing interlock checked for TTs at bay. Found operational. H. Checked for Fire Engines. Found operational. Fire Engine logbook also found well maintained. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1278 | JODHPUR TERMINAL | Fire Engine logbook to also contain running hours of engine pertaining to fire drill. | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144664 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144664 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144664 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144664 | AUD-2026-07-2000015346ACN-2026-07-4000144664 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-07 | As per OISD guideline the location is maintaining more than 50% of maximum foam demand scenario i.e. 50% of 7.381kl ~3.6 kl | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144663 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | 1. 8.5 Kl x 2 tanks were having 2700 litre x 2 = 5.4 KL foam. Foam was thick and level indicator was not showing foam inside horizontal tank. Foam level was measured by using dip tape. 2. Foam requirement is 16 KL as per MOU with MARG members 4. Location informed that each of the 49 WCFM is having 200 litre foam barrel. Total foam quantity is approx 27 Kl inside Terminal | 2.9 | Foam inventory verified | 1278 | JODHPUR TERMINAL | Foam quantity is not found sufficient. Pls ensure that all foam barrels are fully filled near fire fighting device, central foam tanks in CFS should be minimum half filled. HVLR daughter tanks should be fully filled. | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144663 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144663 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144663 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144663 | AUD-2026-07-2000015346ACN-2026-07-4000144663 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-07 | On 16.07.2026, with the assistance of AMC, a monitor was installed at the Main Gate to facilitate real-time monitoring of VA alertsby security personnel. The location is regularly monitoring and acknowledging legitimate VA alerts, while false alerts are being taken up with the vendor for necessary resolution. Several tickets have been raised with the vendor against the identified false alerts, and appropriate corrective actions have been taken accordingly. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144662 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | VA system alerts were checked for last three months: Non-compliance towards PPE: 4 cases Non-compliance towards Fire ext: 6 Non-compliance towards wheel choke: 0 Perimeter intrusion in non-working hr: 10 cases Emergency gate opening cases: 0 No. of cases which were declared as false in last 3 months: Non-compliance towards PPE: 0 Non-compliance towards Fire ext: 6 Non-compliance towards wheel choke: 0 Perimeter intrusion in non-working hr: 10 cases Emergency gate opening cases: 0 | 2.7 | VA alerts checked / analysed | 1278 | JODHPUR TERMINAL | Location is required to keep close watch on VA alert. Critical alert iof VA system (like perimeter intrusion, leakage, fire etc) should reflect at security room in the display provided. This will help location to get the emergency informed even in night time through security. If any false alerts are repeatedly coming, the same needs to be rectified with the help of HQO support team. Critical VA alrets are more in Jodhpur IRD. It needs to be reduced to almost nil | SOD | Marketing | NWF | 2026-07-31 | THIRD PARTY ERRORS | 15 | PROCESS SAFETY | S3 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144662 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144662 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144662 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144662 | AUD-2026-07-2000015346ACN-2026-07-4000144662 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-07 | CCTV footage is being reviewed at location on a weekly basis, and the observations are being compiled and shared with the Zonal Head for review and necessary action. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144661 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | Checked through CCTV footage of 1st April 2026 for checking readiness of Security personnel. Time of checking was 02.00 am to 03.00am. Also checked CCTV footage of TT gantry area from 16.30 hr to 17.30 hr on 31st March 2026. Found okay | 2.4 | Security alertness checked (night-halt / surprise checks) | 1278 | JODHPUR TERMINAL | CCTV footage to be checked by location on weekly basis and observations to be share with Zonal head. | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 15 | PROCESS SAFETY | S3 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144661 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144661 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144661 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144661 | AUD-2026-07-2000015346ACN-2026-07-4000144661 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | Lux levels at TK-29 valve area and road enroute to ETP have been checked and enhanced to meet the required illumination levels. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144660 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Lux requirement/ Lux achieved: 1. Road enroute ETP (secondary road): 06/10 2. Pump House: 100/163 4. Tank farm valve manifold area: a) Near TK-29: 60/54 b) Near Mother Foam Tank- 60/82 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1278 | JODHPUR TERMINAL | Lux reading was lesser than requirement at TK29 valve area and Road enroute ETP. Pls check. | SOD | Marketing | NWF | 2026-07-31 | COST-CUTTING COMPROMISING SAFETY | 15 | PROCESS SAFETY | S3 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144660 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144660 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144660 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144660 | AUD-2026-07-2000015346ACN-2026-07-4000144660 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-24 | KUSHAGRA VASHISHTH | 2026-09-17 | Last six OISD audit recommendations and ESA observations have been reviewed. Nearby OMC HSE officers/LICs have been invited as observers for fire drills, and drills are being conducted at all potential hazard facilities identified in the HAZOP and Risk Register. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000144659 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Contingency scenario of leakage from compartment no. 2 of tank truck (TT) at bay no.1. Following observations made: 1) Involment ofTT crew in fire fighting to be avoided. Fire fighting to be handled by FOC team members only. 2) Coordination among all FOC team heads and CIC to be improved. 3) LEL to be checked by a person wearing SCABA with supporting rope attached and should be backed by fire fighting arrangement in ready condition. 4) There was delay in EDS siren 5) Foam not spreaded on nearby bays. 6) All clear siren to be given after confirmation from rescue team for nil injury/casuality. 7) Head count to be done properly by each team head. Duringhead count total nos. of team memeber to be provided along with no. of members present and whether they are safe or not. | 2.2 | Single contingency scenario simulated; observations recorded | 1278 | JODHPUR TERMINAL | Location to check last 6 OISD audit recommendations already shared with them. Observe the points being raised by ESA team. Locationshould also invite nearby OMC HSE officers and LICs to become their observer at the time of carrying out fire drill. Ensure fire drill is carried out at all identified potential hazard facilities which is mentioned in HAZOP and Risk register | SOD | Marketing | NWF | 2026-07-31 | INADEQUATE SAFETY CULTURE | 15 | PROCESS SAFETY | S3 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144659 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144659 | 2026-09-25 20:45 | 23.8893 | 388 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144659 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144659 | AUD-2026-07-2000015346ACN-2026-07-4000144659 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Officers are having hand on exercise for operating all the fire fighting equipment. Officers are sensitized w.r.t positioning of all the safety critical equipment and ESD . Location arresting the black oil rake receipt losses by suitable coordination and actions. Mail sent to loading location after each rake receipt ascertaining the losses. Location arresting the ethanol losses by suitable coordination and actions. Losses are regularly monitored. Transporters and DCTs taken on board for conversion of their TTs to bottom loading. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150232 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Individual review of officer carried out with respect to KPI and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1650 | HALDIA TERMINAL | Officers were advised to have hand on exercise for operating all the fire fighting equipment. Further, they should have the knowledge w.r.t positioning of all the safety critical equipment and ESD (Repeat Point). Location to arrest the black oil rake receipt losses by suitable coordination and actions. Location to also arrest the ethanol losses by suitable coordination and actions. Transporters and DCTs to be taken on board for conversion of their TTs to bottom loading. To be expedited. | SOD | Marketing | EZ | 2026-09-15 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-15 | AUD-2026-08-2000016860ACN-2026-08-4000150232 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150232 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150232 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150232 | AUD-2026-08-2000016860ACN-2026-08-4000150232 | 21 | 21 | 27 | 80 | 5 | 5 | 55 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | 1. Traffic management done by security. TTs are called in a staggered way to avoid chocking of TTs at ingate. 2. Grass removal done outside tank dyke / product & hydrant pipe tracks. 3. ETP outlet drain cleared. Water flowing freely. 4. Wrapping Coating of inlet pipe of TK-15 rectified. 5. Product unloading hose arranged at designated place. 6. Drums of sludge kept at designated place.Will be disposed off in line with company policy. 7. Emergency trolley properly maintained . Lock and key mapping done on trolley for easy opening in case of any emergency. All the emergency kit available and usable in their respective compartments. 8. SOP boards changed wherever faded. EPs signages replaced wherever necessary. All the EPs tested as per the regular periodicity. 9. Job sites are cleared. Location ensures that the site is cleared by contractor up to the satisfaction of HPCL Terminal officer after completion of job. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150234 | Closed | ISLAM SK WAHIUL | 2026-09-24 | During last visit, it was advised to have good housekeeping specially in the backside of the black oil tanks. Location had improvedsignificantly w.r.t last visit however following were observed : 1. Chocking of TT In gate due to large no. of TT assembled at onetime for entry. Traffic management to be done by security 2. Grass removal to be done outside tank dyke / product & hydrant pipe tracks. 3. Chocking of the ETP outlet drain to be checked and cleared. 4. Wrapping Coating of inlet pipe of TK-15 found damaged. To be rectified. 5. Product unloading hose found lying inside the black oil tank. 6. Drums of sludge was kept outside the black oil tank farm. To be disposed off in line with company policy. 7. Emergency trolley to be properly maintained . Lock and key mapping to be done on trolley for easy opening in case of any emergency. All the emergency kit should be available and usable in their respective compartments. 8. SOP boards in field found faded. Maximum EPs signages found faded. To be rectified / updated. All the EPs to be tested as per the regular periodicity. 9. Many of the contractor items / left over items of project found lying at job site. Location to ensure that the site is cleared by contractor up to the satisfaction of HPCL Terminal officer after completion of job. | 1.4 | Earlier action points status checked | 1650 | HALDIA TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-09-15 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-15 | AUD-2026-08-2000016860ACN-2026-08-4000150234 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150234 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150234 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150234 | AUD-2026-08-2000016860ACN-2026-08-4000150234 | 21 | 21 | 27 | 80 | 5 | 5 | 55 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Calibration verification for TTs done and records maintained | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150236 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1650 | HALDIA TERMINAL | Calibration verification for TTs to be done and records maintained | SOD | Marketing | EZ | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150236 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150236 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150236 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150236 | AUD-2026-08-2000016860ACN-2026-08-4000150236 | 21 | 21 | 27 | 80 | 5 | 5 | 54 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Location ensuring to complete all the scenario as per ERDMP in the mock drills. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150237 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Location has prepared the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1650 | HALDIA TERMINAL | Location to ensure to complete all the scenario as per ERDMP in the mock drills. | SOD | Marketing | EZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150237 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150237 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150237 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150237 | AUD-2026-08-2000016860ACN-2026-08-4000150237 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Hands on training on safety critical equipment acquired by all the officers. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150243 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Junior Executive officers demonstrated the WCFM during the drill | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1650 | HALDIA TERMINAL | More hands on training on safety critical equipment to be acquired by all the officers | SOD | Marketing | EZ | 2026-09-10 | POOR COMMUNICATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150243 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150243 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150243 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150243 | AUD-2026-08-2000016860ACN-2026-08-4000150243 | 21 | 21 | 27 | 80 | 5 | 5 | 54 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Observations and recommendations implemented in the next and subsequent drills. Communication done clearly to the security guards. ESD activated instantaneously once drill started. MEFG operated in pool fire scenario. Sprinklers used to cool nearby tanks. Fire clock changed timely. Security Guard at Main gate called Mutual Aid members. Depot main gate kept open for movement of emergency vehicle. Security personnel trained w.r.t operating the WCFM/ MEFG. Planning officer trained for operating the HVLR. He is sensitized about the ESD positioning. SCABA - Training imparted to SGs w.r.t SCABA wearing and usages | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150238 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Mock Fire Drill Scenario : Leakage from 2nd body valve of HSD tank TK - 03 and then converted in to fire upon advise of the Inspection team. This was identified by a contractor coming from that side after completion of his work. This was an off shift scenario. Following were the observations : 1 Communication was not clearly conveyed to the SGs. 2. Drill started at 1815 hrs, However ESD activated at 1820 hrs 3. Nearest WCFM was operated 4. MEFG was not operated to carpet the leaked oil 5. Sprinkler was not used on the nearby tanks for cooling 6. Fire Clock position was changed at 1825 hrs. 7. Security Guard at Main gate didn't called LIC, DSO, Mutual Aid members 8. Depot main gate was kept close which is a potential hindrance in movement of emergency vehicle. 9. Security personnel were not fully trained w.r.t operating the WCFM/ MEFG. 10. Planning officer who was present in depot that time was not very conversant with operating the HVLR. He was also not aware of the ESD positioning. 11. SCABA - Training to be imparted to all SGs w.r.t SCABA wearing and usages | 2.2 | Double contingency scenario simulated; observations recorded | 1650 | HALDIA TERMINAL | All the observation and recommendation of the drill to be implemented in the next and subsequent drill | SOD | Marketing | EZ | 2026-09-30 | POOR COMMUNICATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150238 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150238 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150238 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150238 | AUD-2026-08-2000016860ACN-2026-08-4000150238 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Old lights repaired. Lux Level on secondary roads found satisfactory. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150239 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Lux level checked : TT gantry : Required : 60 and observed : 100 Secondary roads : Required 10 and observed 8 at few places | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1650 | HALDIA TERMINAL | It was advised to improve the lux levels on the secondary roads by repairing the old lights. NPCB also approved for procurement of lights. Projects to be executed timely so as to comply this point | SOD | Marketing | EZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150239 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150239 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150239 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016860ACN-2026-08-4000150239 | AUD-2026-08-2000016860ACN-2026-08-4000150239 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | VMS implemented. Visitors enrolled accordingly. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150241 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Access control system found functional. | 2.8 | Access control systems checked | 1650 | HALDIA TERMINAL | VMS has been implemented. Nil case of visitors entry without VMS to be ensured | SOD | Marketing | EZ | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150241 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150241 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150241 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150241 | AUD-2026-08-2000016860ACN-2026-08-4000150241 | 21 | 21 | 27 | 80 | 5 | 5 | 54 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Emptiness of Ethanol TTs after getting unloaded checked personally by officers following SOP. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150245 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Random checking of the dip for TTs at TTG post loading done and found satisfactory. | 3.2 | Post-loading dip checks verified | 1650 | HALDIA TERMINAL | Emptiness of Ethanol TTs after getting unloaded to be checked personally by officers following SOP. | SOD | Marketing | EZ | 2026-08-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000016860ACN-2026-08-4000150245 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150245 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150245 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150245 | AUD-2026-08-2000016860ACN-2026-08-4000150245 | 21 | 21 | 27 | 80 | 5 | 5 | 52 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Location ensures EBP checks daily of the outgoing trucks and records maintained. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150247 | Closed | ISLAM SK WAHIUL | 2026-09-24 | Random checking of EBP done from the all level sample of TT WB33C5356 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1650 | HALDIA TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-09-10 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-10 | AUD-2026-08-2000016860ACN-2026-08-4000150247 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150247 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150247 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150247 | AUD-2026-08-2000016860ACN-2026-08-4000150247 | 21 | 21 | 27 | 80 | 5 | 5 | 54 | 56
KUNDU DEBARUN | 2026-09-24 | ISLAM SK WAHIUL | 2026-09-24 | Mahul pumps received at Terminal. 12 inch line supplied by vendor. | HALDIA TERMINAL Q2 FY 26-27 INSPECTION | 2026-08-20 00:14 | AUD-2026-08-2000016860 | 2026-08-18 12:45 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150255 | Closed | ISLAM SK WAHIUL | 2026-09-24 | MS unloading line project was reviewed and depot ensured to close all the project within timeline. | 4.3 | Project progress reviewed | 1650 | HALDIA TERMINAL | Understand pumps from Mahul got dispatched but not yet received at Terminal. Further, the 12 inch line not yet supplied by vendor,to be expedited. | SOD | Marketing | EZ | 2026-09-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-30 | AUD-2026-08-2000016860ACN-2026-08-4000150255 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016860ACN-2026-08-4000150255 | 2026-08-20 00:14 | 60.7441 | 388 | >20 | AUD-2026-08-2000016860 - ACN-2026-08-4000150255 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016860ACN-2026-08-4000150255 | AUD-2026-08-2000016860ACN-2026-08-4000150255 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 56
POTHALA VENKATA RAO | 2026-09-25 | M.RAJKUMAR | 2026-09-18 | Internal Inspection of TK5, TK14 and TK15 completed and put back into service. TK16 Cleaning completed and put back into Operation. TK3 inspection and repair completed and put back into Operation. | COIMBATORE_IRD_Q1_FY26_ZONAL_HEAD_INSPEC | 2026-06-20 18:00 | AUD-2026-07-2000015339 | 2026-06-20 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142957 | Closed | M.RAJKUMAR | 2026-09-18 | All OISD points are complied. Pending MDSA/SSA points related to tank inpection is reviewed and works are in progress | 3.18 | OISD/MDSA/SSA compliance reviewed | 1856 | COIMBATORE DEPOT | To follow up and put back the Tank TK03 into operation at the earliest. | SOD | Marketing | SZ | 2026-07-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-31 | AUD-2026-07-2000015339ACN-2026-07-4000142957 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015339ACN-2026-07-4000142957 | 2026-08-28 17:00 | 52.0455 | 389 | >20 | AUD-2026-07-2000015339 - ACN-2026-07-4000142957 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015339ACN-2026-07-4000142957 | AUD-2026-07-2000015339ACN-2026-07-4000142957 | 21 | 21 | 27 | 80 | 0 | 1 | 48 | 56
|  | SAXENA UMESH CHANDRA | 2026-05-20 | Newly joined officers are being trained by senior officers. Senior Officers are monitoring their learnings, extending necessary guidance and support in all critical activities | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000010980 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-05-4000130250 | Completed | SAXENA UMESH CHANDRA | 2026-05-20 |  | 1.1 |  | 1457 | INDORE DEPOT | XX | SOD | Marketing | CEN | 2026-05-20 |  | 1 |  | S1 | F1 | 2026-05-20 | AUD-2026-03-2000010980ACN-2026-05-4000130250 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010980ACN-2026-05-4000130250 | 2026-09-09 19:00 | 39.9622 | 261 | >20 | AUD-2026-03-2000010980 - ACN-2026-05-4000130250 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010980ACN-2026-05-4000130250 |  | AUD-2026-03-2000010980ACN-2026-05-4000130250 | 21 |  | 26 | 80 | 0 | -3 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | all route corections has been completed | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122294 | Closed | JOSVIN SUNNY | 2026-05-23 | Individual performace are reviewed and encouraged for their best performance area. Training requirements discussed | 1.2 | Performance review conducted | 1892 | KOZHIKODE DEPOT | Route correction by 28.2.26 | SOD | Marketing | CZR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-02-28 | AUD-2026-02-2000010911ACN-2026-03-4000122294 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122294 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122294 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122294 | AUD-2026-02-2000010911ACN-2026-03-4000122294 | 21 | 21 | 26 | 80 | 2 | -4 | 26 | 38
HARINIVAS S | 2026-06-12 | JOSVIN SUNNY | 2026-06-12 | not pretaining to location | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122295 | Closed | JOSVIN SUNNY | 2026-06-12 | TT induction.Railway payment 53 lakhs pending. (total 93 l, paid 40 L, 53 lakhs more needed) | 1.3 | Pending issues reviewed | 1892 | KOZHIKODE DEPOT | Coordinate with CPO | SOD | Marketing | CZR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-02-28 | AUD-2026-02-2000010911ACN-2026-03-4000122295 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122295 | 2026-09-17 16:00 | 32.0872 | 284 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122295 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000010911ACN-2026-03-4000122295 | AUD-2026-02-2000010911ACN-2026-03-4000122295 | 21 | 21 | 26 | 80 | 2 | -4 | 26 | 41
MAZUMDER SAUVIK | 2026-08-10 | UMESH KUMAR SINGH | 2026-07-31 | Location has ensured optimum TT parking making it make it more accessible and maneuverable in case of emergency. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-06-4000137704 | Closed | UMESH KUMAR SINGH | 2026-07-31 | TT parking fire fighting system: None of the monitors or hydrants are approachable easily. Hydrant points are not visible as well due to parking of TTs infront of them. | 6.13 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure less TT parking and make it more maneuverable. Hydrants to be accessible in case of emergency | SOD | Marketing | PZR | 2026-07-15 | THIRD PARTY ERRORS | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137704 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137704 | 2026-09-19 10:00 | 30.3372 | 343 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137704 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137704 | AUD-2026-06-2000012744ACN-2026-06-4000137704 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 49
MAZUMDER SAUVIK | 2026-08-11 | UMESH KUMAR SINGH | 2026-07-31 | Regualr cleaning is being done on regular basis. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-06-4000137706 | Closed | UMESH KUMAR SINGH | 2026-07-31 | DG yard: 500 KV DG was found maintained clean with no leakage, etc. However, deposition of mugs on spilled/leaked coolant on floor of DG, was found. | 6.15 | Quarterly Inspection | 1742 | BOKARO DEPOT | Regualr cleaning needs to be done. Location to ensure the same. | SOD | Marketing | PZR | 2026-07-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137706 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137706 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137706 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137706 | AUD-2026-06-2000012744ACN-2026-06-4000137706 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-08-11 | UMESH KUMAR SINGH | 2026-07-31 | Regualr training is being carried out with gate meeting/others is being imparted by Location safety officer and monitored by LIC. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-06-4000137708 | Closed | UMESH KUMAR SINGH | 2026-07-31 | Stake holder interaction: TT crew were interacted on Recent TT accidents, their root causes, importance of role of TT crew in our business, impact of accident on lives of TT crew, defensive driving. Importance of emergency button, night driving, continuous driving, medical check up under fit for road ,etc. were discussed. Most of the crew interacted with, were found to be aware of emergency button and its work. Operation of DCP extinguisher was also practiced. All TT crew, interacted with found to be aware of functioning and operation of fire extinguisher. TT crew were also asked for any suggestions with respect to the facility at depot. | 6.17 | Quarterly Inspection | 1742 | BOKARO DEPOT | OK. Ensure regualr training to be imparted by Location safety officer and monitored by LIC. | SOD | Marketing | PZR | 2026-07-15 | THIRD PARTY ERRORS | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137708 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137708 | 2026-09-19 10:00 | 30.3372 | 344 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137708 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137708 | AUD-2026-06-2000012744ACN-2026-06-4000137708 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 50
MAZUMDER SAUVIK | 2026-09-09 | UMESH KUMAR SINGH | 2026-07-31 | Two officer's have been engaged for checking the tanker before their exit. | BOKARO AUDIT Q1 | 2026-06-09 | AUD-2026-06-2000012744 | 2026-06-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.38QUARTERLY INSPECTION | ACN-2026-06-4000137728 | Closed | UMESH KUMAR SINGH | 2026-07-31 | Ethanol empty TT going out is not being checked by 2 officers. Only one officer is checking the tankers. | 6.38 | Quarterly Inspection | 1742 | BOKARO DEPOT | LIC to ensure that 2 officer are checking the tanker before the exit. | SOD | Marketing | PZR | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-15 | AUD-2026-06-2000012744ACN-2026-06-4000137728 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012744ACN-2026-06-4000137728 | 2026-09-19 10:00 | 30.3372 | 373 | >20 | AUD-2026-06-2000012744 - ACN-2026-06-4000137728 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000012744ACN-2026-06-4000137728 | AUD-2026-06-2000012744ACN-2026-06-4000137728 | 21 | 21 | 27 | 80 | 1 | 1 | 46 | 54
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 QUARTERLY INSPECTION | ACN-2026-09-4000153831 | Open |  |  | Display of safety slogans in tank farm area found inadequate. There were no safety slogans around Dyke 2 | 6.1 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety slogans to be displayed on outer wall of dyke 2 | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153831 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153831 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153831 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153831 |  | AUD-2026-09-2000017506ACN-2026-09-4000153831 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 QUARTERLY INSPECTION | ACN-2026-09-4000153832 | Open |  |  | MEFG of Tank 102 was operated. It worked well. | 6.2 | Quarterly Inspection | 1742 | BOKARO DEPOT | No recommendation | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153832 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153832 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153832 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153832 |  | AUD-2026-09-2000017506ACN-2026-09-4000153832 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-09-4000153833 | Open |  |  | Foam pourers of Tank 102 found not numbered. During testing, inadequate foam formation found from all foam pourers. Even water was coming out thru the air eductors, One of the foam pourer lines developped leakage | 6.3 | Quarterly Inspection | 1742 | BOKARO DEPOT | Foam pourers to be numbered. Location to check reason for inadequate foam generation and repair the leaky line | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153833 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153833 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153833 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153833 |  | AUD-2026-09-2000017506ACN-2026-09-4000153833 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 QUARTERLY INSPECTION | ACN-2026-09-4000153834 | Open |  |  | Sprinkers of Tank 201 were operated. Except nozzles M14 and M15, all nozzles functioned properly | 6.4 | Quarterly Inspection | 1742 | BOKARO DEPOT | Choked nozzles to be cleaned | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153834 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153834 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153834 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153834 |  | AUD-2026-09-2000017506ACN-2026-09-4000153834 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5QUARTERLY INSPECTION | ACN-2026-09-4000153835 | Open |  |  | Chamber of Earthpit no 153 found broken with cover plate caved in | 6.5 | Quarterly Inspection | 1742 | BOKARO DEPOT | Earthpit compartment to be made proper | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153835 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153835 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153835 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153835 |  | AUD-2026-09-2000017506ACN-2026-09-4000153835 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6QUARTERLY INSPECTION | ACN-2026-09-4000153836 | Open |  |  | Creepers found on hydrant line and nearby hose box 46. Front glass of the hose box found completely blurred | 6.6 | Quarterly Inspection | 1742 | BOKARO DEPOT | Proper housekeeping to be maintained. Blurred glass to be replaced. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153836 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153836 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153836 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153836 |  | AUD-2026-09-2000017506ACN-2026-09-4000153836 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-09-4000153837 | Open |  |  | No record of LEL measurement is there on renewed hot work permits. Tool box talk document found generic in many permits. Details, viz, place , etc. found blank in all tool box talk documents | 6.7 | Quarterly Inspection | 1742 | BOKARO DEPOT | Work permits and tool box talk documents to be maintained properly | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153837 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153837 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153837 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153837 |  | AUD-2026-09-2000017506ACN-2026-09-4000153837 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8QUARTERLY INSPECTION | ACN-2026-09-4000153838 | Open |  |  | Heaps of nuts and bolts found kept infront of approach towards hydrant point opposite bay no1. A pipe was also found kept infront of stair leading to hydrant post at corner of scrap yard | 6.8 | Quarterly Inspection | 1742 | BOKARO DEPOT | Approaches to fire fighting facilities to be kept clear | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153838 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153838 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153838 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153838 |  | AUD-2026-09-2000017506ACN-2026-09-4000153838 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9QUARTERLY INSPECTION | ACN-2026-09-4000153839 | Open |  |  | Repaired segment of sprinker line of Tank 201y, near spiral stair, found having no paint on welding area, leading to rusting | 6.9 | Quarterly Inspection | 1742 | BOKARO DEPOT | Proper painting to be ensured | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153839 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153839 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153839 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153839 |  | AUD-2026-09-2000017506ACN-2026-09-4000153839 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-09-4000153840 | Open |  |  | Leaks observed from pumps, near gland areas of Tank wagon pumphouse pumps MS2, LDO1, ARV of HSD1. Oil cup of pump no HSD1 found to be almost empty | 6.10 | Quarterly Inspection | 1742 | BOKARO DEPOT | Corrective action to be taken, by attending leaks and topping up the oil cup | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153840 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153840 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153840 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153840 |  | AUD-2026-09-2000017506ACN-2026-09-4000153840 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11QUARTERLY INSPECTION | ACN-2026-09-4000153841 | Open |  |  | Level gauge glass tube of one Fuel tank of 1010 KVA DG set of TW siding found broken. Location automation officer found not having full awareness of the facility. Some of the glass panes of windows found broken. Cut pieces of glass/ vinyl sheets, papers, etc. found scattered inside MCC room of TW Pump house | 6.11 | Quarterly Inspection | 1742 | BOKARO DEPOT | All officers to be made aware of location facilities. Proper maintenance to be ensured | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153841 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153841 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153841 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153841 |  | AUD-2026-09-2000017506ACN-2026-09-4000153841 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12QUARTERLY INSPECTION | ACN-2026-09-4000153842 | Open |  |  | Driveway near front road , infront of bay no 1 has caved in , exposing underground drain below and reinforcements | 6.12 | Quarterly Inspection | 1742 | BOKARO DEPOT | The driveway to be repaired immediately | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153842 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153842 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153842 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153842 |  | AUD-2026-09-2000017506ACN-2026-09-4000153842 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13QUARTERLY INSPECTION | ACN-2026-09-4000153843 | Open |  |  | Pontoon 17 and 21 of Tank 102 were check and found proper. Formation of mugs observed in patches inside foam dam | 6.13 | Quarterly Inspection | 1742 | BOKARO DEPOT | Mugs to be cleaned to prevent rusting of roofplates inside foam dam | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153843 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153843 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153843 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153843 |  | AUD-2026-09-2000017506ACN-2026-09-4000153843 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14QUARTERLY INSPECTION | ACN-2026-09-4000153844 | Open |  |  | Last date of testing and testing pressure not mentioned on PV vents of Tank 102, neither are there any identification marks of these vents | 6.14 | Quarterly Inspection | 1742 | BOKARO DEPOT | PV vents to be numbered, testing pressure , last date and next date of testing to be painted on PV vents | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153844 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153844 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153844 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153844 |  | AUD-2026-09-2000017506ACN-2026-09-4000153844 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-09-4000153845 | Open |  |  | Tank 102 and 201 were gauged. Following were the observations: Tank 102: Ref ht as per TAS 1405.5 cm, Observed: 1405.5 cm. Gross dip: 546.1 cm (TAS), observed: 546.1 cm, water dip (TAS): nil. Observed: 4 cm, Temp (TAS): 30.6 Deg cent, Observed: 30.5 Deg Cent, Density @15 Deg: 739.9 (TAS), Observed: 739.3 Tank 201: Ref ht as per TAS 1314.4 cm, Observed: 1314.4 cm. Gross dip: 308.3 cm (TAS),observed: 308.2 cm, water dip (TAS): nil, observed: nil. Temp (TAS): 29.8 Deg cent, Observed: 31 Deg Cent, Density @15 Deg: 827.7 (TAS), Observed: 827.6 | 6.15 | Quarterly Inspection | 1742 | BOKARO DEPOT | Corrective action to be taken on water dip of Tank 201 | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153845 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153845 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153845 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153845 |  | AUD-2026-09-2000017506ACN-2026-09-4000153845 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16QUARTERLY INSPECTION | ACN-2026-09-4000153846 | Open |  |  | SOP of operation in scrap area found missing | 6.16 | Quarterly Inspection | 1742 | BOKARO DEPOT | SOP to be displayed | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153846 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153846 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153846 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153846 |  | AUD-2026-09-2000017506ACN-2026-09-4000153846 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-09-4000153847 | Open |  |  | Integrity/ leakproofness of Sample thief lid was checked. Found the same ok. Sampling thief is inserted with the help of a rope. However, there is no graduation or making on the rope to know the level to which the sample container has been lowered | 6.17 | Quarterly Inspection | 1742 | BOKARO DEPOT | Sample thief to be inserted and taken to the desired level using gaduated/ marked rope/ tape | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153847 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153847 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153847 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153847 |  | AUD-2026-09-2000017506ACN-2026-09-4000153847 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-09-4000153848 | Open |  |  | High qty of misc MS scraps found kept in scrap yard | 6.18 | Quarterly Inspection | 1742 | BOKARO DEPOT | The scraps are to be disposed off immediately | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153848 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153848 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153848 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153848 |  | AUD-2026-09-2000017506ACN-2026-09-4000153848 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-09-4000153849 | Open |  |  | There are no field phones or hand sirens around scrap yard to declare any emergency | 6.19 | Quarterly Inspection | 1742 | BOKARO DEPOT | Corrective action to be taken | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000153849 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000153849 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000153849 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000153849 |  | AUD-2026-09-2000017506ACN-2026-09-4000153849 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-09-4000154350 | Open |  |  | Walkie talkies are being used in different frequencies, making it difficult to communicate via walkie talkies | 6.20 | Quarterly Inspection | 1742 | BOKARO DEPOT | Loaction to ensure communication in a common channel to avoid mis communication. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154350 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154350 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154350 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154350 |  | AUD-2026-09-2000017506ACN-2026-09-4000154350 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21QUARTERLY INSPECTION | ACN-2026-09-4000154351 | Open |  |  | During fire drill, one of the two Rescue team leaders reached site in normal shoes | 6.21 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to be in propoer uniform at all times. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154351 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154351 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154351 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154351 |  | AUD-2026-09-2000017506ACN-2026-09-4000154351 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-09-4000154352 | Open |  |  | There was no clear communication on exact location of fire for 2nd place of emergency and fire figthing was left to imagination | 6.22 | Quarterly Inspection | 1742 | BOKARO DEPOT | Loaction to ensure communication in a common channel to avoid mis communication. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154352 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154352 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154352 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154352 |  | AUD-2026-09-2000017506ACN-2026-09-4000154352 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23QUARTERLY INSPECTION | ACN-2026-09-4000154353 | Open |  |  | There was inordinate delay in making the key of scrap yard reach site | 6.23 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to respond in time for the emergency situation. Roles and responsibility to be clearly defined. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154353 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154353 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154353 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154353 |  | AUD-2026-09-2000017506ACN-2026-09-4000154353 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24QUARTERLY INSPECTION | ACN-2026-09-4000154354 | Open |  |  | All clear was declared before head count and from head count it was not clear, whether, all those were supposed to be inside, were indeed hale and hearty after the drill. | 6.24 | Quarterly Inspection | 1742 | BOKARO DEPOT | Required procredural declaration to be informed and made aware to the concerned . | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154354 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154354 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154354 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154354 |  | AUD-2026-09-2000017506ACN-2026-09-4000154354 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25QUARTERLY INSPECTION | ACN-2026-09-4000154355 | Open |  |  | Though, double contingency location, 2nd teams of each group were not identified properly. | 6.25 | Quarterly Inspection | 1742 | BOKARO DEPOT | Different teams to assemble and line up seperately for briefing | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154355 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154355 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154355 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154355 |  | AUD-2026-09-2000017506ACN-2026-09-4000154355 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26QUARTERLY INSPECTION | ACN-2026-09-4000154356 | Open |  |  | A meeting was held with transporters of the location , where VTS violations, monitoring of violations,ITDG actions, status of toll gate setting, purging of old claims, requirement of timely submission of claims, concept of consortium outlets, etc. were discussed.16 transporters took part in the meeting | 6.26 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to maintian regualr meeting a being done. | SOD | Marketing | PZR | 2026-09-20 |  | 8 |  | S2 | F4 | 2026-09-20 | AUD-2026-09-2000017506ACN-2026-09-4000154356 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154356 | 2026-09-19 10:00 | 30.3372 | 384 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154356 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154356 |  | AUD-2026-09-2000017506ACN-2026-09-4000154356 | 21 |  | 27 | 80 | 1 | 1 | 55
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27QUARTERLY INSPECTION | ACN-2026-09-4000154357 | Open |  |  | A CSA training involving 28 CSA was conducted. Safety precautions during unloading of TTs, operation of DCP and CO2 extinguishers, types of extinguishers and fires, etc. were explained thru class room and field training. Practical demonstration and operation of extinguishers by the CSAs was also done | 6.27 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to maintian regualr trainings as being done. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154357 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154357 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154357 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154357 |  | AUD-2026-09-2000017506ACN-2026-09-4000154357 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.29QUARTERLY INSPECTION | ACN-2026-09-4000154358 | Open |  |  |  | 6.29 | Quarterly Inspection | 1742 | BOKARO DEPOT | XX | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154358 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154358 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154358 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154358 |  | AUD-2026-09-2000017506ACN-2026-09-4000154358 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.30QUARTERLY INSPECTION | ACN-2026-09-4000154359 | Open |  |  | Contract labour register was not properly maintained. | 6.30 | Quarterly Inspection | 1742 | BOKARO DEPOT | Blank space between the daily entries. Can be misused by entry at a later day. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154359 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154359 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154359 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154359 |  | AUD-2026-09-2000017506ACN-2026-09-4000154359 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.31QUARTERLY INSPECTION | ACN-2026-09-4000154360 | Open |  |  |  | 6.31 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location is advised to do briefing to all the personal entering the premises. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154360 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154360 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154360 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154360 |  | AUD-2026-09-2000017506ACN-2026-09-4000154360 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.32QUARTERLY INSPECTION | ACN-2026-09-4000154361 | Open |  |  | Details on display board at entry | 6.32 | Quarterly Inspection | 1742 | BOKARO DEPOT | Found OK. Details updated with current details. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154361 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154361 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154361 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154361 |  | AUD-2026-09-2000017506ACN-2026-09-4000154361 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.33QUARTERLY INSPECTION | ACN-2026-09-4000154362 | Open |  |  | Ethanol register entries Signature of security and officer was not present on the register. | 6.33 | Quarterly Inspection | 1742 | BOKARO DEPOT | Security personal was advised to sign and get the signature from officers timely. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154362 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154362 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154362 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154362 |  | AUD-2026-09-2000017506ACN-2026-09-4000154362 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.34QUARTERLY INSPECTION | ACN-2026-09-4000154363 | Open |  |  |  | 6.34 | Quarterly Inspection | 1742 | BOKARO DEPOT | Security personal was advised to get the signature from officers timely. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154363 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154363 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154363 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154363 |  | AUD-2026-09-2000017506ACN-2026-09-4000154363 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.35QUARTERLY INSPECTION | ACN-2026-09-4000154364 | Open |  |  | Bihourly density registry and display at gantry 2. Density register and display not available. | 6.35 | Quarterly Inspection | 1742 | BOKARO DEPOT | Density register and display to be made available at all times. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154364 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154364 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154364 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154364 |  | AUD-2026-09-2000017506ACN-2026-09-4000154364 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.36QUARTERLY INSPECTION | ACN-2026-09-4000154365 | Open |  |  | Gantry TT checking | 6.36 | Quarterly Inspection | 1742 | BOKARO DEPOT | JH06J2808 / JH09A21413 | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154365 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154365 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154365 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154365 |  | AUD-2026-09-2000017506ACN-2026-09-4000154365 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.37QUARTERLY INSPECTION | ACN-2026-09-4000154366 | Open |  |  | Fire extinguisher at bays. No fire extinguisher has sticker on its testing dates. | 6.37 | Quarterly Inspection | 1742 | BOKARO DEPOT | Safety officer was asked to speak to the vendor and issue stickers for the fire cylinders | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154366 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154366 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154366 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154366 |  | AUD-2026-09-2000017506ACN-2026-09-4000154366 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.38QUARTERLY INSPECTION | ACN-2026-09-4000154367 | Open |  |  | SOP Boards at gantry. Boards installed were dirty. | 6.38 | Quarterly Inspection | 1742 | BOKARO DEPOT | All boards to be cleaned by the location. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154367 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154367 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154367 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154367 |  | AUD-2026-09-2000017506ACN-2026-09-4000154367 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.39QUARTERLY INSPECTION | ACN-2026-09-4000154368 | Open |  |  | Ethanol blending at gantry bays | 6.39 | Quarterly Inspection | 1742 | BOKARO DEPOT | OK. EBP 18.5% (2808, 1413) | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154368 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154368 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154368 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154368 |  | AUD-2026-09-2000017506ACN-2026-09-4000154368 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.40QUARTERLY INSPECTION | ACN-2026-09-4000154369 | Open |  |  | Density display board at gantry 1. Not updated. | 6.40 | Quarterly Inspection | 1742 | BOKARO DEPOT | Density display board to be updated in every 2 hours. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154369 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154369 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154369 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154369 |  | AUD-2026-09-2000017506ACN-2026-09-4000154369 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.41QUARTERLY INSPECTION | ACN-2026-09-4000154370 | Open |  |  | Gantry cleanness. Plastic bottles stacked in dustbins. | 6.41 | Quarterly Inspection | 1742 | BOKARO DEPOT | Gantry officers have been asked to get the wate removed on regularly basis. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154370 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154370 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154370 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154370 |  | AUD-2026-09-2000017506ACN-2026-09-4000154370 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.42QUARTERLY INSPECTION | ACN-2026-09-4000154371 | Open |  |  | Safety belt/ Harness at gantry. 1 bay each at gantry 1 and 2 had one safety harness missing. | 6.42 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to arrange for new safety belts immediately. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154371 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154371 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154371 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154371 |  | AUD-2026-09-2000017506ACN-2026-09-4000154371 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.43QUARTERLY INSPECTION | ACN-2026-09-4000154372 | Open |  |  |  | 6.43 | Quarterly Inspection | 1742 | BOKARO DEPOT | Security and safety officer has been asked to comply with safety checks. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154372 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154372 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154372 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154372 |  | AUD-2026-09-2000017506ACN-2026-09-4000154372 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.44QUARTERLY INSPECTION | ACN-2026-09-4000154373 | Open |  |  | Fire pump house (jockey pump noise). Swing check valve make loud noise. | 6.44 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location asked to replace the noisy Valve. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154373 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154373 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154373 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154373 |  | AUD-2026-09-2000017506ACN-2026-09-4000154373 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.45QUARTERLY INSPECTION | ACN-2026-09-4000154374 | Open |  |  | TT unloading on BAY. One ethanol TT had placed earthing clip at painted portion | 6.45 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location has been asked to communicate all transporters to provide earthing strips on the middle part of the tanker. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154374 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154374 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154374 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154374 |  | AUD-2026-09-2000017506ACN-2026-09-4000154374 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.46QUARTERLY INSPECTION | ACN-2026-09-4000154375 | Open |  |  | PM activity. Tank top inspection Goose neck did not have any bonding | 6.46 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to get the bonding done immediately. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154375 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154375 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154375 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154375 |  | AUD-2026-09-2000017506ACN-2026-09-4000154375 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.47QUARTERLY INSPECTION | ACN-2026-09-4000154376 | Open |  |  | Night patrol of guards | 6.47 | Quarterly Inspection | 1742 | BOKARO DEPOT | Patrol found OK. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154376 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154376 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154376 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154376 |  | AUD-2026-09-2000017506ACN-2026-09-4000154376 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.48QUARTERLY INSPECTION | ACN-2026-09-4000154377 | Open |  |  | Strainer cleaning | 6.48 | Quarterly Inspection | 1742 | BOKARO DEPOT | Found OK | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154377 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154377 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154377 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154377 |  | AUD-2026-09-2000017506ACN-2026-09-4000154377 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.49QUARTERLY INSPECTION | ACN-2026-09-4000154378 | Open |  |  | CCTV cameras 5 non operation out of 99 cameras. | 6.49 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location was asked to get all the cameras operational immediately. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154378 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154378 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154378 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154378 |  | AUD-2026-09-2000017506ACN-2026-09-4000154378 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.50QUARTERLY INSPECTION | ACN-2026-09-4000154379 | Open |  |  | LUX inspection was carried out, found inadequate at TLF Entry Main road : 17.5 against 20 Tank Farm 2st MS Tank : 56.8 againt 60 Tank Farm HSD, Ethanol, SKO: 56.3 against 60 | 6.50 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to install new lights and increase illumination. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154379 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154379 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154379 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154379 |  | AUD-2026-09-2000017506ACN-2026-09-4000154379 | 21 |  | 27 | 80 | 1 | 1 | 59
[5 empty] | Q2 SMA BOKARO | 2026-09-19 08:00 | AUD-2026-09-2000017506 | 2026-09-18 03:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.51QUARTERLY INSPECTION | ACN-2026-09-4000154380 | Open |  |  | 1st Fire senario at Black Oil Tank Farm observation: 1. Response time to operate monitor was slow. 2. Foam Operated and found ok 3. Sprinklers found OK of the nearby tank. 4. Other team members to be more active. 5. Communication to improve. 6. Monitor operator was spraying at the wrong position | 6.51 | Quarterly Inspection | 1742 | BOKARO DEPOT | Location to ensure communication through a common channel. All teams to coordinate for proper fire fighting. Team to respond to emergency situation more actively and promptly. | SOD | Marketing | PZR | 2026-10-17 |  | 8 |  | S2 | F4 | 2026-10-17 | AUD-2026-09-2000017506ACN-2026-09-4000154380 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017506ACN-2026-09-4000154380 | 2026-09-19 10:00 | 30.3372 | 411 | >20 | AUD-2026-09-2000017506 - ACN-2026-09-4000154380 | 532 | 8294 | 21 | 8294 | 2 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017506ACN-2026-09-4000154380 |  | AUD-2026-09-2000017506ACN-2026-09-4000154380 | 21 |  | 27 | 80 | 1 | 1 | 59
KUSHAGRA VASHISHTH | 2026-09-25 |  |  | All points highlighted points complied. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144681 | Closed | KUSHAGRA VASHISHTH | 2026-09-25 | 1) 1 inch line to be replaced with TSV near Ethanol PH. 2) Mobile Foam Trolley found in unusable condition near TK-16/17. It is also blocking the road. 3) Foam Pourer riser in TK17 to repainted. 4) Rusting observed on loading arms in TT Gantry. 5) There is water sharing arrangement with BPCL. Location to (a) take water from BPCL and note down all challenges faced (b) location should sign an MOU with BPCL for water sharing and also develop an SOP for the same. (6) Patch work to be done on TK-1 (6) Locations M&R officer to study load consumption with breakup for all major power consuming equipment day wise for a week. (7) Orientation of CCTV-27 (TT Gantry) to be corrected. | 6.12 | M&R Jobs | 1278 | JODHPUR TERMINAL | Pls ensure pointwise compliance | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144681 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144681 | 2026-09-25 20:45 | 23.8893 | 389 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144681 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144681 | AUD-2026-07-2000015346ACN-2026-07-4000144681 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-25 |  |  | Mr Akhilesh Bijalwan-Chief Manager - Product Supplies (North) has confirmed on his visit on 15.09.26 reviewing the lube stock available at location. Action for liquidation of lubes will be taken in coordination with Lubes Dept. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144680 | Closed | KUSHAGRA VASHISHTH | 2026-09-25 | Old Lubes are required to be liquidated | 6.11 | Liquidation of slow moving Lube | 1278 | JODHPUR TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is already done by Mr. darpan. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-08-31 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-31 | AUD-2026-07-2000015346ACN-2026-07-4000144680 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144680 | 2026-09-25 20:45 | 23.8893 | 389 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144680 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144680 | AUD-2026-07-2000015346ACN-2026-07-4000144680 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUSHAGRA VASHISHTH | 2026-09-25 | KUSHAGRA VASHISHTH | 2026-09-17 | Monthly inventory of all additives has been monitored, with physical stock reconciled against book stock and records maintained. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144678 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.9 | Additive stock monitoring | 1278 | JODHPUR TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144678 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144678 | 2026-09-25 20:45 | 23.8893 | 389 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144678 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144678 | AUD-2026-07-2000015346ACN-2026-07-4000144678 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-25 | KUSHAGRA VASHISHTH | 2026-09-07 | Monthly monitoring of RTGP is being carried out by the Security team, physical register and HP gate pass portal reconciliation being carried out. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144677 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | Pending RTGP record (month wise) to be parepared on RTGP register itself. List of open RTGP as per security vs list of open RTGP asper online gate pass portal | 6.8 | RTGP monitoring | 1278 | JODHPUR TERMINAL | Monthly monitoring of RTGP by security to be done | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144677 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144677 | 2026-09-25 20:45 | 23.8893 | 389 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144677 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144677 | AUD-2026-07-2000015346ACN-2026-07-4000144677 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
DINKAR SUMIT | 2026-09-25 | KUMAR GOPESH | 2026-09-23 | UG06 -Not having product in that & UG07 Radar installed as 23.09.2026 .As advised by GM (O&D), Jaipur Zone, this point is being closed. The same observation has been recorded in another audit dated 08.09.2026 to 09.09.2026 Sr Manager audit , vide Audit No. AUD-2026-09-200017605. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127337 | Closed | KUMAR GOPESH | 2026-09-23 | Checked for Jan 2026. There were 33 cases out of 383 where reco is carried out using manual dips. Most of the case pertains to UG6 and UG7. Location has floated tender for radar systen both the underground tanks | 3.8 | Auto vs Manual reconciliation checked | 1281 | AJMER TERMINAL | Both these tanks have to be fitted with radar for auto gauging. | SOD | Marketing | NWF | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-03-2000011239ACN-2026-03-4000127337 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127337 | 2026-09-09 17:45 | 40.0143 | 389 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127337 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127337 | AUD-2026-03-2000011239ACN-2026-03-4000127337 | 21 | 21 | 26 | 80 | 0 | 0 | 48 | 56
DINKAR SUMIT | 2026-09-25 | KUMAR GOPESH | 2026-09-23 | The Transportation officer taken follwup as per notification and contacted NAHI Tolls Plazzas for discount and at some plazza its formalities complited and discount given for few he is taking follwups with authrities giving letteres for dicount .As advised by GM (O&D), Jaipur Zone, this point is being closed. The same observation has been recorded in another audit dated 08.09.2026 to 09.09.2026 , vide Audit No. AUD-2026-09-200017605. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127345 | Closed | KUMAR GOPESH | 2026-09-23 | Discounted toll to be implemented | 6.7 | Discounted toll | 1281 | AJMER TERMINAL | There is Gazette notification. Email shared with location on discounted toll concept. Pls implement | SOD | Marketing | NWF | 2026-03-31 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011239ACN-2026-03-4000127345 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127345 | 2026-09-09 17:45 | 40.0143 | 389 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127345 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127345 | AUD-2026-03-2000011239ACN-2026-03-4000127345 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 56
DINKAR SUMIT | 2026-09-25 | KUMAR GOPESH | 2026-09-23 | Project under progress and work pending tendering also in under process for some parts ,,As advised by GM (O&D), Jaipur Zone, this point is being closed. The same observation has been recorded in another audit dated 08.09.2026 to 09.09.2026 Sr Manager audit , vide Audit No. AUD-2026-09-200017605. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127339 | Closed | KUMAR GOPESH | 2026-09-23 | Yes reviewed. Bay 12 to be converted to mixed loading. | 4.3 | Project progress reviewed | 1281 | AJMER TERMINAL | Pls complete the project by 30.04.2026 | SOD | Marketing | NWF | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127339 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127339 | 2026-09-09 17:45 | 40.0143 | 389 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127339 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127339 | AUD-2026-03-2000011239ACN-2026-03-4000127339 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 56
DINKAR SUMIT | 2026-09-25 | KUMAR GOPESH | 2026-09-23 | Necessary follow-up has been initiated with the Lube Department for the urgent liquidation of the balance stock lying at the location. Communications were sent via email dated 27 August 2026 and 7 September 2026. Sampling has been completed at Techanical QC jaipur ; however, the Lube Department has not yet lifted the stock. As advised by GM (O&D), Jaipur Zone, this point is being closed. Thesame observation has been recorded in another audit dated 08.09.2026, vide Audit No. AUD-2026-09-200017605. | AUDIT UPLOAD IN SAP | 2026-01-27 19:00 | AUD-2026-03-2000011239 | 2026-01-27 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000127346 | Closed | KUMAR GOPESH | 2026-09-23 | Old Lubes are required to be liquidated | 6.8 | Liquidation of slow moving Lube | 1281 | AJMER TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is already done by Mr. darpan. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-30 | AUD-2026-03-2000011239ACN-2026-03-4000127346 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011239ACN-2026-03-4000127346 | 2026-09-09 17:45 | 40.0143 | 389 | >20 | AUD-2026-03-2000011239 - ACN-2026-03-4000127346 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011239ACN-2026-03-4000127346 | AUD-2026-03-2000011239ACN-2026-03-4000127346 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 56
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153413 | Open |  |  | A.Dip Elimination: Dip elimination is pending and in progress B.NPCB Projects due as on 30.09.2026: 1. SWZ_HUBLI_SOP BOARDS & SAFETY 2. SWZ_HUBLI_BIODIESEL CLOSED LOOP LINE 3. PCC Below hydrant line in TT Parking 4. Dyke Imperviousness Jobs in Dyke 1 5. FLPHooters with visual indicator dyke 3 6. DC Based lighting jobs at Hubli New IRD 7. Replacement of Sprinkler & Foam Lines 8. Closed Loop Hydrant Line near Ethanol UL 9. Bluru_Hubli Safety PLC UPS Replacement 10. BZ_HUBLI_SIL RADAR REPLACEMENT 11. BZ_HUBLI_TAS_NOVEX_INTG | 1.3 | Pending issues reviewed | 1800 | HUBLI DEPOT | 1. Location to expedite and initiate dip elimination file note at the earliest. 2. To expediate the closure of 11 AR's as per respective AR target date, last AR closing date is 31/03/2028. | SOD | Marketing | SWZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017610ACN-2026-09-4000153413 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153413 | 2026-09-11 19:30 | 37.9413 | 576 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153413 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153413 |  | AUD-2026-09-2000017610ACN-2026-09-4000153413 | 21 |  | 27 | 80 | 18 | 18 | 83
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153414 | Open |  |  | 11 pending point of total 26 points of inspection in last senior management inspection. | 1.4 | Earlier action points status checked | 1800 | HUBLI DEPOT | Pending observations to be complied at the earliest | SOD | Marketing | SWZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017610ACN-2026-09-4000153414 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153414 | 2026-09-11 19:30 | 37.9413 | 486 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153414 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153414 |  | AUD-2026-09-2000017610ACN-2026-09-4000153414 | 21 |  | 27 | 80 | 18 | 18 | 70
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153415 | Open |  |  | 1. CAMC of VRU and TAS Process & TFMS required. | 1.5 | HQO / Zonal support required identified | 1800 | HUBLI DEPOT | To collect OEM offer for CAMC to HQO for immediate placement of PO | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017610ACN-2026-09-4000153415 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153415 | 2026-09-11 19:30 | 37.9413 | 394 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153415 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153415 |  | AUD-2026-09-2000017610ACN-2026-09-4000153415 | 21 |  | 27 | 80 | 18 | 18 | 57
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153416 | Open |  |  | a) HSD tankage is inadequate b) Location LUX level improvement | 1.8 | Improvement plans discussed | 1800 | HUBLI DEPOT | 1) Proposal to be sent to Zone 2) Proposal to be sent to Zone | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017610ACN-2026-09-4000153416 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153416 | 2026-09-11 19:30 | 37.9413 | 394 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153416 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153416 |  | AUD-2026-09-2000017610ACN-2026-09-4000153416 | 21 |  | 27 | 80 | 18 | 18 | 57
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153417 | Open |  |  | Lux level checked on 11.09.2026. Below Lux level found: Ethanol Unloading Pump House - 15 & 16 against 100 Secondary Road near HVLR number 4: 32 against 10 required Gantry: 82, 68 against 60 Tank Manifold: 35 against 60 Fire Pump house: 179, 280 & 133 against 100 Sealing Bay: 132 against 60 required. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1800 | HUBLI DEPOT | Lux level to be improved at Tank Farm Area | SOD | Marketing | SWZ | 2027-03-31 |  | 8 |  | S4 | F2 | 2027-03-31 | AUD-2026-09-2000017610ACN-2026-09-4000153417 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153417 | 2026-09-11 19:30 | 37.9413 | 576 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153417 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153417 |  | AUD-2026-09-2000017610ACN-2026-09-4000153417 | 21 |  | 27 | 80 | 18 | 18 | 83
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153418 | Open |  |  | CCTV System Status: 1 cameras out of 46 are not operational. | 2.6 | CCTV functioning checked | 1800 | HUBLI DEPOT | The 1 non-working camera to be made functional at earliest. | SOD | Marketing | SWZ | 2026-11-30 |  | 8 |  | S4 | F2 | 2026-11-30 | AUD-2026-09-2000017610ACN-2026-09-4000153418 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153418 | 2026-09-11 19:30 | 37.9413 | 455 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153418 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153418 |  | AUD-2026-09-2000017610ACN-2026-09-4000153418 | 21 |  | 27 | 80 | 18 | 18 | 65
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153419 | Open |  |  | VA is enabled on 38 cameras, with 36 cameras functioning normally. The remaining 2 non-functional cameras are not available for VA monitoring | 2.7 | VA alerts checked / analysed | 1800 | HUBLI DEPOT | The VA of 2 non-working cameras are to be made functional after correction of the cameras. | SOD | Marketing | SWZ | 2026-11-30 |  | 8 |  | S4 | F2 | 2026-11-30 | AUD-2026-09-2000017610ACN-2026-09-4000153419 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153419 | 2026-09-11 19:30 | 37.9413 | 455 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153419 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153419 |  | AUD-2026-09-2000017610ACN-2026-09-4000153419 | 21 |  | 27 | 80 | 18 | 18 | 65
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153420 | Open |  |  | TTs fittings are being checked regularly and any deviation are being reported to transporter for compliance. | 3.1 | TT fittings & discipline checked | 1800 | HUBLI DEPOT | Location to take appropriate action to avoid any deviation from compliance of statutory. Location to check all TTs with PESO approved tank dimensions and action to be initiated if any violation is observed. | SOD | Marketing | SWZ | 2026-11-30 |  | 8 |  | S4 | F2 | 2026-11-30 | AUD-2026-09-2000017610ACN-2026-09-4000153420 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153420 | 2026-09-11 19:30 | 37.9413 | 455 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153420 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153420 |  | AUD-2026-09-2000017610ACN-2026-09-4000153420 | 21 |  | 27 | 80 | 18 | 18 | 65
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153421 | Open |  |  | Yes records maintained. However, Hose for ethanol unloading need to be replaced also Lux level in Ethanol gantry need to be improved. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1800 | HUBLI DEPOT | Location to replace Hose pipe of the Ethanol unloading gantry and LUX level need to be improved. | SOD | Marketing | SWZ | 2026-09-15 |  | 4 |  | S2 | F2 | 2026-09-15 | AUD-2026-09-2000017610ACN-2026-09-4000153421 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153421 | 2026-09-11 19:30 | 37.9413 | 379 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153421 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153421 |  | AUD-2026-09-2000017610ACN-2026-09-4000153421 | 21 |  | 27 | 80 | 18 | 18 | 55
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153422 | Open |  |  | House keeping to be improved | 3.15 | Housekeeping & PPE usage checked | 1800 | HUBLI DEPOT | 1. Ethanol gantry housekeeping need to be improved. 2. Housekeeping of TT Gantry to be improved. | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017610ACN-2026-09-4000153422 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153422 | 2026-09-11 19:30 | 37.9413 | 394 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153422 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153422 |  | AUD-2026-09-2000017610ACN-2026-09-4000153422 | 21 |  | 27 | 80 | 18 | 18 | 57
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153423 | Open |  |  | Old Earthpits need to be dismantled. | 3.16 | Earth pits / boundary / vegetation control checked | 1800 | HUBLI DEPOT | Location to ensure old earthpit dismantles and disposed. | SOD | Marketing | SWZ | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017610ACN-2026-09-4000153423 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153423 | 2026-09-11 19:30 | 37.9413 | 409 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153423 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153423 |  | AUD-2026-09-2000017610ACN-2026-09-4000153423 | 21 |  | 27 | 80 | 18 | 18 | 59
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153424 | Open |  |  | Audit compliance review and found satisfactory. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1800 | HUBLI DEPOT | Location to expediate the closure of Pending OISD/MDSA/SSA points.OISD pending point - 9, MDSA pending observations: 18 and SSA pending points: 18 | SOD | Marketing | SWZ | 2027-03-31 |  | 8 |  | S4 | F2 | 2027-03-31 | AUD-2026-09-2000017610ACN-2026-09-4000153424 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153424 | 2026-09-11 19:30 | 37.9413 | 576 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153424 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153424 |  | AUD-2026-09-2000017610ACN-2026-09-4000153424 | 21 |  | 27 | 80 | 18 | 18 | 83
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153425 | Open |  |  | All operational areas were inspected and observed to be satisfactory 1. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1800 | HUBLI DEPOT | Grating near foam shed 14 need to be provided. Tank 10D need to be painted also board of Tank 10D need to be installaed. Switch of the light of foam shed need to be replaced. | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017610ACN-2026-09-4000153425 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153425 | 2026-09-11 19:30 | 37.9413 | 425 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153425 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153425 |  | AUD-2026-09-2000017610ACN-2026-09-4000153425 | 21 |  | 27 | 80 | 18 | 18 | 61
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153426 | Open |  |  | Reviewed progress of current projects related to Hydrant Line, Dyke work etc and found satisfactory. 7 project having deadline as 30.09.2026 need to be closed within timeline. | 4.3 | Project progress reviewed | 1800 | HUBLI DEPOT | To complete the projects within the agreed timelines | SOD | Marketing | SWZ | 2027-12-31 |  | 6 |  | S3 | F2 | 2027-12-31 | AUD-2026-09-2000017610ACN-2026-09-4000153426 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153426 | 2026-09-11 19:30 | 37.9413 | 851 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153426 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017610ACN-2026-09-4000153426 |  | AUD-2026-09-2000017610ACN-2026-09-4000153426 | 21 |  | 27 | 80 | 18 | 18 | 122
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153427 | Open |  |  | Location already scrapped 10.9 MT of misc. scrap having value of around 6 lakhs. For remaining, one lot has been already auctioned and sold to party. Vendors are yet to uplift the scrap. RFD to be initiated for bitumen tank misc scraps and other remaining items | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1800 | HUBLI DEPOT | Location to initiate RFD of the remaining items immediately. | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017610ACN-2026-09-4000153427 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153427 | 2026-09-11 19:30 | 37.9413 | 425 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153427 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153427 |  | AUD-2026-09-2000017610ACN-2026-09-4000153427 | 21 |  | 27 | 80 | 18 | 18 | 61
[5 empty] | HUBLI IRD Q2 LOCATION VISIT | 2026-09-11 19:30 | AUD-2026-09-2000017610 | 2026-09-09 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153428 | Open |  |  | Some TTS were found without branding TT no:KA22AA0727, KA25AC2072. | 6.1 | TT Branding | 1800 | HUBLI DEPOT | Branding of 100% TTs to be ensured | SOD | Marketing | SWZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017610ACN-2026-09-4000153428 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017610ACN-2026-09-4000153428 | 2026-09-11 19:30 | 37.9413 | 425 | >20 | AUD-2026-09-2000017610 - ACN-2026-09-4000153428 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017610ACN-2026-09-4000153428 |  | AUD-2026-09-2000017610ACN-2026-09-4000153428 | 21 |  | 27 | 80 | 18 | 18 | 61
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150000 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Day-to-day operational activities were reviewed. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1656 | DURGAPUR DEPOT | Location to control TDG violation, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration (This is a repeat point vis-a-vis last quarterly audit). Spots identified where multiple TTs are stopping unauthorisedly to be intimated to the police station under which the location is identified. Regular feedback to be shared with zone on action taken on such cases. Multiple Tank Trucks are being taken inside the depot for loading simultanesously creating a jam like situationat TT IN Gate. Open Sand was lying near TT locking platform of TT Out gate, open wire was also lying there. (This is a repeat observation vis-a-vis last quarterly audit). | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 10 | EMERGENCY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150000 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150000 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150000 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150000 | AUD-2026-08-2000017103ACN-2026-08-4000150000 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150001 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Individual review of officer carried out with respect to KPI and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1656 | DURGAPUR DEPOT | Officers were advised to have hand on exercise for operating all the fire fighting equipment. As of July'26, loss of 40 KL is booked in Ethanol which is abnormally high. (Repeat Point). Transporters and DCTs to be taken on board for conversion of their TTs to bottom loading (Repeat point) | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150001 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150001 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150001 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150001 | AUD-2026-08-2000017103ACN-2026-08-4000150001 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150002 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | 1. M&I Checklist as per the SOP shared by HPPL officer to be maintained and shared with zone periodically (This is a repeat point vis-a-vis last quarterly audit). 2. 34 no. of open MDSA Points of FY 25-26 to be complied and closed 3. 9 no. of Sr. Management points to be complied and closed 4. Regular E M Lock checking by LIC Master key and records to be maintained 5. Adequate E M Locks & Key inventory at location to be maintained 6. EBMS 20% blending check at TT Gantry to be ensured and records to be maintained 7. Regular EBMS/ Ethanol Sample to be sent to Kolkata/ Haldia Lab for sample testing and records to be maintained. 8. Dry Sand Stoaragetank near Eye Wash (TT Area) is lying empty. (Repeat Point) 9. EBMS Sample Failure case w.r.t TT no. WB19M2560 | 1.3 | Pending issues reviewed | 1656 | DURGAPUR DEPOT | Expeditious action / compliance to be taken | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150002 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150002 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150002 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150002 | AUD-2026-08-2000017103ACN-2026-08-4000150002 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150003 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | During last visit, it was advised to have good housekeeping Location had improved significantly w.r.t last visit however following were observed : 1. Surprise fire drill has not been conducted by LIC in last 3 months 2. Open MOC still not closed 3. Gantry Permissive on account of water tank reading not coming in TAS 4. Fire Engine was found kept in local mode. Upon enquiry, it was givento understand that Jockey pump (Jockey is in Auto Mode) is unable to hold the water pressure and thus Fire Engine is getting started every time. LIC is advised to review the entire hydrant network and arrnage for early rectification of the possible passage of thewater due to whcih pressure is not being maintained. | 1.4 | Earlier action points status checked | 1656 | DURGAPUR DEPOT | Corrective action to be taken | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150003 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150003 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150003 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150003 | AUD-2026-08-2000017103ACN-2026-08-4000150003 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150004 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1656 | DURGAPUR DEPOT | 1. Location to upload the 100%TT dip checking data in SAP. Dip elimination FN to be processed at the earliest. (Repeat Point) 2. Location to ensure the recovery w.r.t VTS equipment charges 3. Location to monitor and take action line with ITDG for the deviations(route/ speed/ night halting etc). 4. All open Audit points to be closed 5. T4S Audit is due in Nov'26. All purchase activity to be done well in advance. 6. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 7. Manual allocation of TT in IMS to be minimised and records with justification to be maintained for all such cases. 8. EM lock handling and Monitoring : Part load must not be executed without prior approval of zonal O&D head, Post decantation OTP to be ensured, programming key usages to be ensured for all TT within a periodof max. 1 month. 9. All RTGPs to be reviewed periodically and closed 10. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL cases of scope change in any AR to be done without prior approval. | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 10 | EMERGENCY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150004 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150004 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150004 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150004 | AUD-2026-08-2000017103ACN-2026-08-4000150004 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150006 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | No Surprise fire drill conducted at location. As advised in last inspection, location has not prepared the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. (Repeat Point) | 2.1 | Fire drill conducted in last 6 months (surprise) | 1656 | DURGAPUR DEPOT | Location to ensure to complete all the fire scenario as per ERDMP in the mock drills. | SOD | Marketing | EZ | 2026-09-30 | OUTDATED OR COMPLEX SOPS | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-08-2000017103ACN-2026-08-4000150006 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150006 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150006 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150006 | AUD-2026-08-2000017103ACN-2026-08-4000150006 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150007 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Leakage and Fire from the ethanol tank truck delivery valve at ethanol unloading point was simulated following observations recorded : 1. TT Crew of the ethanol TT used DCP and was in very close proximity of the said TT. 2. ESD was operated by security guardat main gate 3. Nearest WCFM with ARAFFF foam was operated and carpet of white foam was there. 4. Main gate was chocked becasue of multiple no. of TT waiting in queue for their entry. This hinderence created resulted in obstruction of smooth movement of incoming emergency vehicle. 5. TT crew/ helper was found wearing safety harness belt at the Top of the incoming TT near TT locking platform. | 2.2 | Double contingency scenario simulated; observations recorded | 1656 | DURGAPUR DEPOT | All the observation and recommendation of the drill to be implemented in the next and subsequent drill | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150007 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150007 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150007 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150007 | AUD-2026-08-2000017103ACN-2026-08-4000150007 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Old Lights repaired | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150008 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Lux level checked : TT gantry : Required : 60 and observed : 170 Secondary roads : Required 10 and observed 7 at few places (Repeat Point) | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1656 | DURGAPUR DEPOT | It was advised to improve the lux levels on the secondary roads by repairing the old lights. | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150008 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150008 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150008 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150008 | AUD-2026-08-2000017103ACN-2026-08-4000150008 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Improved | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150009 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Security personnel were interrogated on night time preparedness on emergency and mitigation measures to be taken. The team was found to be well versed on the same. Night Inspection by DSO and LIC carried out and only gate entry records maintained. No report of night inspection maintained at location. (repeat Point) | 2.4 | Security alertness checked (night-halt / surprise checks) | 1656 | DURGAPUR DEPOT | Night alertness to be more strengthened. Frequency of Surprise night inspection to be increased, report to be maintained along withCCTV footage in the report. | SOD | Marketing | EZ | 2026-08-31 | POOR COMMUNICATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150009 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150009 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150009 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150009 | AUD-2026-08-2000017103ACN-2026-08-4000150009 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Improved and Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150010 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Location has total of 42 CCTV Camera and all of them were functional on the date of visit. | 2.6 | CCTV functioning checked | 1656 | DURGAPUR DEPOT | Security frisking at TT in gate and SOP adherence to be strengthened | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150010 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150010 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150010 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150010 | AUD-2026-08-2000017103ACN-2026-08-4000150010 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150011 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. CCTVs were not active over VA and all of them were down. It was given to understand that there is power back up issue of UPS and MCB use to get tripped every time whenever there is power disconnect. (Repeat Point) | 2.7 | VA alerts checked / analysed | 1656 | DURGAPUR DEPOT | Location to closely monitor and ensure to maintain the VA active all the time. | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150011 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150011 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150011 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150011 | AUD-2026-08-2000017103ACN-2026-08-4000150011 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150012 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Access control system found functional. It was noted that the VMS service is not operational. | 2.8 | Access control systems checked | 1656 | DURGAPUR DEPOT | VMS to be implemented. Nil case of visitors entry without VMS to be ensured | SOD | Marketing | EZ | 2026-08-31 | THIRD PARTY ERRORS | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150012 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150012 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150012 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150012 | AUD-2026-08-2000017103ACN-2026-08-4000150012 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150013 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Yes officer operated DCP | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1656 | DURGAPUR DEPOT | More hands on training on safety critical equipment to be acquired by all the officers | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150013 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150013 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150013 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150013 | AUD-2026-08-2000017103ACN-2026-08-4000150013 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150014 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | TT fitting check carried for TT no. JH10AO1528 and found satisfactory. Rear Crash Guard from left side for TT no. WB571551, WB29C0100 (Repeat point w.r.t other TTs.) Branding of TT no. WB39B9830 was not as per the standard. To be rectified. | 3.1 | TT fittings & discipline checked | 1656 | DURGAPUR DEPOT | Corrective action to be taken. | SOD | Marketing | EZ | 2026-08-31 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150014 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150014 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150014 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150014 | AUD-2026-08-2000017103ACN-2026-08-4000150014 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150021 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | MFM vs BCU totaliser comparison available at location. Remarks updated for in case of variation due to calibration, local loading, overrun etc. Dayend Totalizer report is not being signed by LIC regularly. Officer to take up with the TAS vendor immeiately upon variation found in MFM V/s BCU totaliser reading. | 3.11 | MFM vs BCU totalizer comparison checked | 1656 | DURGAPUR DEPOT | The SOP violation to be arrested and corrective procedure to be implemented | SOD | Marketing | EZ | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150021 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150021 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150021 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150021 | AUD-2026-08-2000017103ACN-2026-08-4000150021 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150022 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1656 | DURGAPUR DEPOT | LIC to review the critical alarms periodically and report if any abnormalities found. | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 10 | PROCESS SAFETY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150022 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150022 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150022 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150022 | AUD-2026-08-2000017103ACN-2026-08-4000150022 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150023 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1656 | DURGAPUR DEPOT | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-08-31 | INSTRUMENTATION OR ALARM FAILURES | 10 | ASSET INTEGRITY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150023 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150023 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150023 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150023 | AUD-2026-08-2000017103ACN-2026-08-4000150023 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150024 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Local loading record maintained at location. However following are the observations : 1. Location to take up with TAS vednor ifany abnormality found in the report. 2. Local loading to be done only for prover verification. In case of and top up of TT, approval from LIC to be obtained. | 3.14 | Local loading checks (if applicable) | 1656 | DURGAPUR DEPOT | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 10 | CONTRACTOR SAFETY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150024 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150024 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150024 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150024 | AUD-2026-08-2000017103ACN-2026-08-4000150024 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150025 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Housekeeping practice is found satisfactory. PPE usages to be strengthened. The main gate of TT entry was found partially block by officers CAR of visitors (Depot/ RO). It was advised to have NIL car parking in front of TT IN gate and TT to be parked at designated place only, Since complied. (Repeat Point) | 3.15 | Housekeeping & PPE usage checked | 1656 | DURGAPUR DEPOT | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 10 | CONTRACTOR SAFETY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150025 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150025 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150025 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150025 | AUD-2026-08-2000017103ACN-2026-08-4000150025 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150026 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Vegetation inside the depot was also under control EP was not tested on time and are overdue. Location failed to produce the EP testng reprot. This is a serious voilation w.r.t safety of man and machine inside depot. | 3.16 | Earth pits / boundary / vegetation control checked | 1656 | DURGAPUR DEPOT | Location to ensure that EPs are tested well within the time period. Further, all EPs to be tested in presence of Officer | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 10 | ASSET INTEGRITY | S2 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150026 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150026 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150026 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150026 | AUD-2026-08-2000017103ACN-2026-08-4000150026 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150027 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | MOC is being reviewed at zonal level on regular basis. 3 no. of open obsolete MOC not closed. (Repeat Point) | 3.17 | MOC status reviewed | 1656 | DURGAPUR DEPOT | Location to review the open MOC periodically and get the needful done for timely closure in system | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150027 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150027 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150027 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150027 | AUD-2026-08-2000017103ACN-2026-08-4000150027 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150028 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | OISD - NIL pending Point MDSA FY 25-26 - 34 pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1656 | DURGAPUR DEPOT | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S2 | F4 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150028 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150028 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150028 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150028 | AUD-2026-08-2000017103ACN-2026-08-4000150028 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150015 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Random checking of the dip for TT no. JH10A01528 post loading done and found marginally high in chamber no. 3. TT to be taken for reverification. There was difference in PL for 4 KL chamber no.3 for the TT no. JH10A01528 | 3.2 | Post-loading dip checks verified | 1656 | DURGAPUR DEPOT | Corrective action to be taken. | SOD | Marketing | EZ | 2026-08-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150015 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150015 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150015 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150015 | AUD-2026-08-2000017103ACN-2026-08-4000150015 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150016 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Review of VTS deviation done on regular basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC. Spots identified where multiple TTs are stopping unauthorisedly to be intimated to the police station under which thelocation is identified. Regular feedback to be shared with zone on action taken on such cases. | 3.3 | VTS deviations reviewed | 1656 | DURGAPUR DEPOT | Location is advised to create the secondary route wherever applicable and action to be taken as per ITDG wherever deemed fit. | SOD | Marketing | EZ | 2026-08-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | EMERGENCY | S2 | F4 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150016 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150016 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150016 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017103ACN-2026-08-4000150016 | AUD-2026-08-2000017103ACN-2026-08-4000150016 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Complied | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150017 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Random checking of EBP done from the all level sample of TT JH10A01528 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1656 | DURGAPUR DEPOT | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-08-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150017 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150017 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150017 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150017 | AUD-2026-08-2000017103ACN-2026-08-4000150017 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150018 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Physical DIP taken for TK-06 (MS) and TK-02 (HSD) and physical reading found matching with TSI installed. | 3.7 | Inventory physical dip of minimum two tanks taken | 1656 | DURGAPUR DEPOT | TSI display for secondary radar found defunct and non-functional. To be corrected (Repeat Point) Tank to tank movement from roof of TK2 (HSD) and TK-1 (HSD) was found open. Access for tank to tank movement to be restricted thru suitable measures (repeat Point) | SOD | Marketing | EZ | 2026-08-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150018 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150018 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150018 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150018 | AUD-2026-08-2000017103ACN-2026-08-4000150018 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150019 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Reco done through Manual dips due to WDM issue and dip not getting posted. It was given to understand that the WDMs to Durgapur is planned to be dispatched from Hassan. | 3.8 | Auto vs Manual reconciliation checked | 1656 | DURGAPUR DEPOT | Location to closely coordinate with Hassan and vendor M/s AST for early installation and functioning of the dip posting. | SOD | Marketing | EZ | 2026-09-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-30 | AUD-2026-08-2000017103ACN-2026-08-4000150019 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150019 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150019 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150019 | AUD-2026-08-2000017103ACN-2026-08-4000150019 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150020 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1656 | DURGAPUR DEPOT | Ethanol losses to be brought under control | SOD | Marketing | EZ | 2026-08-31 | OUTDATED OR COMPLEX SOPS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150020 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150020 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150020 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150020 | AUD-2026-08-2000017103ACN-2026-08-4000150020 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-09-24 | Corrective action taken | DURGAPUR IRD Q2 FY 26-27 INSPECTION | 2026-08-07 13:00 | AUD-2026-08-2000017103 | 2026-08-05 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000150032 | Closed | HARAPRASAD GUCHHAIT | 2026-09-24 | 1. safety harness to be used by all the stakeholders at TTG for TT dip checking, TT locking and TT security checking platform 2. Wear and tear found w.r.t Insulation rubber on the swing ladder at TTG, TT locking shed, TT security checking platform (repeat Point) 3. It is advised to use non sparking tool only in the licenced area. 4. It was given to understand that the power dosing is being done manually sometime. Location to get MOC approval prior to such irregular activity. 5. Dry Grass at TTG to be removed periodically. LIC to personally monitor the same 6. Cable needs to be dressed and cable tray to be used for cable going in BCU post bottom loading project (Repeat Point) 7. Cable dressing to be done near HVLR 2 Panel (Repeat Point) 8. Old AC found near the lube godown. To be disposed off. (Repeat Point) 9. Bonding / Electrical continuity of Ethanol unloading hose found not as per requirement. (Repeat Point) 10 All the 3 no. of Fire Engine found in local mode. DSO and LIC to ensure that the fire engine are in auto mode all the time (Repeat Point) 11. As per TAS screen, secondary link found non functional for TMPC, security PC (Repeat Point) 12. TK1 outlet ROSOV is not getting operated in remote mode (Repeat Point) 13. TK-2 and TK-5, inlet ROSOV not getting operated in remote mode (repeat Point) 14. HVLR covering MS tank and TTG was found to be non functional and no MOC was taken. To be arrested immediately. 15. Boundary wall collapsed for the culvert of pipeline near boundary wall. No action taken even after 10 days. 16. Storm water drain wall collapsed near the TT calibration shed. No action taken even after 10 days. 17. TT Gantry, bonding wire to be changed. 18. Secondary Battery for Fire Engine no. 1 was found non functional. Since Complied. 19. Fire Engine no. 3 found to be non functional. To be attended immediately. 20. Drippage from Bay-8 (HSD) swivel joint was observed. To be rectified. | 6.1 | Additional Observations | 1656 | DURGAPUR DEPOT | Corrective action to be taken | SOD | Marketing | EZ | 2026-08-31 | INADEQUATE SAFETY CULTURE | 5 | EMERGENCY | S1 | F5 | 2026-08-31 | AUD-2026-08-2000017103ACN-2026-08-4000150032 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017103ACN-2026-08-4000150032 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-08-2000017103 - ACN-2026-08-4000150032 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017103ACN-2026-08-4000150032 | AUD-2026-08-2000017103ACN-2026-08-4000150032 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143180 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Day-to-day operational activities were reviewed. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1656 | DURGAPUR DEPOT | Location to control TDG violation, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration (This is a repeat point vis-a-vis last quarterly audit). Spots identified where multiple TTs are stopping unauthorisedly to be intimated to the police station under which the location is identified. Regular feedback to be shared with zone on action taken on such cases. | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | EMERGENCY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143180 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143180 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143180 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143180 | AUD-2026-07-2000015091ACN-2026-07-4000143180 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143181 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Individual review of officer carried out with respect to KPI and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1656 | DURGAPUR DEPOT | Officers were advised to have hand on exercise for operating all the fire fighting equipment. Further, they should have the knowledge w.r.t positioning of all the safety critical equipment and ESD. As of May'26, loss of 20 KL is booked in Ethanol which is abnormally high. Transporters and DCTs to be taken on board for conversion of their TTs to bottom loading (Repeat point) | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143181 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143181 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143181 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143181 | AUD-2026-07-2000015091ACN-2026-07-4000143181 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143182 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | 1. M&I Checklist as per the SOP shared by HPPL officer to be maintained and shared with zone periodically (This is a repeat point vis-a-vis last quarterly audit). 2. 31 no. of open MDSA Points of FY 25-26 to be complied and closed 3. 2 no. of HLSA open points to be complied and closed 4. 12 no. of Sr. Management points to be complied and closed 5. Regular E M Lock checking by LIC Master key and records to be maintained 6. Adequate E M Locks & Key inventory at location to be maintained 7. EBMS 20% blending check at TT Gantry to be ensured and records to be maintained | 1.3 | Pending issues reviewed | 1656 | DURGAPUR DEPOT | Expeditious action / compliance to be taken | SOD | Marketing | EZ | 2026-06-30 | FATIGUE AND STRESS | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143182 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143182 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143182 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143182 | AUD-2026-07-2000015091ACN-2026-07-4000143182 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143183 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | During last visit, it was advised to have good housekeeping Location had improved significantly w.r.t last visit however following were observed : 1. Surprise fire drill has not been conducted by LIC in last 3 months 2. Open MOCs are still not closed 3. Gantry Permissive on account of water tank reading not coming in TAS | 1.4 | Earlier action points status checked | 1656 | DURGAPUR DEPOT | Corrective action to be taken | SOD | Marketing | EZ | 2026-06-30 | FATIGUE AND STRESS | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143183 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143183 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143183 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143183 | AUD-2026-07-2000015091ACN-2026-07-4000143183 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143184 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1656 | DURGAPUR DEPOT | 1. Location to upload the 100%TT dip checking data in SAP. Dip elimination FN to be processed at the earliest. 2. Location to ensure the recovery w.r.t VTS equipment charges 3. Location to monitor and take action line with ITDG for the deviations (route/ speed/night halting etc). 4. All open HLSA points to be closed 5. T4S Audit is due in Nov'26. All purchase activity to be done well in advance. 6. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 7. Manual allocation of TT in IMS to be minimised and records with justificationto be maintained for all such cases. 8. EM lock handling and Monitoring : Part load must not be executed without prior approval ofzonal O&D head, Post decantation OTP to be ensured, programming key usages to be ensured for all TT within a period of max. 1 month. 9. All RTGPs to be reviewed periodically and closed 10. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL cases of scope change in any AR to be done without prior approval. | SOD | Marketing | EZ | 2026-06-30 | POOR COMMUNICATION | 10 | EMERGENCY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143184 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143184 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143184 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143184 | AUD-2026-07-2000015091ACN-2026-07-4000143184 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | All the fire scenario as per ERDMP in the mock drills conducted. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143186 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | No Surprise fire drill conducted at location. As advised in last inspection, location has not prepared the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1656 | DURGAPUR DEPOT | Location to ensure to complete all the fire scenario as per ERDMP in the mock drills. | SOD | Marketing | EZ | 2026-09-30 | OUTDATED OR COMPLEX SOPS | 5 | EMERGENCY | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015091ACN-2026-07-4000143186 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143186 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143186 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143186 | AUD-2026-07-2000015091ACN-2026-07-4000143186 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143187 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Leakage from the tank truck delivery valve at TTG Bay no. 6 was simulated following observations recorded : 1. TT Crew of the nearest TT i.e. Bay no. 7 neither moved the standing TT out nor went out of the TT cabin. TT Crew and helper remain inside the TT whowas waiting for their turn to place the TT at Bay no. 7 (They were on the RCC driveway behind bay no. 7) 2. ESD was operated by security guard at main gate 3. Nearest WCFM was operated from one sides as the other side was blocked by the TT 4. There was a gap in role clarity which resulted in delay in the operation of Water hose 5. Personnel wearing SCABA was not communicated properly about the scenario due to which he went on Bay no. 7 for LEL measurement 6. LIC was absent in the scenario and Security personnel didn't informed the LIC over call. 7. Empty Ethanol TT waiting to go out beside Bay no. 1 went to emergency gate which cause Criss crossmovement and delay in unrolling of hose. 8. Main gate was kept closed which resulted in entry restriction for emergency vehicles. | 2.2 | Double contingency scenario simulated; observations recorded | 1656 | DURGAPUR DEPOT | All the observation and recommendation of the drill to be implemented in the next and subsequent drill | SOD | Marketing | EZ | 2026-06-30 | POOR COMMUNICATION | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143187 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143187 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143187 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143187 | AUD-2026-07-2000015091ACN-2026-07-4000143187 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | The lux levels on the secondary roads improved by repairing the old lights. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143188 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Lux level checked : TT gantry : Required : 60 and observed : 230 Secondary roads : Required 10 and observed 6 at few places | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1656 | DURGAPUR DEPOT | It was advised to improve the lux levels on the secondary roads by repairing the old lights. | SOD | Marketing | EZ | 2026-07-15 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S2 | F4 | 2026-07-15 | AUD-2026-07-2000015091ACN-2026-07-4000143188 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143188 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143188 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143188 | AUD-2026-07-2000015091ACN-2026-07-4000143188 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Surprise night inspection is being done. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143189 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Security personnel were interrogated on night time preparedness on emergency and mitigation measures to be taken. The team was found to be well versed on the same. Night Inspection by DSO and LIC carried out and only gate entry records maintained. No report of night inspection maintained at location. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1656 | DURGAPUR DEPOT | Night alertness to be more strengthened. Frequency of Surprise night inspection to be increased, report to be maintained along withCCTV footage in the report. | SOD | Marketing | EZ | 2026-07-15 | FATIGUE AND STRESS | 5 | EMERGENCY | S1 | F5 | 2026-07-15 | AUD-2026-07-2000015091ACN-2026-07-4000143189 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143189 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143189 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143189 | AUD-2026-07-2000015091ACN-2026-07-4000143189 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Security frisking at TT in gate and SOP adherence is strengthened by doing refreshers training. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143190 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Location has total of 42 CCTV Camera and all of them were functional on the date of visit. | 2.6 | CCTV functioning checked | 1656 | DURGAPUR DEPOT | Security frisking at TT in gate and SOP adherence to be strengthened | SOD | Marketing | EZ | 2026-07-15 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-07-15 | AUD-2026-07-2000015091ACN-2026-07-4000143190 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143190 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143190 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143190 | AUD-2026-07-2000015091ACN-2026-07-4000143190 | 21 | 21 | 27 | 80 | 0 | 0 | 46 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143191 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. CCTVs were not active over VA and all of them were down. It was given to understand that there is power back up issue of UPS and MCB use to get tripped every time whenever there is power disconnect. | 2.7 | VA alerts checked / analysed | 1656 | DURGAPUR DEPOT | Location to closely monitor and ensure to maintain the VA active all the time.Frequent similar outage observed for the location andeach time power back up reason provided. LIC to trouble shoot the issue. | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143191 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143191 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143191 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143191 | AUD-2026-07-2000015091ACN-2026-07-4000143191 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143193 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Yes officer operated DCP | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1656 | DURGAPUR DEPOT | More hands on training on safety critical equipment to be acquired by all the officers Periodic training of new officers to be carried in a structured manner covering all aspects of FF equipment and Fire fighting. | SOD | Marketing | EZ | 2026-06-30 | FATIGUE AND STRESS | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143193 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143193 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143193 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143193 | AUD-2026-07-2000015091ACN-2026-07-4000143193 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | The SOP violation is arrested and corrective procedure implemented. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143402 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | MFM vs BCU totaliser comparison available at location. Remarks updated for in case of variation due to calibration, local loading, overrun etc. Product of Local loading done prover testing are being unloaded in UG tanks but no records of dip gain is being maintained. It was given to understand that this is because of simultaneous operation of that tank or product is being pushed from UG to AG tank. | 3.11 | MFM vs BCU totalizer comparison checked | 1656 | DURGAPUR DEPOT | The SOP violation to be arrested and corrective procedure to be implemented | SOD | Marketing | EZ | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143402 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143402 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143402 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143402 | AUD-2026-07-2000015091ACN-2026-07-4000143402 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | LIC reviewed the critical alarms periodically and reported for abnormalities. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143403 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1656 | DURGAPUR DEPOT | LIC to review the critical alarms periodically and report if any abnormalities found. | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143403 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143403 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143403 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143403 | AUD-2026-07-2000015091ACN-2026-07-4000143403 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | LIC reviewed the K Factor and meter factor in system and in BCU periodically. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143404 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1656 | DURGAPUR DEPOT | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143404 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143404 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143404 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143404 | AUD-2026-07-2000015091ACN-2026-07-4000143404 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143405 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Local loading record maintained at location. However following are the observations : 1. TT no. is not being mentioned while making the order in BCU for local loading for all the local loads 2. Justification and records not maintained for local loading donein Jan'26 and Feb'26 | 3.14 | Local loading checks (if applicable) | 1656 | DURGAPUR DEPOT | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 10 | EMERGENCY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143405 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143405 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143405 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143405 | AUD-2026-07-2000015091ACN-2026-07-4000143405 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143406 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Housekeeping practice is found satisfactory. PPE usages found to be strengthened specially usages of Safety harness belt at TT locking / unlocking shed. The main gate of TT entry was found partially block by officers CAR of visitors (Depot/ RO). It was advisedto have NIL car parking in front of TT IN gate and TT to be parked at designated place only, Since complied. | 3.15 | Housekeeping & PPE usage checked | 1656 | DURGAPUR DEPOT | To be corrected and ensure NIL recurrence | SOD | Marketing | EZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 10 | EMERGENCY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143406 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143406 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143406 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143406 | AUD-2026-07-2000015091ACN-2026-07-4000143406 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | EPs are tested in presence of Officer. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143407 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Vegetation inside the depot was also under control | 3.16 | Earth pits / boundary / vegetation control checked | 1656 | DURGAPUR DEPOT | Location to ensure that EPs are tested well within the time period. Further, all EPs to be tested in presence of Officer | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143407 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143407 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143407 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143407 | AUD-2026-07-2000015091ACN-2026-07-4000143407 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143409 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | OISD - NIL pending Point MDSA FY 25-26 - 31 pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1656 | DURGAPUR DEPOT | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-07-31 | INADEQUATE SAFETY CULTURE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015091ACN-2026-07-4000143409 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143409 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143409 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143409 | AUD-2026-07-2000015091ACN-2026-07-4000143409 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143410 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Maintenance activity found satisfactory. However, 4 no. of barrels (2 empty) found lying inside the Pump House. 1 no. of Pump marked as not in use as per below details found inside pump house. Pump no. 4, 11 KW, 15 HP, 415 V, 20 Amp and 1475 RMP Unidentified loose end of cable found near pump house, near store house area towards the planning room. Sand lying at TT out gate. | 4.2 | Maintenance activities reviewed | 1656 | DURGAPUR DEPOT | Location to declare the pump as surplus inventory in the designated portal. Cable dressing to be ensured and cables not required to be removed/ to ensure safe working condition. | SOD | Marketing | EZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143410 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143410 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143410 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143410 | AUD-2026-07-2000015091ACN-2026-07-4000143410 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | The secondary routes are created wherever applicable and action is taken as per ITDG wherever deemed fit. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143196 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Review of VTS deviation done on regular basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC. Spots identified where multiple TTs are stopping unauthorisedly to be intimated to the police station under which thelocation is identified. Regular feedback to be shared with zone on action taken on such cases. | 3.3 | VTS deviations reviewed | 1656 | DURGAPUR DEPOT | Location is advised to create the secondary route wherever applicable and action to be taken as per ITDG wherever deemed fit. | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | EMERGENCY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143196 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143196 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143196 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015091ACN-2026-07-4000143196 | AUD-2026-07-2000015091ACN-2026-07-4000143196 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Location ensured EBP checks daily of the outgoing trucks and records maintained. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143197 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Random checking of EBP done from the all level sample of TT WB19J7191 & WB37D5926 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1656 | DURGAPUR DEPOT | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-06-30 | FATIGUE AND STRESS | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143197 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143197 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143197 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143197 | AUD-2026-07-2000015091ACN-2026-07-4000143197 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143198 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Same is being ensured at location. TT dip checked for ethanol TT and found ok. Empty Ethanol TT no. NL01AC9872 was found kept inside depot for last 7-10 days. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1656 | DURGAPUR DEPOT | Corrective action to be taken | SOD | Marketing | EZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143198 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143198 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143198 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143198 | AUD-2026-07-2000015091ACN-2026-07-4000143198 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action taken for the recomendation, hence complied. | DURGAPUR IRD Q1 FY 26-27 INSPECTION | 2026-06-11 20:00 | AUD-2026-07-2000015091 | 2026-06-10 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143199 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Physical DIP taken for TK-05 (MS) and TK-02 (HSD) and physical reading found matching with TSI installed. | 3.7 | Inventory physical dip of minimum two tanks taken | 1656 | DURGAPUR DEPOT | TSI display for secondary radar found defunct and non-functional. To be corrected Tank to tank movement from roof of TK2 (HSD) and TK-1 (HSD) was found open. Access for tank to tank movement to be restricted thru suitable measures | SOD | Marketing | EZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015091ACN-2026-07-4000143199 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015091ACN-2026-07-4000143199 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-07-2000015091 - ACN-2026-07-4000143199 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015091ACN-2026-07-4000143199 | AUD-2026-07-2000015091ACN-2026-07-4000143199 | 21 | 21 | 27 | 80 | 0 | 0 | 44 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122683 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Yes Review of location performance carried out. It is noticed that post DPC, assignment to be changed for officers. LIC advised to take charge of all the present and incoming officers, Train them and lead the team for meeting all safety and operational parameters. | 1.2 | Performance review conducted | 1656 | DURGAPUR DEPOT | Location to improve on route corrections, control TDG violations, Strengthen the DIP checking at TT gantry , to strictly adhere to ethanol TT unloading SOP . Location is advised to have NIL SOP deviation w.r.t safety/ safe working practice and to have strict controls on local loading/ PLT documentation. | SOD | Marketing | EZ | 2026-03-10 | OUTDATED OR COMPLEX SOPS | 10 | CONTRACTOR SAFETY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122683 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122683 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122683 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122683 | AUD-2026-03-2000011011ACN-2026-03-4000122683 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122684 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Yes pending issues reviewed. | 1.3 | Pending issues reviewed | 1656 | DURGAPUR DEPOT | Location to process FN for TT Dip elimination and ensure monthly TAS v/s actual dip checks. Location to carryout newly laid pipeline SOP and filling the checklist given by HPPL. Location to follow-up with NHAI for early release of BG which was submitted to NHAI for new pipeline laying job Depot night operation permission from PESO to be expedited | SOD | Marketing | EZ | 2026-06-01 | LACK OF TRAINING OR COMPETENCY | 10 | CONTRACTOR SAFETY | S2 | F5 | 2026-06-01 | AUD-2026-03-2000011011ACN-2026-03-4000122684 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122684 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122684 | 532 | 8294 | 21 | 8294 | 140 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122684 | AUD-2026-03-2000011011ACN-2026-03-4000122684 | 21 | 21 | 26 | 80 | 0 | 0 | 39 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122685 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Yes checked. During last visit, it was advised to complete the bottom loading job in totality. It is noticed that work has been completed. Further improvements needed. | 1.4 | Earlier action points status checked | 1656 | DURGAPUR DEPOT | To be expedited and tranporter/ DCT s to be taken up for early conversion of TTs. Project surplus material beside the Fire engineshed and water tank to be cleared. | SOD | Marketing | EZ | 2026-03-05 | POOR COMMUNICATION | 4 | EMERGENCY | S1 | F4 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000122685 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122685 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122685 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000122685 | AUD-2026-03-2000011011ACN-2026-03-4000122685 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Corrective action is taken for all recomendation, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122686 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Compliance to zonal/HQO circular is being carried out. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1656 | DURGAPUR DEPOT | Needs improvement in following domain : 1. 100% TT dip checking for all the TTs loaded and maintain records 2. Random EBP%age checking for EBMS loads by LIC and maintain records. Regular EBMS blend checks to be carrried out by planning officer throughout the day and records maintain. 3. LIC to personally review and ensure records of all TAS critical parameters are available vis-a-vis local loading report, MFM meter factor change report, sick TT report. 4. Sealing of MFM display is not as per the model sealing design. To be corrected. | SOD | Marketing | EZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122686 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122686 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122686 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122686 | AUD-2026-03-2000011011ACN-2026-03-4000122686 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Surprised Drill Conducted in July 26, hence complied. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122687 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Fire drill carried out with the team | 2.1 | Fire drill conducted in last 6 months (surprise) | 1656 | DURGAPUR DEPOT | LIC to ensure to conduct surprise fire drill without knowledge of other officers every month | SOD | Marketing | EZ | 2026-03-15 | INADEQUATE SAFETY CULTURE | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122687 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122687 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122687 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122687 | AUD-2026-03-2000011011ACN-2026-03-4000122687 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 56
KUMAR ANAND | 2026-09-25 | HARAPRASAD GUCHHAIT | 2026-08-11 | Location ensured post load TT dip checks and records maintained. Surprise check by LIC is done and records maintained. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122698 | Closed | HARAPRASAD GUCHHAIT | 2026-08-11 | Random checking of the dip for TT post loading done and found satisfactory | 3.2 | Post-loading dip checks verified | 1656 | DURGAPUR DEPOT | Location to ensure to have post load TT dip checks by officers and maintain records. Surprise check by LIC and maintain records. | SOD | Marketing | EZ | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 5 | EMERGENCY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000122698 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122698 | 2026-08-07 13:00 | 73.2122 | 389 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122698 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000122698 | AUD-2026-03-2000011011ACN-2026-03-4000122698 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 56
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154465 | Open |  |  | Reviewed performance of all Officers and officers were found focussed on the Goals and Targets with emphasis on process/efficiency improvement | 1.2 | Performance review conducted | 1777 | Hassan Terminal | Team to focus on G&T for the year and come up with improvements process and work efficency. LIC advised to review the individual performance and advise officers to ensure 100% achievement. | SOD | Marketing | SWZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017410ACN-2026-09-4000154465 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154465 | 2026-09-22 17:00 | 27.0455 | 576 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154465 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154465 |  | AUD-2026-09-2000017410ACN-2026-09-4000154465 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154466 | Open |  |  | Dip elimination to be completed at the earliest | 1.3 | Pending issues reviewed | 1777 | Hassan Terminal | Location to expedite and achieve dip elimination at the earliest. | SOD | Marketing | SWZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154466 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154466 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154466 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154466 |  | AUD-2026-09-2000017410ACN-2026-09-4000154466 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154467 | Open |  |  | 7 pending point of total 28 points of last inspection | 1.4 | Earlier action points status checked | 1777 | Hassan Terminal | Pending observations to be complied at the earliest | SOD | Marketing | SWZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154467 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154467 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154467 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154467 |  | AUD-2026-09-2000017410ACN-2026-09-4000154467 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154468 | Open |  |  | 1. Land Mutation is pending at KIADB Head office, Bengaluru. Need support for regular follow up at Bengaluru 2. CSR budget is required to support local police and local fire bridage. | 1.5 | HQO / Zonal support required identified | 1777 | Hassan Terminal | Location to follow up for approvals. | SOD | Marketing | SWZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017410ACN-2026-09-4000154468 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154468 | 2026-09-22 17:00 | 27.0455 | 576 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154468 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154468 |  | AUD-2026-09-2000017410ACN-2026-09-4000154468 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154469 | Open |  |  | Officers were advised that execptional performance is expected out the team. | 1.6 | Expectations clearly communicated to officers | 1777 | Hassan Terminal | Officers were informed to strengthen Safe Operations of the terminal & develop cross functional knowledge of the departments to handle all the jobs. | SOD | Marketing | SWZ | 2027-03-31 |  | 2 |  | S2 | F1 | 2027-03-31 | AUD-2026-09-2000017410ACN-2026-09-4000154469 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154469 | 2026-09-22 17:00 | 27.0455 | 576 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154469 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154469 |  | AUD-2026-09-2000017410ACN-2026-09-4000154469 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154470 | Open |  |  | 1) MOV Master panel 2) Installation of Additional 14.5KW Solar | 1.8 | Improvement plans discussed | 1777 | Hassan Terminal | 1) Proposal sent & 2) Proposal to be sent to Zone | SOD | Marketing | SWZ | 2027-10-31 |  | 1 |  | S1 | F1 | 2027-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154470 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154470 | 2026-09-22 17:00 | 27.0455 | 790 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154470 | 532 | 8294 | 21 | 8294 | -376 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154470 |  | AUD-2026-09-2000017410ACN-2026-09-4000154470 | 21 |  | 27 | 80 | 1 | 2 | 113
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154471 | Open |  |  | Lux level to be improved at Tank Farm Area, TW and TT Parking Area | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1777 | Hassan Terminal | Lux level to be improved at Tank Farm Area, TW and Parking Area | SOD | Marketing | SWZ | 2027-03-31 |  | 8 |  | S4 | F2 | 2027-03-31 | AUD-2026-09-2000017410ACN-2026-09-4000154471 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154471 | 2026-09-22 17:00 | 27.0455 | 576 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154471 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017410ACN-2026-09-4000154471 |  | AUD-2026-09-2000017410ACN-2026-09-4000154471 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154472 | Open |  |  | Access control arrangements at the Main Gate and Licensed Area entry were checked and found satisfactory | 2.8 | Access control systems checked | 1777 | Hassan Terminal | Unable to register new entries due to site issue. Corrective action to be taken | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154472 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154472 | 2026-09-22 17:00 | 27.0455 | 425 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154472 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154472 |  | AUD-2026-09-2000017410ACN-2026-09-4000154472 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154473 | Open |  |  | Combined stock of AFFF (3KL) and AR-AFFF ( 48 KL) meets the requirement of location | 2.9 | Foam inventory verified | 1777 | Hassan Terminal | Mother & Daughter tanks to be replenished on continuous basis to have adequate stocks as per OISD requirement | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017410ACN-2026-09-4000154473 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154473 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154473 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154473 |  | AUD-2026-09-2000017410ACN-2026-09-4000154473 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154474 | Open |  |  | HVLR No-9 & HVLR-1 were operated by DSO. HVLR-12 was operated by Sr. Manager-Operations | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1777 | Hassan Terminal | All officers & including new officers shall be trained on Fire fighting equipment operations. Training records to be updated | SOD | Marketing | SWZ | 2026-10-31 |  | 6 |  | S3 | F2 | 2026-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154474 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154474 | 2026-09-22 17:00 | 27.0455 | 425 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154474 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017410ACN-2026-09-4000154474 |  | AUD-2026-09-2000017410ACN-2026-09-4000154474 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154475 | Open |  |  | Medical check up and Eye check up last done on 24th-27th Sept 2025. | 2.16 | Eyesight / colour-blindness awareness checked | 1777 | Hassan Terminal | Location to carryout medical check/eye check up in current year | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154475 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154475 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154475 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154475 |  | AUD-2026-09-2000017410ACN-2026-09-4000154475 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154476 | Open |  |  | Post loading dips were checked for following tts KA16B9156 (20 KL), KA51AD9059 (14 kl ), KA13AA2548(14kl) were found ok , KA17AB5826 (14 kl) 1 compartment tt variation of 2mm in 1st comp & excess removed | 3.2 | Post-loading dip checks verified | 1777 | Hassan Terminal | Location to check TT dips and update in SAP as per the Policy | SOD | Marketing | SWZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017410ACN-2026-09-4000154476 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154476 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154476 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154476 |  | AUD-2026-09-2000017410ACN-2026-09-4000154476 | 21 |  | 27 | 80 | 1 | 2 | 57
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154477 | Open |  |  | Records of ethanol blending percentage checks for first-load TTs are being maintained at the location in SAP for month of Jul 26 was 18 %. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1777 | Hassan Terminal | Random checking of TTs for EBP to be done on regular basis and Blending percentage of 20% to be maintained | SOD | Marketing | SWZ | 2026-12-31 |  | 6 |  | S3 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154477 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154477 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154477 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017410ACN-2026-09-4000154477 |  | AUD-2026-09-2000017410ACN-2026-09-4000154477 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154478 | Open |  |  | House keeping to be improved | 3.15 | Housekeeping & PPE usage checked | 1777 | Hassan Terminal | 1. Fire Pump house housekeeping to be improved 2. Drains to be cleaned from vegitation 3. Housekeeping to be improved in Ethanol Gantry 4. Grass cutting to be done in Tank wagon gantry, tankfarm and parking area 5. Cleanless to be improved in TT Gantry 6. housekeeping to be improved under the pipelines | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154478 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154478 | 2026-09-22 17:00 | 27.0455 | 425 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154478 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154478 |  | AUD-2026-09-2000017410ACN-2026-09-4000154478 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154479 | Open |  |  | Grass observed in the parking, TW gantry | 3.16 | Earth pits / boundary / vegetation control checked | 1777 | Hassan Terminal | Grass cutting to be done in TW gantry, TT parking area and Tankfarm. | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154479 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154479 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154479 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154479 |  | AUD-2026-09-2000017410ACN-2026-09-4000154479 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154480 | Open |  |  | All OISD points are complied. Pending MDSA/SSA points to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1777 | Hassan Terminal | Location to expediate the closure of Pending MDSA/SSA points.MDSA 2024-25- 2 nos & MDSA 2025-26- 2 nos. | SOD | Marketing | SWZ | 2026-12-31 |  | 8 |  | S4 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154480 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154480 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154480 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017410ACN-2026-09-4000154480 |  | AUD-2026-09-2000017410ACN-2026-09-4000154480 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154481 | Open |  |  | Inspected the following areas 1. Fire pump house 2. Ethanol gantry 3. Tankfarm 4. TT Gantry 5. Fabrication yard 6. PMCC 7. Product Pump House 8. Central Foam shed 9. Tank Wagon Gantry 10. ETP | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1777 | Hassan Terminal | Unwanted sheds to be removed Scrap to be segregated and RFD to be initiated Missing nut bolts to be fixed in PMCC Housekeeping to be improved in all operating areas | SOD | Marketing | SWZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154481 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154481 | 2026-09-22 17:00 | 27.0455 | 425 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154481 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154481 |  | AUD-2026-09-2000017410ACN-2026-09-4000154481 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154482 | Open |  |  | 3 Projects to be completed | 4.3 | Project progress reviewed | 1777 | Hassan Terminal | 1. TAS novex integration 2. UG Tanks overfill protection 3.Replacement of secondary radar of AG tanks | SOD | Marketing | SWZ | 2027-03-31 |  | 6 |  | S3 | F2 | 2027-03-31 | AUD-2026-09-2000017410ACN-2026-09-4000154482 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154482 | 2026-09-22 17:00 | 27.0455 | 576 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154482 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017410ACN-2026-09-4000154482 |  | AUD-2026-09-2000017410ACN-2026-09-4000154482 | 21 |  | 27 | 80 | 1 | 2 | 83
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154483 | Open |  |  | Auctioning by MSTC of Scrap Lots in progress | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1777 | Hassan Terminal | Location to be ready for physical disposal once Disposal Order released by MSTC | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154483 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154483 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154483 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154483 |  | AUD-2026-09-2000017410ACN-2026-09-4000154483 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-09-4000154484 | Open |  |  | MFM stamping to be done | 5.1 | MFM based accounting at Pipeline and OMC location | 1777 | Hassan Terminal | PLT receipts to be cross checked with HPCL MFM | SOD | Marketing | SWZ | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017410ACN-2026-09-4000154484 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154484 | 2026-09-22 17:00 | 27.0455 | 425 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154484 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154484 |  | AUD-2026-09-2000017410ACN-2026-09-4000154484 | 21 |  | 27 | 80 | 1 | 2 | 61
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-09-4000154485 | Open |  |  | Dyke Valve hooter was not functioning for TK202 | 5.2 | Functioning of all Hooters in control room | 1777 | Hassan Terminal | Dyke valve hooters to be repaired for functioning | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154485 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154485 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154485 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154485 |  | AUD-2026-09-2000017410ACN-2026-09-4000154485 | 21 |  | 27 | 80 | 1 | 2 | 70
[5 empty] | Q2 LOCATION VISIT OF HASSAN TERMINAL | 2026-09-22 17:00 | AUD-2026-09-2000017410 | 2026-09-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154486 | Open |  |  | 1. Road Repair to be done at out gate & Ethanol gantry road 2. Non-functional gauges of Fire Engine HSD tanks to be closed 3. Sand filling to be done for HSD open duct near Fire engine HSD tanks 4. Files/Spares to be kept in a Rack in Fire engine shed 5. LubeOil leakage marks observed under Fire Engine 1, 3 and 5. Necessary action to be taken for compliance 6. Area cordoning to be done for any repair works. FE-4 to be segregated with necessary cordining arrangement 7. Vegitation to be removed from Storm water drains. 8. Water leakages from Monitors and Double Hydrant to be arrested. 9. Housekeeping to be improved in Ethanol Gantry. Debris to be cleared from the Dust bins 10. Cleaning in TT Gantry & Ethanol Gantry 11. Hydro testing details to be painted on the hoses/Stickering to be done. 12. Wheel chocks to be properly placed near the trucks. 13. Loose Cable trays to be properly tied in the Ethanol Gantry. 14. Leakages to be arrested at CI dosing Shed. 15. Fire Extinguishers to be cleaned and maintained in good condition 16. End plug for CI Dosing unit to be provided. 17. Unwanted earthing strips to be removed at Ethanol gantry 18. foam availability in Mother foam tank to be checked and topped up. Level indication and equivalent foam ltrs to be marked 19. Foam unloading hoses to be replaced. 20. Toilet to ethanol gantry 21. JB to be removed 22. Pipeline painting of Diesel filling lines of DGs to be done. 23. touch up painting to be done in MCC room 24. HSD level tube to be changed for DGs HSD tanks 25. Rusted end caps to be changed at strainers drain points. 26. Damaged wind socks to be replaced. | 6.1 | Safety | 1777 | Hassan Terminal | Location to take corrective action | SOD | Marketing | SWZ | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-09-2000017410ACN-2026-09-4000154486 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017410ACN-2026-09-4000154486 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017410 - ACN-2026-09-4000154486 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017410ACN-2026-09-4000154486 |  | AUD-2026-09-2000017410ACN-2026-09-4000154486 | 21 |  | 27 | 80 | 1 | 2 | 70
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | The Excess budget from old depot has been transfered to new depot. As of now no action is require. Although location keep close monitoring over the budget consumption pattern. In future, if location identify any excess budget in old depot code then that will betransfer to new depot | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153259 | Closed | KAMLESH SAHU | 2026-09-25 | Review of major KPIs of stock loss , scrap disposal , M&I , Projects discussed for last year . MEB budget requirement for new depotalso discussed & asked to provide details | 1.2 | Performance review conducted | 1527 | RAIPUR DEPOT | Advised to transfer the excess budget to New Depot | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153259 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153259 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153259 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153259 | AUD-2026-09-2000017609ACN-2026-09-4000153259 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Location pass needful instruction of DS Group on daily basis and ensure the on time closure of depot. Location also ensure no timeextention of the depot operation | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153262 | Closed | KAMLESH SAHU | 2026-09-25 | Improvement plan with smooth transition of important portfolio of officers was discussed with LIC in view of transfer of officers | 1.8 | Improvement plans discussed | 1527 | RAIPUR DEPOT | Advised improve the TT placement time of Black oil . No time extension of the Depot operations | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153262 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153262 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153262 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153262 | AUD-2026-09-2000017609ACN-2026-09-4000153262 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Positioning of Level tube in Mother tank has been modified and now foam volume can be visible on lowest level also. Location hasreceived foam inventroy from foamtech anti fire company on 08 September 26 Also foam level in mother tank has topped up. | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153264 | Closed | KAMLESH SAHU | 2026-09-25 | Verified and found okay . | 2.9 | Foam inventory verified | 1527 | RAIPUR DEPOT | Advised to keep the additional stock in Mother tank and level should be visible . | SOD | Marketing | ECZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153264 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153264 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153264 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153264 | AUD-2026-09-2000017609ACN-2026-09-4000153264 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Pending points status as follow OISD-Nil Pending MDSA-Nil Pending SSA-Nil Pending | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153267 | Closed | KAMLESH SAHU | 2026-09-25 | Compliance status reviewed . | 3.18 | OISD/MDSA/SSA compliance reviewed | 1527 | RAIPUR DEPOT | OISD/MDSA/SSA compliance reviewed | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153267 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153267 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153267 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153267 | AUD-2026-09-2000017609ACN-2026-09-4000153267 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Location has completed all pending route correction and continue to correct wherever anomolies will observe | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153265 | Closed | KAMLESH SAHU | 2026-09-25 | Checked . Route deviation voilation found | 3.3 | VTS deviations reviewed | 1527 | RAIPUR DEPOT | route correction in some cases | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153265 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153265 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153265 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153265 | AUD-2026-09-2000017609ACN-2026-09-4000153265 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Location has separated usable items and scrap items. Usable items has shifted to engineering store | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153266 | Closed | KAMLESH SAHU | 2026-09-25 | Several project material lying idle like valves , fittings , strainer , etc which was shifted from other locations by project team | 3.9 | Abnormal variations / unused assets reviewed | 1527 | RAIPUR DEPOT | Location advised to seggregate the material in usable and scrap items and take action | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153266 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153266 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153266 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153266 | AUD-2026-09-2000017609ACN-2026-09-4000153266 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | Black oil tank conversion has completed TK17 Converted into LDO Whereas TK4 converted into FO | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153270 | Closed | KAMLESH SAHU | 2026-09-25 | Tank conversion -Black oil | 4.3 | Project progress reviewed | 1527 | RAIPUR DEPOT | Needs to close | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153270 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153270 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153270 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153270 | AUD-2026-09-2000017609ACN-2026-09-4000153270 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | All solar area in between old depot and new depot has been cleaned and now it is free from grass Also some of the project spare shifted out of solar area | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153272 | Closed | KAMLESH SAHU | 2026-09-25 | Solar Plant Sorrounding area found poor housekeeping | 6.1 | Solar Plant approch | 1527 | RAIPUR DEPOT | Unwanted project material to be sifted to designated area and maintain cleanness around | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153272 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153272 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153272 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153272 | AUD-2026-09-2000017609ACN-2026-09-4000153272 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | All the unwanted materials like civil structure, metal piece, growth of grass etc has been cleared from emergency route | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153274 | Closed | KAMLESH SAHU | 2026-09-25 | Needs the keep the way clean | 6.3 | Emergency gate | 1527 | RAIPUR DEPOT | Remove the unwanted item in the approach rode | SOD | Marketing | ECZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153274 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153274 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153274 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153274 | AUD-2026-09-2000017609ACN-2026-09-4000153274 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
YADAV GIRISH KUMAR | 2026-09-25 | KAMLESH SAHU | 2026-09-25 | All transparent level tube of mother tank and HVLR TANK has replaced | RAIPUR-1 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:28 | AUD-2026-09-2000017609 | 2026-08-26 13:28 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153275 | Closed | KAMLESH SAHU | 2026-09-25 | Foam level indicator visibility found poor | 6.4 | HVLR Daughter Tanks | 1527 | RAIPUR DEPOT | Needs to be replaced | SOD | Marketing | ECZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017609ACN-2026-09-4000153275 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017609ACN-2026-09-4000153275 | 2026-08-28 18:28 | 51.9844 | 389 | >20 | AUD-2026-09-2000017609 - ACN-2026-09-4000153275 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017609ACN-2026-09-4000153275 | AUD-2026-09-2000017609ACN-2026-09-4000153275 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
KUSHAGRA VASHISHTH | 2026-09-26 | KUSHAGRA VASHISHTH | 2026-09-07 | Job schedule for the security guards for second shift (1400-1900) during TT loading operation 1S - Visitor Gate 1S - TT Entry Gate 1S - TT Exit Gate 1S - TT Parking Out Gate 1S - Plant Patrolling Job schedule for the security guards for second shift (1900-2200) once the TT loading operation is over 1S - Visitor Gate 1S – CCTV monitoring & VA alert screen monitoring 1S – Document reconciliation 2S - Water tank dip gauging & Plant Patrolling (RFID based guard tour monitoring system, BCU lock checking, Open panels of High Mast and other electrical equipments) | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144684 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | It is observed that 5 security guards are deployed in 2nd shift. The job role of these security guards is not defined after the completion of TT loading operations. | 6.15 | Deployment of Security Guards | 1278 | JODHPUR TERMINAL | Location to develop a job schedule for the security guards as to who will do which job once the TT loading operation is over. Location to also check whether one security guard can be replaced with once contract workmen for TT in/out entry in register. | SOD | Marketing | NWF | 2026-08-31 | INSUFFICIENT SUPERVISION | 15 | PROCESS SAFETY | S3 | F5 | 2026-08-31 | AUD-2026-07-2000015346ACN-2026-07-4000144684 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144684 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144684 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144684 | AUD-2026-07-2000015346ACN-2026-07-4000144684 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 56
KUSHAGRA VASHISHTH | 2026-09-26 | KUSHAGRA VASHISHTH | 2026-09-17 | Patch painting of TK-2 has been carried out at the rust-affected areas as per OISD requirements. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144683 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Painting of TK-2 is advised in view of OISD this year. Marks of rusting observed on one side of the tank. Last paiting done in 2015. | 6.14 | Major Maintenance | 1278 | JODHPUR TERMINAL | Pls carry out patch painting of tank | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144683 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144683 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144683 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144683 | AUD-2026-07-2000015346ACN-2026-07-4000144683 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-26 | KUSHAGRA VASHISHTH | 2026-09-07 | All Log books maintained are being signed by officers. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144676 | Closed | KUSHAGRA VASHISHTH | 2026-09-07 | Log books are required to be signed by officers | 6.7 | Log Book | 1278 | JODHPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144676 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144676 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144676 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144676 | AUD-2026-07-2000015346ACN-2026-07-4000144676 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-26 | KUSHAGRA VASHISHTH | 2026-09-17 | All MOVs have been checked and ensured to remain in remote mode. | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144675 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | TK-17 MOV- 610/615 in local. TK-16 MOV-607 in local. MOV -512 in local mode. | 6.3 | mov repair and communication | 1278 | JODHPUR TERMINAL | Location to ensure that all MOVs are in remote mode only | SOD | Marketing | NWF | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144675 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144675 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144675 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144675 | AUD-2026-07-2000015346ACN-2026-07-4000144675 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-26 | KUSHAGRA VASHISHTH | 2026-09-17 | Complied and closed | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000144679 | Closed | KUSHAGRA VASHISHTH | 2026-09-17 | Location has submitted the documents at respective tolls of 5 districts. | 6.1 | Discounted toll | 1278 | JODHPUR TERMINAL | Activity to be completed for Jodhpur also by 31.07.2026 | SOD | Marketing | NWF | 2026-07-31 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-07-31 | AUD-2026-07-2000015346ACN-2026-07-4000144679 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144679 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144679 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144679 | AUD-2026-07-2000015346ACN-2026-07-4000144679 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
KUSHAGRA VASHISHTH | 2026-09-26 |  |  | Location is ensuring that scrap generated in H1 is disposed during H2 | INSPECTION OF JODHPUR IRD 24 TO 26 JUNE | 2026-06-26 15:30 | AUD-2026-07-2000015346 | 2026-06-24 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000144674 | Closed | KUSHAGRA VASHISHTH | 2026-09-26 | Location to ensure removal of e-scrap items | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1278 | JODHPUR TERMINAL | Location to ensure that scrap generated in H1 is disposed during H2 | SOD | Marketing | NWF | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-07-2000015346ACN-2026-07-4000144674 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015346ACN-2026-07-4000144674 | 2026-09-25 20:45 | 23.8893 | 390 | >20 | AUD-2026-07-2000015346 - ACN-2026-07-4000144674 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015346ACN-2026-07-4000144674 | AUD-2026-07-2000015346ACN-2026-07-4000144674 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
MANDAL PRATAPKUMAR | 2026-09-26 | NILABH | 2026-09-25 | CBAC devise made functional at location. New Devise installed at location. | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150274 | Closed | NILABH | 2026-09-25 | During the visit, the access control system was checked and found to be partially non-functional. Out of 10 CBAC systems installed,06 were found non-functional. Further, out of 02 biometric access control systems, only 01 system, installed at the main gate entry, was found operational. | 2.8 | Access control systems checked | 1305 | KANPUR TERMINAL | The non-functional CBAC and biometric access control system (for manual entry to licensed area) to be rectified at the earliest. | SOD | Marketing | NCR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 9 | PROCESS SAFETY | S3 | F3 | 2026-10-31 | AUD-2026-08-2000017157ACN-2026-08-4000150274 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150274 | 2026-08-26 17:00 | 54.0455 | 390 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150274 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017157ACN-2026-08-4000150274 | AUD-2026-08-2000017157ACN-2026-08-4000150274 | 21 | 21 | 27 | 80 | 4 | 4 | 61 | 56
MANDAL PRATAPKUMAR | 2026-09-26 | NILABH | 2026-09-25 | CBAC Device made functional. New CBAC device installed completed. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127433 | Closed | NILABH | 2026-09-25 | Access control system: CBACs devices ( 1 visitor enrollment and 2 license area entry gate) is not working. MOC approval initiated vide no 3100000316 dtd 09.06.2025 however same is not in approved status. | 2.8 | Access control systems checked | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-05-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-05-30 | AUD-2026-04-2000011243ACN-2026-04-4000127433 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127433 | 2026-08-26 17:00 | 54.0455 | 390 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127433 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127433 | AUD-2026-04-2000011243ACN-2026-04-4000127433 | 21 | 21 | 26 | 80 | 4 | 4 | 39 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | Status of compliances of audits: OISD Jan 2025: 4848(0Pending) MDSA 2025-26: 4949(0Pending) SSA 2025-26: 6060(0Pending) | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124923 | Closed | SINGH KUNAL | 2026-09-26 | Status of compliances of audits: OISD Jan 2025: 44/48 (4 Pending) MDSA 2025-26: 42/49 (7 Pending) SSA 2025-26: 55/60 (5 Pending) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-03-2000010974ACN-2026-03-4000124923 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124923 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124923 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124923 | AUD-2026-03-2000010974ACN-2026-03-4000124923 | 21 | 21 | 26 | 80 | 0 | -26 | 57 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | Solar generating monitoring is being done on continuous basis. 1 No. fire engine is has been repaired and put to use. | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124924 | Closed | SINGH KUNAL | 2026-09-26 | Solar generation for a period Apr’25 to Jan’26 was reviewed and observed that frequent inverter tripping was happened due to which generation on those days were affected. Location has been advised to ensure close monitoring of solar generation for generation as per design basis. 1 No Fire Engine is under breakdown, to be repaired and put back in service. | 4.2 | Maintenance activities reviewed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124924 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124924 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124924 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124924 | AUD-2026-03-2000010974ACN-2026-03-4000124924 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | Stock loss is there in LAN due to dormancy. For all products stock variation is within range. Blending ratio for SKO has been takenand SKO blending shall be carried out when issue of Hazy HSD from HRRL Barmer is rectified.Once clear HSD is received. | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124927 | Closed | KAPIL DEV | 2026-09-26 | Location to ensure stock loss for LAN, MTO, Bio-Diesel to be within AOP Targets. Also location to take corrective action for liquidation of old SKO laying at location. | 6.1 | Stockloss | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-03-2000010974ACN-2026-03-4000124927 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124927 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124927 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124927 | AUD-2026-03-2000010974ACN-2026-03-4000124927 | 21 | 21 | 26 | 80 | 0 | -26 | 44 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | Trained personnel Mr. Mohsin Rathod having hazardous license upto 22-07-2029 is available. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146314 | Closed | SINGH KUNAL | 2026-09-26 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146314 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146314 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146314 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146314 | AUD-2026-07-2000016503ACN-2026-07-4000146314 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 56
KAPIL DEV | 2026-09-26 |  |  | Facility for testing of Eyesight / colour-blindness has been made available. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146315 | Closed | SINGH KUNAL | 2026-09-26 | Facility not available. | 2.16 | Eyesight / colour-blindness awareness checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146315 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146315 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146315 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146315 | AUD-2026-07-2000016503ACN-2026-07-4000146315 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | 2. Signboards are provided which shows the route direction for the emergency exit gate. 3.Fire Engine B has been repaired and put back to use. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146310 | Closed | SINGH KUNAL | 2026-09-26 | Yes observed to be satisfactory 1. MCP-6 in Control Room Admin building was tested and found to be working properly with audio visual alarm and paging announcement. 2. Inside the License Area, only assembly point boards are shown and no signboard found available indicating the route direction for the emergency exit gate. 3. Fire Engines F, E, D, and A were tested and all units started successfully in the programmed priority sequence with rated RPM of 1500 and nil deficiencies observed. FE-F: Started in auto mode. RPM observed: 1499–1509. FE-E: Started in auto mode. RPM observed: 1497–1500. FE-D: Started in auto mode. RPM observed: 1495–1503. FE-A: Started in auto mode. RPM observed: 1495–1504. All fire engines operated satisfactorily during testing. Fire engine testing shall be carried out without opening the hydrant. Fire Engine B is taken out for repairs, the same to be put back into operations at the earliest. | 2.5 | Emergency response preparedness reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146310 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146310 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146310 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146310 | AUD-2026-07-2000016503ACN-2026-07-4000146310 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | TT crew has been sensitised on usage of PPE complaince. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146319 | Closed | SINGH KUNAL | 2026-09-26 | Helmet was not used by helper of TT GJ16AV9886 | 3.15 | Housekeeping & PPE usage checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146319 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146319 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146319 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146319 | AUD-2026-07-2000016503ACN-2026-07-4000146319 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 56
KAPIL DEV | 2026-09-26 | SINGH KUNAL | 2026-09-26 | Training has been provided to TT crew on usage of PPE complaince. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146322 | Closed | SINGH KUNAL | 2026-09-26 | • Training to be given to be TT Crew for usage of PPE. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016503ACN-2026-07-4000146322 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146322 | 2026-09-10 21:00 | 38.8788 | 390 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146322 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146322 | AUD-2026-07-2000016503ACN-2026-07-4000146322 | 21 | 21 | 27 | 80 | 0 | -26 | 50 | 56
|  | SUNITA | 2026-09-26 | Emergency Evacution gate of Mahul Terminal is through Lube Refinery gate. This gate is regular in use and there is no unauthorizedparking there. At Entry gate of Mahul Vehiles are those only lined up for entry. Hence this point is closed. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152239 | Completed | SUNITA | 2026-09-26 | CISF does not do check vehile satnding outside gates leading to blockage of emergency gates. Location has informed head security MR | 6.3 | CISF still does not do check vehile satnding outside gates leading to blockage of emergency gates | 1585 | MAHUL TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152239 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152239 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152239 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152239 |  | AUD-2026-07-2000016410ACN-2026-09-4000152239 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-26 | Non Sparking tools procured for wagon gantry and deployed. | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152911 | Completed | SUNITA | 2026-09-26 | To purchase the Non Sparking tool & make availble in TWG during Class A product Loading. | 6.1 | Since MS Wagon Loading will be started in TWG, 100% compliance for using Non sparking tools | 1585 | MAHUL TERMINAL | Location to take NPCB | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017701ACN-2026-09-4000152911 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152911 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152911 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152911 |  | AUD-2026-09-2000017701ACN-2026-09-4000152911 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-26 | Continuous follow up is maintained with Mumbai Refinery Security in charge HR department for patrolling internal and external routes. Communication trails attached with. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152237 | Completed | SUNITA | 2026-09-26 | CISF does not do outside boundary patroling. Location has taken up with Head security MR | 6.1 | CISF still does not do outside boundary patroling | 1585 | MAHUL TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152237 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152237 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152237 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152237 |  | AUD-2026-07-2000016410ACN-2026-09-4000152237 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-26 | Continuous follow up is maintained with Mumabi Refinery HR dept Security incharge for CISF related issues such as patroling internal and external routes, lady guard availability, night patroling etc. Records attached. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152238 | Completed | SUNITA | 2026-09-26 | CISF Does not do inside night patroling. Location has taken up with head security MR | 6.2 | CISF still Does not do inside night patroling | 1585 | MAHUL TERMINAL | Location to maintain follow up | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016410ACN-2026-09-4000152238 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152238 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152238 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152238 |  | AUD-2026-07-2000016410ACN-2026-09-4000152238 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-09-26 | Field hooters added for UG tank farm HCD. All ESD connected with siren. Records attached. Dyke drain hooters not availability covered in point no. 5.2 of audit dt 09.03.2026 which is kept open till compliance. Accordingly, this point is closed. | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-09-4000152910 | Completed | SUNITA | 2026-09-26 | Field Hooters not availble for HCD/ESD and Dyke drains | 5.2 | Functioning of all Hooters in control room | 1585 | MAHUL TERMINAL | Location to take NPCB | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017701ACN-2026-09-4000152910 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152910 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152910 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152910 |  | AUD-2026-09-2000017701ACN-2026-09-4000152910 | 21 |  | 27 | 80 | 28 | 28 | 83
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-08-22 | TWD HSD-1 pump has not yet been attended as HSD-2 motor winding was burnt and HDS-1 was the only pump avaiable for rake unloading. However vendor visit has been completed and will be attended as the HSD-2 pump is amde functional. | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131395 | Closed | KUMAR ATUL | 2026-08-22 | Tank wagon decantation pump-01 for HSD has abnormal sound from the pump | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | The Tank Wagon Decantation Pump-01 for HSD is observed to be generating abnormal sound, indicating a possible bearing-related issue. The same should be inspected and attended on priority | SOD | Marketing | NCR | 2026-07-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-30 | AUD-2026-05-2000012753ACN-2026-05-4000131395 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131395 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131395 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131395 | AUD-2026-05-2000012753ACN-2026-05-4000131395 | 21 | 21 | 27 | 80 | 1 | 1 | 48 | 56
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-08-22 | Audit observations are being closed by close monitoring ans below is the status: 1. MDSA 47 closed 3 pending( Under compliance) 2. SSA- all 28 points closed 3. OISD- all 49 points closed 4. T4S- 24 complied out of 40 | BAITALPUR IRD Q1 SENIOR MGMT INSPECTION | 2026-05-16 17:30 | AUD-2026-05-2000012753 | 2026-05-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131389 | Closed | KUMAR ATUL | 2026-08-22 |  | 3.18 | OISD/MDSA/SSA/T4S compliance reviewed | 1313 | BAITALPUR DEPOT | Expedite compliance of all the pending audit observations through close monitoring | SOD | Marketing | NCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S1 | F4 | 2026-06-30 | AUD-2026-05-2000012753ACN-2026-05-4000131389 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012753ACN-2026-05-4000131389 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-05-2000012753 - ACN-2026-05-4000131389 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012753ACN-2026-05-4000131389 | AUD-2026-05-2000012753ACN-2026-05-4000131389 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 56
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-03-25 | Partition provided and the plates were cut in proper shape for the easy lifting. Handles have been provided in each sheet for ease of lifting | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122039 | Closed | KUMAR ATUL | 2026-03-25 | Cover plates of sand pits are huge size irregular shaped plates. Hence not covering pit properly, rather kept stacked and dumped (this observation was there in Nov 25 also) | 6.15 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122039 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122039 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122039 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122039 | AUD-2026-02-2000011111ACN-2026-02-4000122039 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 56
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-07-30 | Seperate holes have been made in the earth stip and all earthin connections have been connected to seperate points. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122040 | Closed | KUMAR ATUL | 2026-07-30 | Multiple earthing connection from same point found near light pole near RW harvesting facility. | 6.16 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122040 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122040 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122040 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122040 | AUD-2026-02-2000011111ACN-2026-02-4000122040 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 56
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-03-14 | All trees near boundary wall & before admin building have been trimmed | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122041 | Closed | KUMAR ATUL | 2026-03-14 | Tree branches were obstructing lights from street light poles towards backside of the tank farm. Similar is the case with street light poles in front of the Admin building. Lux level details are as per report. | 6.17 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122041 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122041 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122041 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122041 | AUD-2026-02-2000011111ACN-2026-02-4000122041 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 56
VIKAS CHANDRA | 2026-09-26 | KUMAR ATUL | 2026-07-30 | SOp for STP has been taken from the OEM vendor and now is abvailable at the location. | SR MANAGEMENT INSPECTION BTL Q4 25-26 | 2026-02-07 17:00 | AUD-2026-02-2000011111 | 2026-02-06 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122042 | Closed | KUMAR ATUL | 2026-07-30 | No SOP was there for STP. | 6.18 |  | 1313 | BAITALPUR DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011111ACN-2026-02-4000122042 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011111ACN-2026-02-4000122042 | 2026-09-26 17:30 | 23.0247 | 390 | >20 | AUD-2026-02-2000011111 - ACN-2026-02-4000122042 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011111ACN-2026-02-4000122042 | AUD-2026-02-2000011111ACN-2026-02-4000122042 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 56
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154041 | Open |  |  | 02 points pertaining to previous inspection are pending. 1 pertaining to Dip Elimnination and 1 pertaining to closure of MDSA Auditobservations. | 1.4 | Earlier action points status checked | 1424 | JABALPUR DEPOT | To be closed on priority. | SOD | Marketing | CEN | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017560ACN-2026-09-4000154041 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154041 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154041 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154041 |  | AUD-2026-09-2000017560ACN-2026-09-4000154041 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154043 | Open |  |  | Lux level checked at TT Gantry, Control Room Admn Bldg, Calibration shed, TLF and TWD Pump House, MCC Room, Transformer Yard, HT Room. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1424 | JABALPUR DEPOT | Additional light fixtures to be provided at Transformer Yard, HT Room. One light to be replaced at TWD Pump house. | SOD | Marketing | CEN | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017560ACN-2026-09-4000154043 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154043 | 2026-09-26 17:30 | 23.0247 | 409 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154043 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154043 |  | AUD-2026-09-2000017560ACN-2026-09-4000154043 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154045 | Open |  |  | Yes, operated thru cleaner of TT No: MP22 H 1452. However, the cleaner couldn't operate the same. | 2.14 | TT crew fire extinguisher usage checked | 1424 | JABALPUR DEPOT | Training to be imparted to TT crew and make them more aware about Fire Extinguisher operation and other Safety aspect. | SOD | Marketing | CEN | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154045 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154045 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154045 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154045 |  | AUD-2026-09-2000017560ACN-2026-09-4000154045 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154046 | Open |  |  | Yes, checked. Physcial gauging was done for TK23 (MS), TK20 (HSD)and TK18 Ethanol UG Tank. | 3.7 | Inventory physical dip of minimum two tanks taken | 1424 | JABALPUR DEPOT | Reference height board to be displayed at Top of tank. | SOD | Marketing | CEN | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017560ACN-2026-09-4000154046 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154046 | 2026-09-26 17:30 | 23.0247 | 409 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154046 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154046 |  | AUD-2026-09-2000017560ACN-2026-09-4000154046 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154047 | Open |  |  | Location achieved 95% performance in the month of August 2026. | 3.8 | Auto vs Manual reconciliation checked | 1424 | JABALPUR DEPOT | Location is advised to ensure achieving performance more than 98% | SOD | Marketing | CEN | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154047 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154047 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154047 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154047 |  | AUD-2026-09-2000017560ACN-2026-09-4000154047 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154048 | Open |  |  | Yes checked. Vegetation to be removed along boundar wall, Rly siding area. | 3.16 | Earth pits / boundary / vegetation control checked | 1424 | JABALPUR DEPOT | Vegetation to be removed along boundary wall, Rly siding area. | SOD | Marketing | CEN | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154048 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154048 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154048 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154048 |  | AUD-2026-09-2000017560ACN-2026-09-4000154048 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154049 | Open |  |  | Only 1 MOC open as on date for TK22 for VFT Maintenance. | 3.17 | MOC status reviewed | 1424 | JABALPUR DEPOT | MOC to be closed on top priority. Likely to be closed by 31.10.2026. | SOD | Marketing | CEN | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154049 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154049 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154049 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154049 |  | AUD-2026-09-2000017560ACN-2026-09-4000154049 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154550 | Open |  |  | Nil OISD and SSA points are open. Comprehensive MDSA was carried out in Dec' 2025, wherein out of 40 points, 25 points are compliedand 15 are still open. Targeted to complete it by Dec' 2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1424 | JABALPUR DEPOT | Location to expedite closure of remaining 15 open points in time bound manner. | SOD | Marketing | CEN | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017560ACN-2026-09-4000154550 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154550 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154550 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154550 |  | AUD-2026-09-2000017560ACN-2026-09-4000154550 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154551 | Open |  |  | Scrap disposal of 2 nos. AG Tanks of FO is withheld in order to get clarity from DS SBU. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1424 | JABALPUR DEPOT | The scattered material lying in old tank farm area to be stacked properly at one place. | SOD | Marketing | CEN | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154551 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154551 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154551 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154551 |  | AUD-2026-09-2000017560ACN-2026-09-4000154551 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154552 | Open |  |  | Nil | 6.1 | High priority areas requiring immediate action. | 1424 | JABALPUR DEPOT | Location is advised to pursue following 2 projects: 1) Construction of 3 x 180 KL UG Tanks 2) Construction of 4500 KL A/G HSD Tank | SOD | Marketing | CEN | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017560ACN-2026-09-4000154552 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154552 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154552 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154552 |  | AUD-2026-09-2000017560ACN-2026-09-4000154552 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154392 | Open |  |  | For any long peding issue, location is requested to ensure the followings: 1) 1st three mails by officer concerned. Officer shouldmention relevant tender clause against which HPCL is asking job completion. In 3rd letter, penalty clause can also be added. 2) Call for MOM either through VC or in physical mode. Mail should be sent by LIC for meeting. 3) If there is still no response, mail should go from Zone for meeting. If meeting is conducted, MOM to be made and to be signed by both the parties. Zone should also take part in meeting. 4) If no response, SCN to be issued by Zone. Above is applicable for all vendors including TAS, CCTV, EM lock, VTS, MB Lal Equipment AMC etc | 1.3 | Pending issues reviewed | 1278 | JODHPUR TERMINAL | Location to follow this practice | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154392 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154392 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154392 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154392 |  | AUD-2026-09-2000017808ACN-2026-09-4000154392 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154393 | Open |  |  | Yes. Old lubes are required to be liquidated on priority. Location is not able to carry out cycle count. Some lubes in containers, were bulked in drum. This is not accounted in SAP. Location needs to coordinate with Lube SBU and get the issue resolved at the earliest. Toll tax payment is pending. | 1.4 | Earlier action points status checked | 1278 | JODHPUR TERMINAL | 1) Cycle count to be done for all packed items after accounting lube bulked in barrel. 2) Toll tax payment to be ensured. Pls sendletter to all DCT/transporter to submit their toll related documents. This should be taken on priority. | SOD | Marketing | NWF | 2026-11-15 |  | 12 |  | S3 | F4 | 2026-11-15 | AUD-2026-09-2000017808ACN-2026-09-4000154393 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154393 | 2026-09-25 20:45 | 23.8893 | 440 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154393 | 532 | 8294 | 21 | 8294 | -26 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154393 |  | AUD-2026-09-2000017808ACN-2026-09-4000154393 | 21 |  | 27 | 80 | 0 | 0 | 63
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154394 | Open |  |  | Location has been advised to focus on Samridhi 2.0. Pls make drive of reporting UA and US in this week by contract labour/securityguard/TT crew. Let them report through suggestion scheme. Give award to persons for maximum reporting. It is observed that location is not following circular of Award on small wins. This is very much required to motivate workforce. We should not limit ourselves to give award during Independance Day and Republic day. There is circular to give month award to TT crew of Rs.1000 and quarterly award to contract labour of Rs.1000. | 1.8 | Improvement plans discussed | 1278 | JODHPUR TERMINAL | 1. Location has been advised to focus on Samridhi 2.0. 2. Pls make drive of reporting UA and US in this week by contract labour/security guard/TT crew. Let them report through suggestion scheme. Give award to persons for maximum reporting. 3. e-diary reporting is less. LIC to note 5 e-ediaries per day. Make round of locations twice in a day. If any issue is observed, pls inform through e-diary to officer. 4. Location is requested to increase frequency of award ceremony as per small win circular. This will help to motivate workforce. 5. Location should also display best officer (on monthly basis) and best contract labour at prominent place. This will encourage our workforce to do better. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154394 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154394 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154394 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154394 |  | AUD-2026-09-2000017808ACN-2026-09-4000154394 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154395 | Open |  |  | Yes being done. VRU area not done. TK5 and TK6 to be done | 2.1 | Fire drill conducted in last 6 months (surprise) | 1278 | JODHPUR TERMINAL | Pls carry out fire drill in VRU area and TK5/6 tank farm. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154395 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154395 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154395 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154395 |  | AUD-2026-09-2000017808ACN-2026-09-4000154395 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154396 | Open |  |  | Double contingency simulated on 9th Sept. One was leakage scenario in bay 16 and 2nd was fire scenario in pump no. 3 at PH. Mr. Rathore was made as an observer; Observation recorded as below: 1. Equipment worked well and foam generation was good. 2. There were good coordination among team members. 3. Person who attended to check LEL, he should be backed with fire hose in ready condition. He should also be wrapped with rope for pulling him in case of emergency. 4. Security guard needs to direct fire tender and TTs to move properly. 5. Security guard should use whistle for better attention. 6. Location should check drain and ETP for checking of product seepage. 7. Team member didn't tell anything about information given to outsider. | 2.2 | Double contingency scenario simulated; observations recorded | 1278 | JODHPUR TERMINAL | Pls keep one officer as observer. LIC can also become observer. You may also engage IOC/BPC officer as an observer. Work on improvements. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154396 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154396 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154396 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154396 |  | AUD-2026-09-2000017808ACN-2026-09-4000154396 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154397 | Open |  |  | Surprise night inspection is carried out. It is not done for Sept 2026 | 2.4 | Security alertness checked (night-halt / surprise checks) | 1278 | JODHPUR TERMINAL | Location to carry out surprise night inspection for Sep 26. Location officer needs to mention time of inspection also in their record. | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154397 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154397 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154397 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154397 |  | AUD-2026-09-2000017808ACN-2026-09-4000154397 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154398 | Open |  |  | Reviewed the same. 1. It is advised to get the workforce trained by called personnel from Fire Brigade office. 2. It is also advised to have security coordination committee meeting with Police personnel, mutual aid members and statutory authorities. 3. Fit for road campaign not done for H1 | 2.5 | Emergency response preparedness reviewed | 1278 | JODHPUR TERMINAL | Reviewed the same. 1. It is advised to get the workforce trained by called personnel from Fire Brigade office. 2. It is also advised to have security coordination committee meeting with Police personnel, mutual aid members and statutory authorities in Q3 3.Fit for road campaign to be conducted. | SOD | Marketing | NWF | 2026-11-30 |  | 12 |  | S3 | F4 | 2026-11-30 | AUD-2026-09-2000017808ACN-2026-09-4000154398 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154398 | 2026-09-25 20:45 | 23.8893 | 455 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154398 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154398 |  | AUD-2026-09-2000017808ACN-2026-09-4000154398 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154399 | Open |  |  | VA alerts were high in Jodhpur. Location to keep check on all kind of VA alerts. Location to see that they receive visual/audio alarm in security gate as well as alert through SMS/whatsapp for any VA alert. | 2.7 | VA alerts checked / analysed | 1278 | JODHPUR TERMINAL | VA alerts were high in Jodhpur. Location to keep check on all kind of VA alerts. Location to see that they receive visual/audio alarm in security gate as well as alert through SMS/whatsapp for any VA alert. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154399 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154399 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154399 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154399 |  | AUD-2026-09-2000017808ACN-2026-09-4000154399 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154600 | Open |  |  | Checked HVLR 08 and 06. HVLR 08 not reaching tank. One WCFM checked. Found working. W&M seal of all prover tanks (fixed) checked and found okay. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1278 | JODHPUR TERMINAL | HVLR 08 to be repaired on priority. Foam + water is not reaching tank top. | SOD | Marketing | NWF | 2026-09-30 |  | 12 |  | S3 | F4 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154600 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154600 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154600 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154600 |  | AUD-2026-09-2000017808ACN-2026-09-4000154600 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154601 | Open |  |  | 1. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1278 | JODHPUR TERMINAL | 1. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154601 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154601 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154601 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154601 |  | AUD-2026-09-2000017808ACN-2026-09-4000154601 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154602 | Open |  |  | Yes it is there. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1278 | JODHPUR TERMINAL | It is suggested to maintain control register for training of all stakeholders inside terminal. 1st column should be name of all regular contract labour/security guards/TT crew (with TT no.). 2nd column should be date of training and 3rd column should be Topic of training given. This register will ensure that whether 100% stakeholders are trained and they are trained in almost all topics. Thisis also required to maintain as per oisd audit recom 2026. | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154602 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154602 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154602 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154602 |  | AUD-2026-09-2000017808ACN-2026-09-4000154602 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154603 | Open |  |  | 1. Pls purchase snellen chart (eye chart) to check whether drivers are able to read through some distance even after wearing spectacle. | 2.16 | Eyesight / colour-blindness awareness checked | 1278 | JODHPUR TERMINAL | 1. Pls purchase snellen chart (eye chart) to check whether drivers are able to read through some distance even after wearing spectacle. | SOD | Marketing | NWF | 2026-09-30 |  | 12 |  | S3 | F4 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154603 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154603 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154603 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154603 |  | AUD-2026-09-2000017808ACN-2026-09-4000154603 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154604 | Open |  |  | Checked dip of following TTs: 1. RJ19GC3900: ok/ok/+2 mm, This TT is about to complete 15 years. Branding not okay 2. RJ24GA3946:ok/+1 mm/ok 3. RJ35GA0999: -1 mm/ok/+2 mm/+1 mm 4. RJ07GD6927: ok/ok/+1 mm 5. RJ19GA0342: /ok/ok/+1 mm Bay combination: 1 to 4 and 8: MS/HSD/Ethanol 5 and 6: HSD express bay bay 7: HSD and SKO (both bottom loading), one more top loading arm of HSD is there. Bay 4 is having B7 loading facility. | 3.2 | Post-loading dip checks verified | 1278 | JODHPUR TERMINAL | 1) MFM of bay 5 is to be recalibrated. 2) Location is maintaining gantry maintenance register. Hiwever, it is not reviewed by LIC and TAS officer. It needs to be reviewed by M&I Officer and TAS officer once in a week and by LIC once in a month. 3. Location to purchase device to check working condition of overspill sensor of TT. | SOD | Marketing | NWF | 2026-10-31 |  | 12 |  | S3 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154604 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154604 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154604 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154604 |  | AUD-2026-09-2000017808ACN-2026-09-4000154604 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154605 | Open |  |  | Identify 3 most suspected multiple loaded TT stoppage point per month. Issue letter to transporters/DCT. Take explanation in writing. Talk to TT crew/transport manager. If any suspicion observed, pls inform to Security advisor and Police in writing with a copy toZone. This needs to be done every month. Make excel sheet. 1st column should be 3 suspected points. 2nd column contain TT and transporter details, 3rd column is reply of DCT/transporters, 4th column is explanation given by TT crew verbally during one to one discussion, 5th column is comment from informer (if sent) No. of blocking in Aug is 7, no. of blocking in July is 14, It is 15 in June 26. Good that location has improved. Pls maintain this. | 3.3 | VTS deviations reviewed | 1278 | JODHPUR TERMINAL | 1. Identify 3 most suspected multiple loaded TT stoppage point per month. Issue letter to transporters/DCT. Take explanation in writing. Talk to TT crew/transport manager. If any suspicion observed, pls inform to Security advisor and Police in writing with a copyto Zone. This needs to be done every month. Make excel sheet. 1st column should be 3 suspected points. 2nd column contain TT and transporter details, 3rd column is reply of DCT/transporters, 4th column is explanation given by TT crew verbally during one to one discussion, 5th column is comment from informer (if sent). 2. TT outside terminal radius case is 273. Pls take up with AOT. This willdelay TT loading. Pls take up strongly. | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154605 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154605 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154605 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154605 |  | AUD-2026-09-2000017808ACN-2026-09-4000154605 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154606 | Open |  |  | Checked ethanol blending performance in TT no. RJ38GA1163 and RJ24GA3895. Top sample 18.5+1.07= 19.57%, bottom sample: 18.5+1.07= 19.57% | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1278 | JODHPUR TERMINAL | Location informed that there is one bio diesel PO of 200 KL. Sample has failed for this vendor. Joint sampling is going on. Location is requested to keep close watch on the same. Location is also requested to consume all bio diesel qty by blending it with HSD. For any issue, location may write to GM O&D. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154606 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154606 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154606 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154606 |  | AUD-2026-09-2000017808ACN-2026-09-4000154606 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154607 | Open |  |  | EM locks checked by intelligent key. Results are as follows: 1. RJ19GJ5883: HE17855 Ok/not ok, HE17856: Ok/OK (tpt TT) 2. RJ14GP8176: HE9306: ok/OK, HE9305: Ok/OK (DCT TT) 3. RJ50GA3837: HE17598: ok/OK, HE17597: ok/OK (DCT TT) 4. RJ54GA1442: HE17956 ok/ok, HE17955 ok/not ok (Tpt TT) | 3.5 | EM Lock SOP compliance verified | 1278 | JODHPUR TERMINAL | Location in charge has checked only 34 locks in last 3 months. Location needs to increase checking of EM lock by intelligent key. Record to be maintained. 12 locks are not okay. Give list of defaulters (whose one or both locks are not ok) to transport handling person. Let him issue letter to transporter for any ITDG violations (like route deviation, stoppage violation, speed violation etc). Identify two defaulters among them whose Tts are having maximum ITDG violations. Send lock of these two defaulters to 3rd party for checking of any tampering. If lock is found tampered, take ITDG action as per guidelines. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154607 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154607 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154607 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154607 |  | AUD-2026-09-2000017808ACN-2026-09-4000154607 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154608 | Open |  |  | Checked and found okay. There is loss in ethanol receipt. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1278 | JODHPUR TERMINAL | 1. Location to maintain opening dip and closing dip of AG ethanol tank before and after unloading of each ethanol TT. Pls cross check the volume actually unloaded with TT capacity. Note the same in regsiter and export it in excel sheet also for filtering. 2. Open dome cover of ethanol TT for checking inside compartment. Location is requested to check two dome covers of one TT per week. 3. Location to inform zone if shortage of more than 200 litre is reported in TT. 4. It was discussed that there is heat loss during blending of petrol with ethanol. This reduces the temp. of gasohol. The same is not recorded by MFM. It was informed that MFM records gasohol temp at 80/20 ratio of MS and ethanol line temp. Pls cross check the same for three TTs and share the actual result. Pls also check temp of gasohol in these three TTs using cup thermometer (to ensure minimum delay in measurement of temp.). | SOD | Marketing | NWF | 2026-10-31 |  | 15 |  | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154608 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154608 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154608 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154608 |  | AUD-2026-09-2000017808ACN-2026-09-4000154608 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154609 | Open |  |  |  | 3.7 | Inventory physical dip of minimum two tanks taken | 1278 | JODHPUR TERMINAL | There is variation observed more than tolerance limit in water level and gross level. Temp and density not checked by me. Location should cross verify this also. | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154609 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154609 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154609 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154609 |  | AUD-2026-09-2000017808ACN-2026-09-4000154609 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154610 | Open |  |  | 1. Last R3 has improved in sept 2026. It needs to be maintained. 2. There is stiff throughput target for location. Location to check whether MDP is in line with throughput target. If due to any reason, location is not meeting MDP, pls keep the reason recorded monthwise. We shall have to take up with HQO to revise throughput target and hence OPEX target. 3. CAT A performance was 88% in Aug 2026. It has improved in Sept 2026. Now it is 98.02%. Pls maintain >95% performance | 3.8 | Auto vs Manual reconciliation checked | 1278 | JODHPUR TERMINAL | There is stiff throughput target for location. Location to check whether MDP is in line with throughput target. If due to any reason, location is not meeting MDP, pls keep the reason recorded monthwise. We shall have to take up with HQO to revise throughput target and hence OPEX target | SOD | Marketing | NWF | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154610 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154610 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154610 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154610 |  | AUD-2026-09-2000017808ACN-2026-09-4000154610 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154611 | Open |  |  | a. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise.I have shared the format with Meenakshi. At the time of checking manual dip of tanks, location to compare the manual dips/temp. taken with TAS dip/temp. Location to mention TAS dip/temp also along with manual dip in gauge book whenver PLT is taken. b.. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. d. There is loss in ethanol and HSD. 119 Kl cum loss in HSD. Loss of 11 kl in ethanol in Aug 26. It is in higher side. Location needs to monitor the stock loss in both the products. | 3.9 | Abnormal variations / unused assets reviewed | 1278 | JODHPUR TERMINAL | a. Location needs to maintain PLT loss gain report regularly and should share the report with zone on monthly basis batch wise, product wise. I have shared the format with Meenakshi. At the time of checking manual dip of tanks, location to compare the manual dips/temp. taken with TAS dip/temp. Location to mention TAS dip/temp also along with manual dip in gauge book whenver PLT is taken. b.. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. d. There is loss in ethanol and HSD. Location needs to monitor the stock loss in both the products. | SOD | Marketing | NWF | 2026-09-30 |  | 15 |  | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154611 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154611 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154611 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154611 |  | AUD-2026-09-2000017808ACN-2026-09-4000154611 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154612 | Open |  |  | TK25 radar is to be replaced/repaired through AST. It is not in working condition. TFMS SAP performance in Aug 26 is 87.18%.It should be min 95%. | 3.10 | TFMS/SAP reconciliation checked | 1278 | JODHPUR TERMINAL | 1. Location has been informed about the cases where ITT can be done in SAP. Pls ensure that. 2. TK25 radar is to be brought in operation. There is manual reco of this tank at present. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154612 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154612 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154612 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154612 |  | AUD-2026-09-2000017808ACN-2026-09-4000154612 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154613 | Open |  |  | 1. There are 4 contract staffs working inside Admin Building. Two at planning room. Two are working as office boy. It is advised toshift two contract staffs from office to housekeeping jobs c. Driver of emergency vehicle can be utilised to maintaiun register insecurity gate (if he is educated). This is my suggestion. d. Electrical maintenance PO needs to be revised. One electrician to be called in each shift. General shift electrician should not be paid on manpower basis. It should be on job basis. | 3.15 | Housekeeping & PPE usage checked | 1278 | JODHPUR TERMINAL | 1. There are 4 contract staffs working inside Admin Building. Two at planning room. Two are working as office boy. It is advised toshift two contract staffs from office to housekeeping jobs c. Driver of emergency vehicle can be utilised to maintaiun register insecurity gate (if he is educated). This is my suggestion. d. Electrical maintenance PO needs to be revised. One electrician to be called in each shift. General shift electrician should not be paid on manpower basis. It should be on job basis | SOD | Marketing | NWF | 2026-12-31 |  | 10 |  | S2 | F5 | 2026-12-31 | AUD-2026-09-2000017808ACN-2026-09-4000154613 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154613 | 2026-09-25 20:45 | 23.8893 | 486 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154613 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154613 |  | AUD-2026-09-2000017808ACN-2026-09-4000154613 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154614 | Open |  |  | MOC to be made for Bharti Kumari and Deepak Sharma as new joining | 3.17 | MOC status reviewed | 1278 | JODHPUR TERMINAL | MOC to be made for Bharti Kumari and Deepak Sharma as new joining | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154614 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154614 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154614 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154614 |  | AUD-2026-09-2000017808ACN-2026-09-4000154614 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154615 | Open |  |  | OISD points were reviewed. Target date assigned for all points along with name of responsible officer | 3.18 | OISD/MDSA/SSA compliance reviewed | 1278 | JODHPUR TERMINAL | 1. Mr. Kushagra to share status of OISD points to LIC every 10 days and every month to Zone. He needs to collect status of job fromother officers and submit the consolidated details to LIC/Zone. 2. All points are to be complied by Dec 2026. Location should notwait for final report to come. 3. Tendering is to be done by 7th Oct 2026 for following two jobs: a. SIL certification study. Plsrefer relevant observation by ESA team. b. Capacitance based earthing 4. Approx 16 lakh payment is still balance to be paid (as informed by officers). These are the payment against job done before OISD audit. Out of 16 lakh payment, approx 1.5 lakh payment is against non PO. Balance are job against PO. Location is advised to release all payment. ls ask for bills from vendor. | SOD | Marketing | NWF | 2026-12-31 |  | 15 |  | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017808ACN-2026-09-4000154615 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154615 | 2026-09-25 20:45 | 23.8893 | 486 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154615 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154615 |  | AUD-2026-09-2000017808ACN-2026-09-4000154615 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154616 | Open |  |  | Interacted with TT crew. It is suggested: 1. TT crew should be asked to wear uniform. 2. They should always keep their ID card and display the same. 3. Driver sign is not being taken in TT In/out register. Respective column was found without signed. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1278 | JODHPUR TERMINAL | 1. TT crew should be asked to wear uniform. 2. They should always keep their ID card and display the same. 3. Driver sign is notbeing taken in TT In/out register. Respective column was found without signed. 4. No. of UA, US and NM reported from Apr-Aug 2026 are 2, 20 and 2 respectively. It is very less and not acceptable. Suggestion box to be opened on monthly basis and give award to stakeholders for best suggestions. This should be recorded in regsiter/file with photograph. Contract labours, security guards, TT crew are to be motivated to report unsafe acts, unsafe situation and near misses through suggestion scheme. They should be rewarded suitably. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154616 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154616 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154616 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154616 |  | AUD-2026-09-2000017808ACN-2026-09-4000154616 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154617 | Open |  |  | 1. Pls share details of all spare cable with rating and length of cable. 2. Marble/Tiles of TT gantry bays are found damaged. It needs to be repaired. 3. Ensure good look of Terminal from outside. a. Main gate needs to be cleaned. It may be painted, if rusting observed. b. Barriers, which are used to block vehicle movement, are required to be painted. c. Civil structure of main gate (atthe top), plastering to be done at few places. The same needs to be painted after plaster. d. Safety ploicy is written on boundary wall near main gate. This has got fed and needs to be repainted. e. Vegetation observed near drain along boundary wall just outside main gate. It needs to be removed. f. All vehicles to be parked designated place only, not outside main gate. Security to ensure. 4.Ethanol unloading hose in bay 7, needs to be replaced. 5. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. 6. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1278 | JODHPUR TERMINAL | 1. Pls share details of all spare cable with rating and length of cable. 2. Marble/Tiles of TT gantry bays are found damaged. It needs to be repaired. 3. Ensure good look of Terminal from outside. a. Main gate needs to be cleaned. It may be painted, if rusting observed. b. Barriers, which are used to block vehicle movement, are required to be painted. c. Civil structure of main gate (atthe top), plastering to be done at few places. The same needs to be painted after plaster. d. Safety ploicy is written on boundary wall near main gate. This has got fed and needs to be repainted. e. Vegetation observed near drain along boundary wall just outside main gate. It needs to be removed. f. All vehicles to be parked designated place only, not outside main gate. Security to ensure. 4.Ethanol unloading hose in bay 7, needs to be replaced. 5. It is advised to get filled check list by electricain for all potential hazard areas in following checks: i) Cable gland is intact, not oversize, armour is not visible, entering straight to panel/JB without bend. ii) There is no hole/opening in FP panel, JB. There is no missing allen screw, FP panel cover is fully tight. iv) There is earthing of structure/panel/pump/equipment as per site visited. v) Cables are dressed properly. vi) Eathing jumper is there and intact in all flanges. vii) Earth pit in that area is okay as per design and spec. It is advised to get the same verified by electricians for each of the areas (at least two areas per week). Let them fill check list in Hindi and submit the same to M&I officer for corrective actions. Records should be maintained. 6. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record.Pls share details of allspare cable with rating and length of cable. | SOD | Marketing | NWF | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017808ACN-2026-09-4000154617 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154617 | 2026-09-25 20:45 | 23.8893 | 455 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154617 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154617 |  | AUD-2026-09-2000017808ACN-2026-09-4000154617 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154618 | Open |  |  | Checked MOV and ROSOV working in remote. All ROSOVs are in remote mode. One MOV of HSD, one MOV of MS for TK29 were in local mode. Some more MOVs were found in local mode. Location reverted that MOVs of tank under receipt are kept in local by Pipeline Dept. They forget to switch these MOVs from local to Auto. This practice is not good | 4.2 | Maintenance activities reviewed | 1278 | JODHPUR TERMINAL | 1. Bring all MOVs in remote mode. We have invested considerable amount at Jodhpur IRD in 2025-26 and 2026-27 for this only. 2. There should be SOP to bring MOV from local to remote whenever tanks are taken over from pipeline to Terminal. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154618 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154618 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154618 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154618 |  | AUD-2026-09-2000017808ACN-2026-09-4000154618 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154619 | Open |  |  | Checked working condition of all pumps in PH. All are working. There is one very good shed in vacant condition. This shed was used to keep RO system. Location should use this shed to keep additive drums. Some space should be kept to store fire fighting materials as the same is in very strategic place. VFD is in working condition for all 3 products | 4.4 | Quality of PM compliance reviewed | 1278 | JODHPUR TERMINAL | There is one very good shed in vacant condition. This shed was used to keep RO system. Location should use this shed to keep additive drums. Some space should be kept to store fire fighting materials as the same is in very strategic place. | SOD | Marketing | NWF | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154619 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154619 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154619 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154619 |  | AUD-2026-09-2000017808ACN-2026-09-4000154619 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154620 | Open |  |  | All scraps have been identified. Light MS is to be divided in two lots. Plates of retail region are not kept properly. All platesare to be lifted by using hydra. It needs to be kept above ground by keeping it over some scrap materials. This will increase life of MS plates. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1278 | JODHPUR TERMINAL | Location to prepare e-RFD and dsipose all scrap materials. All plates are to be lifted by using hydra. It needs to be kept aboveground by keeping it over some scrap materials. This will increase life of MS plates. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154620 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154620 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154620 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154620 |  | AUD-2026-09-2000017808ACN-2026-09-4000154620 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154621 | Open |  |  | It was found in working condition. However Fire engine display (both FE) are not in working condition since last 4 months. Fire engine log book and DG log book are well maintained | 6.1 | Fire engine | 1278 | JODHPUR TERMINAL | Fire engine display is to be brought in working condition. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154621 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154621 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154621 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154621 |  | AUD-2026-09-2000017808ACN-2026-09-4000154621 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154622 | Open |  |  | It is advised to monitor diesel consumption in fire engine and DG. Location can maintain monthly record as per the followings: i)Opening physical inv of HSD in DG tanks; ii) HSD given to DG tank in that month: iii) No. of hrs run by individual DG in zero load, no. of hrs run by individual DG in full load iv) Diesel consumption per hr as communicated by OEM for individual DG in no load and full load respectively. v) HSD consumed theoritically vi) Closing book stock of HSd in DG tank vii) Physical closing stock of HSD in DG tank | 6.2 | Additive stock monitoring | 1278 | JODHPUR TERMINAL | It is advised to monitor diesel consumption in fire engine and DG. A) Location can maintain monthly record as per the followings: i) Opening physical inv of HSD in DG tanks; ii) HSD given to DG tank in that month: iii) No. of hrs run by individual DG in zeroload, no. of hrs run by individual DG in full load iv) Diesel consumption per hr as communicated by OEM for individual DG in no load and full load respectively. v) HSD consumed theoritically vi) Closing book stock of HSd in DG tank vii) Physical closing stockof HSD in DG tank B) In the similar way location should keep control register for Company vehicle being used at present. They should monitor diesel consumption on monthly basis by Company Jeep. LIC should sign the same. | SOD | Marketing | NWF | 2026-10-15 |  | 10 |  | S2 | F5 | 2026-10-15 | AUD-2026-09-2000017808ACN-2026-09-4000154622 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154622 | 2026-09-25 20:45 | 23.8893 | 409 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154622 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154622 |  | AUD-2026-09-2000017808ACN-2026-09-4000154622 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154623 | Open |  |  | History card is well maintained. CAMC equipment like CCTV, RSFPS, TAS etc are not maintained well. Could not find history card of TAS equipment and cctv. RSFPS though maintained, location is not mentioning the cost of spares replaced. Though, it is not payable byHPCL, location should maintain the same. | 6.3 | History card | 1278 | JODHPUR TERMINAL | History card is well maintained. CAMC equipment like CCTV, RSFPS, TAS etc are not maintained well. Could not find history card of TAS equipment and cctv. RSFPS though maintained, location is not mentioning the cost of spares replaced. Though, it is not payable byHPCL, location should maintain the same. | SOD | Marketing | NWF | 2026-09-30 |  | 10 |  | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017808ACN-2026-09-4000154623 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154623 | 2026-09-25 20:45 | 23.8893 | 394 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154623 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154623 |  | AUD-2026-09-2000017808ACN-2026-09-4000154623 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154624 | Open |  |  | One point of TAS audit, B7 point to increased. It needs to be dropped if bio diesel allocation is not much. Location has not carried out self TAS audit in H1 TAS room is located in pipeline receiving station area. This is away from Admin building. TAS officer normally sits at Admin Building only. As per rule, control room should always be manned. On questioning, location replied that TAS officers sits there in between, however, one VRU representative always sit there. | 6.4 | TAS audit | 1278 | JODHPUR TERMINAL | 1. Self TAS audit to be done in H1. 2. We cannot rely on VRU representative. It is also not advisable to share any user ID or password with VRU representative. It is dangerous. One officer can be asked to sit at control room only. | SOD | Marketing | NWF | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017808ACN-2026-09-4000154624 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154624 | 2026-09-25 20:45 | 23.8893 | 425 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154624 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154624 |  | AUD-2026-09-2000017808ACN-2026-09-4000154624 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | VISIT TO JODHPUR IRD IN Q2 | 2026-09-25 20:45 | AUD-2026-09-2000017808 | 2026-09-24 09:05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154625 | Open |  |  | Following materials were found in surplus at Jodhpur IRD: 1. Two nos. of vertical submergible pump of UG tanks. 2. ROSOV 8: one no. 3. AUMA actuator for MOV: 2 nos. in good condition 4. 20 ROSOV: Spring set to be repaired. Otherwise in very good condition 5. One no. of SS prover tank of 1000 litre in good condition 6. Pump of capacity: 288 cum/hr: 1 no., 72 cum/hr: 1 no. (very old pump, but location is saying that same are in good condition) 7. Bio Diesel dosing skid of Dencil pump and system of year 2010 8. Two pumps of SKO in PH each of 144 KL/Hr capacity, 55 m head, Kirlosker Bros make, 37 KW/50 HP motor, Model KPD/100/40/MCLM | 6.5 | Surplus materials inside store | 1278 | JODHPUR TERMINAL | Location is requested for the followings: 1. Pls repair Spring set of 20 ROSOV and keep the equipment in good condition as surplus. 2. Pls check with M/s Dencil Pump about Bio Diesel Skid pump. This is kept inside store in never used condition since year 2010. Pls revert on this pump. 3. Two pumps of 288 and 72 cum/hr are very old. Location to take a call whether to dispose it or to keep it inside store. | SOD | Marketing | NWF | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017808ACN-2026-09-4000154625 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017808ACN-2026-09-4000154625 | 2026-09-25 20:45 | 23.8893 | 486 | >20 | AUD-2026-09-2000017808 - ACN-2026-09-4000154625 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017808ACN-2026-09-4000154625 |  | AUD-2026-09-2000017808ACN-2026-09-4000154625 | 21 |  | 27 | 80 | 0 | 0 | 70
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154099 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Effective Interaction done with all officers and also newly joined officers . | 1.1 | Interaction with all officers (1–1.5 hrs) | 1636 | BALASORE DEPOT | LIC to guide the officers to learr all the domain of operations, M&I ,Safety , TAS jobs and time to time take the feedback on learning . Needs more focus on Housekeeing . | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154099 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154099 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154099 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154099 |  | AUD-2026-09-2000017509ACN-2026-09-4000154099 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154650 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | All reviewed | 1.3 | Pending issues reviewed | 1636 | BALASORE DEPOT | Complete Disposal of slow moving lubes, Plan for Removal of FO lines & Disposal of offspec FO need to be focussed . | SOD | Marketing | ECZ | 2026-11-30 |  | 4 |  | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017509ACN-2026-09-4000154650 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154650 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154650 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154650 |  | AUD-2026-09-2000017509ACN-2026-09-4000154650 | 21 |  | 27 | 80 | 12 | 12 | 65
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154651 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Advised to go through all the Manual and Circular | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1636 | BALASORE DEPOT | Advised to read the circulars & Manual | SOD | Marketing | ECZ | 2026-11-30 |  | 4 |  | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017509ACN-2026-09-4000154651 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154651 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154651 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154651 |  | AUD-2026-09-2000017509ACN-2026-09-4000154651 | 21 |  | 27 | 80 | 12 | 12 | 65
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154652 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Improvement of working of junior officers discussed and expaction of mgmt also clearly communicated | 1.8 | Improvement plans discussed | 1636 | BALASORE DEPOT | PPT on all topics (Operation, TAS , IMS , EMLOCKING , Safety , Tanks ) | SOD | Marketing | ECZ | 2026-11-30 |  | 4 |  | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017509ACN-2026-09-4000154652 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154652 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154652 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154652 |  | AUD-2026-09-2000017509ACN-2026-09-4000154652 | 21 |  | 27 | 80 | 12 | 12 | 65
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154653 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Location is falls under single contingency . HVLR NO-3 operated on 26.09.26 | 2.2 | Double contingency scenario simulated; observations recorded | 1636 | BALASORE DEPOT | Flow through was sufficient to cover the Tanks under the Dyke . Advised location to keep the Foam valve completely open . | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017509ACN-2026-09-4000154653 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154653 | 2026-09-26 17:30 | 23.0247 | 394 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154653 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154653 |  | AUD-2026-09-2000017509ACN-2026-09-4000154653 | 21 |  | 27 | 80 | 12 | 12 | 57
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154654 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | The same was checked during HVLR NO-3 operated on 26.09.26 | 2.5 | Emergency response preparedness reviewed | 1636 | BALASORE DEPOT | Flow through was sufficient to cover the Tanks under the Dyke . Advised location to keep the Foam valve completely open . | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017509ACN-2026-09-4000154654 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154654 | 2026-09-26 17:30 | 23.0247 | 394 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154654 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154654 |  | AUD-2026-09-2000017509ACN-2026-09-4000154654 | 21 |  | 27 | 80 | 12 | 12 | 57
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154655 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | CCTV footage was checked in TV available in control room and found from 25.06.2026 (90 days ) | 2.6 | CCTV functioning checked | 1636 | BALASORE DEPOT | Footage CHECKED & found okay - Out of 41 , one cxamera was out of order | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154655 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154655 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154655 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154655 |  | AUD-2026-09-2000017509ACN-2026-09-4000154655 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154656 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Found okay . However turnstile access control to Restricted area was out of order and also security frisking needs to explore at . | 2.8 | Access control systems checked | 1636 | BALASORE DEPOT | To be taken up with Godrej and Security at the Entry to license area needs to be checked during operations hrs | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154656 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154656 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154656 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154656 |  | AUD-2026-09-2000017509ACN-2026-09-4000154656 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154657 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Found okay . TK 11- 1696 KL , TK 12- 1698 KL against the(3394 KL ) requirement of 2960 KL . All level gauges working | 2.10 | Fire water levels verified | 1636 | BALASORE DEPOT | One water tank cleaning completed . Internal Painting pending . To be planned by depot in line with SOP for mutual aid with Industry | SOD | Marketing | ECZ | 2026-12-30 |  | 4 |  | S2 | F2 | 2026-12-30 | AUD-2026-09-2000017509ACN-2026-09-4000154657 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154657 | 2026-09-26 17:30 | 23.0247 | 485 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154657 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154657 |  | AUD-2026-09-2000017509ACN-2026-09-4000154657 | 21 |  | 27 | 80 | 12 | 12 | 70
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154658 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Interacted with Shri Prafulla Dakua , Driver of M/s Stalin FS. The TT Crew successfully operated FE & was aware of TREM Card and Safety precautions to be followed while transporting POL Products | 2.14 | TT crew fire extinguisher usage checked | 1636 | BALASORE DEPOT | Advised planning officer to check for all TTs on random basis and use atleast one TT Fire ext. | SOD | Marketing | ECZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017509ACN-2026-09-4000154658 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154658 | 2026-09-26 17:30 | 23.0247 | 394 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154658 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154658 |  | AUD-2026-09-2000017509ACN-2026-09-4000154658 | 21 |  | 27 | 80 | 12 | 12 | 57
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154659 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | 5 TTs checked in Bay 1,2 & 5. Dip of 4 TTs found to be inline with permissible range. For TT No - OD04V0398, Proof Level was not matching. Location to recalibrate this TT before allotting next load | 3.2 | Post-loading dip checks verified | 1636 | BALASORE DEPOT | TT No - OD04V0398, Proof Level was not matching. Location to recalibrate this TT before allotting next load .location to check first lot and also 3 TTs per officer for Dip and Safety and other Fitting . | SOD | Marketing | ECZ | 2026-09-28 |  | 4 |  | S2 | F2 | 2026-09-28 | AUD-2026-09-2000017509ACN-2026-09-4000154659 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154659 | 2026-09-26 17:30 | 23.0247 | 392 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154659 | 532 | 8294 | 21 | 8294 | 21 | 30 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154659 |  | AUD-2026-09-2000017509ACN-2026-09-4000154659 | 21 |  | 27 | 80 | 12 | 12 | 56
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154660 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Deviation mostly related to night driving , speed voilation during return trip , route deviation , Devise tampering, etc found | 3.3 | VTS deviations reviewed | 1636 | BALASORE DEPOT | These VTS deviations to be discussed in transporter meet, gate meetings . In past one month , no. of deviations reduced by 25% | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154660 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154660 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154660 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154660 |  | AUD-2026-09-2000017509ACN-2026-09-4000154660 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154661 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Lock of below TTs were checked with I Key and found Ok i.e. LED glow steadily OD01AX5297 OD01BA6521 OD01BA6377 | 3.5 | EM Lock SOP compliance verified | 1636 | BALASORE DEPOT | advised LIC to check all locks using intelligent key and have record | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154661 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154661 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154661 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154661 |  | AUD-2026-09-2000017509ACN-2026-09-4000154661 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154662 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Location to record U/G Tank dip before / after unloading of TT. In case of abnormal variation, TT to be checked in Calibration Tower. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1636 | BALASORE DEPOT | high losses to be taken up with supplier strongly . Also take the action on TT having dip correct but still losses due to manupulation in the calidration . Suspend in the IEMS portal as Discussed , in cordination with HQO (Mr. Mishra ). Documents of all the TTs to be preserved in lock &key . | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154662 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154662 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154662 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154662 |  | AUD-2026-09-2000017509ACN-2026-09-4000154662 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154663 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Abnormal variations found during rake receipt only due to high losses incurred in MS, HSD. Stock Loss till Audit Date is MS - (-91.24 KL) HSD - (-22.18 KL) Ethanol - (-14.36 KL) Location to maintain Rake Receipt record as per TW Circular issued by HQO For Ethanol, monitoring of Ethanol TT is required while unloading TT. For Undercalibrated TTs action to be taken inline with agreement | 3.9 | Abnormal variations / unused assets reviewed | 1636 | BALASORE DEPOT | location to maintain Rake Receipt record as per TW Circular issued by HQO For Ethanol, monitoring of Ethanol TT is required while unloading TT. For Undercalibrated TTs action to be taken inline with agreement | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154663 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154663 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154663 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154663 |  | AUD-2026-09-2000017509ACN-2026-09-4000154663 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154664 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Randomly checked for 3 days of Sept 26. Found OK for 20th & 22nd Sept. For 15th Sept there was difference of 12 KL in BCU qty vis-à-vis Invoice Qty. Location had kept hard copy of 15th report generated on 18th in which there was no variation however in System it is showing of 12 KL Variation. It seems some software issue, location to take up with TAS Vendor and rectify issue | 3.11 | MFM vs BCU totalizer comparison checked | 1636 | BALASORE DEPOT | It seems some software issue, location to take up with TAS Vendor and rectify issue | SOD | Marketing | ECZ | 2026-10-15 |  | 4 |  | S2 | F2 | 2026-10-15 | AUD-2026-09-2000017509ACN-2026-09-4000154664 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154664 | 2026-09-26 17:30 | 23.0247 | 409 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154664 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154664 |  | AUD-2026-09-2000017509ACN-2026-09-4000154664 | 21 |  | 27 | 80 | 12 | 12 | 59
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154665 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Pending Points : OISD - NIL SSA - NIL MDSA - 2 out of 80 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1636 | BALASORE DEPOT | Advised to close all points | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154665 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154665 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154665 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154665 |  | AUD-2026-09-2000017509ACN-2026-09-4000154665 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154666 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Full round taken and condition of road in tank farm found bad , Recarpeting to be taken up | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1636 | BALASORE DEPOT | Recarpeting of road to be done with 25mm BM & 6mm seal coat BASED on budget available in MEB | SOD | Marketing | ECZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017509ACN-2026-09-4000154666 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154666 | 2026-09-26 17:30 | 23.0247 | 576 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154666 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154666 |  | AUD-2026-09-2000017509ACN-2026-09-4000154666 | 21 |  | 27 | 80 | 12 | 12 | 83
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154667 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | PM schedule checked and found that M&R activities is being done regularly | 4.2 | Maintenance activities reviewed | 1636 | BALASORE DEPOT | officers advised to carry out PM activities religiously | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154667 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154667 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154667 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154667 |  | AUD-2026-09-2000017509ACN-2026-09-4000154667 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154668 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | All NPCB projects reviewed which are mostly taken for OISD complinaces. Only Major project of Bottom loading is in progress | 4.3 | Project progress reviewed | 1636 | BALASORE DEPOT | Location officers advised to complete all projects by 31.12.2026 | SOD | Marketing | ECZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017509ACN-2026-09-4000154668 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154668 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154668 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154668 |  | AUD-2026-09-2000017509ACN-2026-09-4000154668 | 21 |  | 27 | 80 | 12 | 12 | 70
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154669 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Location has done Rs.10.57 lakhs in LASY FY . Scrap of old /absolute items are lysing and scatterted, needs to be arrange and dispose off | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1636 | BALASORE DEPOT | Some more scrap items of 250 KVA DGSET, Old FVD panels , MCC panels , MS scrap , non-ferous scrap to be disposed | SOD | Marketing | ECZ | 2026-11-30 |  | 4 |  | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017509ACN-2026-09-4000154669 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154669 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154669 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154669 |  | AUD-2026-09-2000017509ACN-2026-09-4000154669 | 21 |  | 27 | 80 | 12 | 12 | 65
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154670 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Office entrance is not maitained and not organised . Workers ammenity not maitained . | 6.2 | Officer Area -Housekeeping | 1636 | BALASORE DEPOT | Needs the cleanup of the office reception area , unwanted material to be shifted to Stores . Good quality Painting needs to be doneinside office , Worker ammenity etc | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154670 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154670 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154670 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154670 |  | AUD-2026-09-2000017509ACN-2026-09-4000154670 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154671 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Slow moving products were there in the godown . | 6.3 | Lube Godown area | 1636 | BALASORE DEPOT | Needs to to be takeup with Lube RO for the upliftment and initiate the disposal activity for the expired product . Also orgnise andupkeep and utilise the dgodown area . | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154671 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154671 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154671 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154671 |  | AUD-2026-09-2000017509ACN-2026-09-4000154671 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154672 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Found unorganised and work was progressing | 6.4 | Engg. Store | 1636 | BALASORE DEPOT | Needs proper segreegation of spares and needs the tagging for identification and tracebility of the spares . | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154672 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154672 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154672 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154672 |  | AUD-2026-09-2000017509ACN-2026-09-4000154672 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154673 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Lot of matterial lying around the shed and inside the shed stored needs the segreegation usablle or non usable | 6.5 | Temporary Shed-Stores | 1636 | BALASORE DEPOT | Needs proper segreegation of spares and needs the tagging for identification and tracebility of the spares and initiate disposal iffound non usable in futture | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154673 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154673 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154673 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154673 |  | AUD-2026-09-2000017509ACN-2026-09-4000154673 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154674 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | Fabrication and matterial kept inside the foam shed | 6.6 | Foam Shed | 1636 | BALASORE DEPOT | No activity of Fabrication to be conducted inside the Foam shed and access to be free . Protection to display glass for Foam tank to be provided . New pipes and angles to be kept in the water free area . | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154674 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154674 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154674 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154674 |  | AUD-2026-09-2000017509ACN-2026-09-4000154674 | 21 |  | 27 | 80 | 12 | 12 | 61
|  |  |  | Pending | Q2 BALASORE -SENIOR MANAGEMENT INSPECTIO | 2026-09-26 17:30 | AUD-2026-09-2000017509 | 2026-09-26 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154675 | Open | KHADE RAKESH GANPATRAO | 2026-09-27 | One room adjuscent to MCC room found lot of scarp and lightfitting | 6.7 | MCC Room | 1636 | BALASORE DEPOT | Needs proper segreegation and cleaning the area | SOD | Marketing | ECZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017509ACN-2026-09-4000154675 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017509ACN-2026-09-4000154675 | 2026-09-26 17:30 | 23.0247 | 424 | >20 | AUD-2026-09-2000017509 - ACN-2026-09-4000154675 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017509ACN-2026-09-4000154675 |  | AUD-2026-09-2000017509ACN-2026-09-4000154675 | 21 |  | 27 | 80 | 12 | 12 | 61
MADHAVI LATHA KARMUNGI | 2026-09-27 | JERRY JOSEPH | 2026-09-10 | Tree trimming to be done | LONI TERMINAL VISIT 25.07.2026 | 2026-07-25 | AUD-2026-09-2000017901 | 2026-07-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152221 | Closed | JERRY JOSEPH | 2026-09-10 | Trees obstructing CCTV view | 6.3 |  | 1584 | LONI TERMINAL | Tree trimming is to be done | SOD | Marketing | WZ | 2026-08-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | ASSET INTEGRITY | S1 | F3 | 2026-08-30 | AUD-2026-09-2000017901ACN-2026-09-4000152221 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017901ACN-2026-09-4000152221 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-09-2000017901 - ACN-2026-09-4000152221 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017901ACN-2026-09-4000152221 | AUD-2026-09-2000017901ACN-2026-09-4000152221 | 21 | 21 | 27 | 80 | 18 | 18 | 52 | 56
MADHAVI LATHA KARMUNGI | 2026-09-27 | JERRY JOSEPH | 2026-09-10 | Concertina coil is replaced | LONI TERMINAL VISIT 25.07.2026 | 2026-07-25 | AUD-2026-09-2000017901 | 2026-07-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152222 | Closed | JERRY JOSEPH | 2026-09-10 | Concertina coil near Pipeline Office is damaged conditiuon | 6.4 |  | 1584 | LONI TERMINAL | Corrective action to be taken | SOD | Marketing | WZ | 2026-08-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | ASSET INTEGRITY | S2 | F3 | 2026-08-30 | AUD-2026-09-2000017901ACN-2026-09-4000152222 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017901ACN-2026-09-4000152222 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-09-2000017901 - ACN-2026-09-4000152222 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017901ACN-2026-09-4000152222 | AUD-2026-09-2000017901ACN-2026-09-4000152222 | 21 | 21 | 27 | 80 | 18 | 18 | 52 | 56
MADHAVI LATHA KARMUNGI | 2026-09-27 | JERRY JOSEPH | 2026-09-10 | The piled up mud and grass below the Pipeline has been cleared | LONI TERMINAL VISIT 25.07.2026 | 2026-07-25 | AUD-2026-09-2000017901 | 2026-07-25 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152223 | Closed | JERRY JOSEPH | 2026-09-10 | Hydrant pipeline bottom is not having adequate gap near Tank farm entry gate | 6.5 |  | 1584 | LONI TERMINAL | Corrective action to be taken | SOD | Marketing | WZ | 2026-08-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | ASSET INTEGRITY | S1 | F3 | 2026-08-30 | AUD-2026-09-2000017901ACN-2026-09-4000152223 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017901ACN-2026-09-4000152223 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-09-2000017901 - ACN-2026-09-4000152223 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017901ACN-2026-09-4000152223 | AUD-2026-09-2000017901ACN-2026-09-4000152223 | 21 | 21 | 27 | 80 | 18 | 18 | 52 | 56
MADHAVI LATHA KARMUNGI | 2026-09-27 | GOPE SIDDHARTH | 2026-08-09 | Scrap kept near the Tank Wagon Gantry is segrregate. Few are reutilised & others RFD is being processed. | LONI LOCATION VISIT 18.05.2026 | 2026-05-18 | AUD-2026-07-2000016452 | 2026-05-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146534 | Closed | GOPE SIDDHARTH | 2026-08-09 | Scrap is observed near Tank Wagon gantry area. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1584 | LONI TERMINAL | Scrap kept near the Tank Wagon Gantry is to be disposed. | SOD | Marketing | WZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-06-30 | AUD-2026-07-2000016452ACN-2026-07-4000146534 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016452ACN-2026-07-4000146534 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-07-2000016452 - ACN-2026-07-4000146534 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016452ACN-2026-07-4000146534 | AUD-2026-07-2000016452ACN-2026-07-4000146534 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 56
MADHAVI LATHA KARMUNGI | 2026-09-27 | JERRY JOSEPH | 2026-09-10 | Discussed with OEM and OEM has recommended to control flow using valve. | LONI LOCATION VISIT 18.05.2026 | 2026-05-18 | AUD-2026-07-2000016452 | 2026-05-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146536 | Closed | JERRY JOSEPH | 2026-09-10 | Fire Engine running parameters were checked and Cooling Water Pressure in FE line is found to be higher ( 8 bar ) than acceptable limits ( 2-3 bar ) | 6.2 |  | 1584 | LONI TERMINAL | Orifice Plates to be installed in Fire Engine 1,2,3,4 as the same is found to be not installed and leading to high pressure in the cooling water line. | SOD | Marketing | WZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | ASSET INTEGRITY | S3 | F1 | 2026-06-30 | AUD-2026-07-2000016452ACN-2026-07-4000146536 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016452ACN-2026-07-4000146536 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-07-2000016452 - ACN-2026-07-4000146536 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016452ACN-2026-07-4000146536 | AUD-2026-07-2000016452ACN-2026-07-4000146536 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 56
MADHAVI LATHA KARMUNGI | 2026-09-27 | JERRY JOSEPH | 2026-09-10 | Bypass Vlave is replaced. leaks arrested. | LONI LOCATION VISIT 18.05.2026 | 2026-05-18 | AUD-2026-07-2000016452 | 2026-05-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146537 | Closed | JERRY JOSEPH | 2026-09-10 | Jockey Pumps are found to start 4-5 times for every hour during day time. | 6.3 |  | 1584 | LONI TERMINAL | The leaks in Fire Water line if any to be arrested | SOD | Marketing | WZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | ASSET INTEGRITY | S2 | F3 | 2026-06-30 | AUD-2026-07-2000016452ACN-2026-07-4000146537 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016452ACN-2026-07-4000146537 | 2026-10-15 | 4.7538 | 391 | >20 | AUD-2026-07-2000016452 - ACN-2026-07-4000146537 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000016452ACN-2026-07-4000146537 | AUD-2026-07-2000016452ACN-2026-07-4000146537 | 21 | 21 | 27 | 80 | 18 | 18 | 44 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | Corrective action has been taken as advised during the audit. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143853 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | A Double Contingency Fire Mock Drill was successfully conducted on 02/07/2026 at 1433 hours, simulating a scenario of product leakage and flange leak fire from ROSOV of TK09 along with leakage from mechanical seal of a HSD pump. The execution of the drill was effective. The sprinklers of adjacent HSD tank were operated effectively. Two Foam Monitors were operated during the drill and there performance was effective. Overall, coordination among team members was effective. Use of mega-pone was not done during the drill which could have made the communication more effective. Other observations for improvement are recorded iin the fire drill report. | 2.02 | Double contingency scenario simulated; observations recorded | 1341 | HISAR TERMINAL | Corrective actions as dicussed at filed to be taken. | SOD | Marketing | NZ | 2026-07-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143853 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143853 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143853 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143853 | AUD-2026-07-2000015093ACN-2026-07-4000143853 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | We are conducting ERDMP again and ratification as advised during the audit will be done by Oct 2026. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143855 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | Yes, the ERDMP was reviewed. The document available was certified during Feb'22 and is due for re-submission/ re-certification in Feb'27. Two scenarios not pertaining to the location viz.. Storage tank TSV Pop-up and Rim Seal Fire in the Floating Roof Tank, were found to be considered under Level-2 Emergency | 2.0499999999999998 | Emergency response preparedness reviewed | 1341 | HISAR TERMINAL | Location to thoroughly review the document to eliminate any discrepancies as pointed out in the observation before submiting it forre-certification. | SOD | Marketing | NZ | 2026-07-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143855 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143855 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143855 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143855 | AUD-2026-07-2000015093ACN-2026-07-4000143855 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | All Sprinklers of TK4 has been cleaned in July 2026. Painting has been done where rusting observed on the line. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143856 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-22 | Sprinklers of tank TK04 was checked during the visit and following observations were made in the presence of the safety officer of the location. 1. Some sprinkler nozzles of the top two tiers of the tank were found choked. 2. Sprinkler on the top of the conicalroof of the tank was found partially choked. 3. Rusting of sprinkler lines observed. Location is carrying out cleaning of sprinkler nozzles once is every six months and the last testing and cleaning was done on dates (17 - 19 Jan'26). | 2.06 | Emergency response preparedness reviewed | 1341 | HISAR TERMINAL | 1 & 2. Location to ensure proper functioning of all the sprinkler nozzles. 3. Re-painting of the sprinkler lines to be planned andcarried out. | SOD | Marketing | NZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-07-2000015093ACN-2026-07-4000143856 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143856 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143856 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143856 | AUD-2026-07-2000015093ACN-2026-07-4000143856 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | Unloading hose has been kept in the TT. Protective screen installed on exhaust pipe. Drain pipe lenght has been increased. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143862 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | Part B Check was done on HR57A0888 on 01/07/2026. Following Observations were recorded: a) Unloading hose not available b) Protective Screen is not available on exhaust pipe c) Drain pipe from top to be extended below TT body. | 3.01 | TT fittings & discipline checked | 1341 | HISAR TERMINAL | NC points to be complied. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143862 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143862 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143862 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143862 | AUD-2026-07-2000015093ACN-2026-07-4000143862 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | 1. Unloading hose has been kept in the TT. 2) Emergency kit is not required as per OISD 244 and 167. 3) DCP fire extinguisher has been kept for easy access for driver. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143861 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | Random check of TT crew on roadside emergency procedures were conducted. Inspection of TT# HR57A0888 was conducted during the visit. The TT was neither carrying product hose nor emergency safety kit. The DCP fire extinguisher was found neatly secured using nut and bolt behind the cabin of the TT. It took few minutes for the TT crew to retrieve it for operation from its secured position. The fire extinguisher was operated and was found to be satisfactory. | 2.2200000000000002 | TT crew roadside emergency procedures checked | 1341 | HISAR TERMINAL | Location to ensure: 1. Availability of product unloading hose pipe with each TT. 2. Availability of emergency kit with each TT as well as training to each TT crew about its usage. 3. DCP Fire extinguisher to be kept for easy accessibility and retrieval in case of any emergency. | SOD | Marketing | NZ | 2026-07-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143861 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143861 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143861 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143861 | AUD-2026-07-2000015093ACN-2026-07-4000143861 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
DURGA NARAIN MEENA | 2026-09-28 | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | Gasket has been replaced to arrest the leakge from venturi. | HISAR TML SR MGMT AUDIT Q1 26 | 2026-07-02 16:00 | AUD-2026-07-2000015093 | 2026-06-30 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143860 | Closed | ASHISH KUMAR GUTHALIYAN | 2026-09-28 | MEFG - There are 06 Nos of MEFG installed at the Location. MEFG located inside the Dyke wall of TK-06 was operated during the visit. While performance of the equipment was satisfactory, small leakage was observed from the gasket of its venturi. The officer was found to be acquainted with the operation of the MEFG. | 2.19 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1341 | HISAR TERMINAL | Leakage to be arrested and all such equipment to be inspected for any such leakage for arresting the same, if observed. | SOD | Marketing | NZ | 2026-07-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-30 | AUD-2026-07-2000015093ACN-2026-07-4000143860 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015093ACN-2026-07-4000143860 | 2026-09-30 17:00 | 19.0455 | 392 | >20 | AUD-2026-07-2000015093 - ACN-2026-07-4000143860 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015093ACN-2026-07-4000143860 | AUD-2026-07-2000015093ACN-2026-07-4000143860 | 21 | 21 | 27 | 80 | 0 | 0 | 48 | 56
[5 empty] | VASHI BOT VISIT DATED 15.09.2026 | 2026-09-15 | AUD-2026-09-2000017370 | 2026-09-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153358 | Open |  |  | Yes, to dispose off sludge in TK 01 . | 1.3 | Pending issues reviewed | 3562 | VASHI BO TML | Approval for Bioremediation of TK01 sludge. | SOD | Marketing | WZ | 2026-10-31 |  | 2 |  | S2 | F1 | 2026-10-31 | AUD-2026-09-2000017370ACN-2026-09-4000153358 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017370ACN-2026-09-4000153358 | 2026-09-15 | 34.7538 | 425 | >20 | AUD-2026-09-2000017370 - ACN-2026-09-4000153358 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017370ACN-2026-09-4000153358 |  | AUD-2026-09-2000017370ACN-2026-09-4000153358 | 21 |  | 27 | 80 | 9 | 9 | 61
[5 empty] | VASHI BOT VISIT DATED 15.09.2026 | 2026-09-15 | AUD-2026-09-2000017370 | 2026-09-15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153359 | Open |  |  | Found OK,Fire siren diagram need to be displayed | 6.9 | Fire Engine Shed | 3562 | VASHI BO TML | To display fire siren diagram | SOD | Marketing | WZ | 2026-10-31 |  | 6 |  | S3 | F2 | 2026-10-31 | AUD-2026-09-2000017370ACN-2026-09-4000153359 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017370ACN-2026-09-4000153359 | 2026-09-15 | 34.7538 | 425 | >20 | AUD-2026-09-2000017370 - ACN-2026-09-4000153359 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017370ACN-2026-09-4000153359 |  | AUD-2026-09-2000017370ACN-2026-09-4000153359 | 21 |  | 27 | 80 | 9 | 9 | 61
[5 empty] | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153364 | Open |  |  | yes | 2.7 | VA alerts checked / analysed | 1588 | VASHI WHITE OIL TERMINAL | followup to be done with vendor | SOD | Marketing | WZ | 2026-10-31 | [5 empty] | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153364 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153364 | 2026-10-14 | 5.7538 | 425 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153364 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 |  | AUD-2026-09-2000017371ACN-2026-09-4000153364 |  | AUD-2026-09-2000017371ACN-2026-09-4000153364 | 21 |  | 27 | 80 | 15 | 11 | 61
[5 empty] | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153365 | Open |  |  | yes | 2.8 | Access control systems checked | 1588 | VASHI WHITE OIL TERMINAL | ACESS control being correted from visitor to via vendor arequest | SOD | Marketing | WZ | 2026-10-31 | [5 empty] | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153365 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153365 | 2026-10-14 | 5.7538 | 425 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153365 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 |  | AUD-2026-09-2000017371ACN-2026-09-4000153365 |  | AUD-2026-09-2000017371ACN-2026-09-4000153365 | 21 |  | 27 | 80 | 15 | 11 | 61
[5 empty] | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153369 | Open |  |  | yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1588 | VASHI WHITE OIL TERMINAL | Barricading to be done near Tanks under maintainence | SOD | Marketing | WZ | 2026-09-30 | [5 empty] | 2026-09-30 | AUD-2026-09-2000017371ACN-2026-09-4000153369 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153369 | 2026-10-14 | 5.7538 | 394 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153369 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 |  | AUD-2026-09-2000017371ACN-2026-09-4000153369 |  | AUD-2026-09-2000017371ACN-2026-09-4000153369 | 21 |  | 27 | 80 | 15 | 11 | 57
|  |  |  | Auction is in progress, shall be completed by 31.12.26 | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153370 | Open | RANA PULKIT | 2026-10-15 | Location is under process to scrap misc. items | 3.9 | Abnormal variations / unused assets reviewed | 1509 | SHOLAPUR TERMINAL | scrap disposal to be completed by 30.11.2026 | SOD | Marketing | WZ | 2026-11-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017372ACN-2026-09-4000153370 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153370 | 2026-09-19 | 30.7538 | 455 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153370 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153370 |  | AUD-2026-09-2000017372ACN-2026-09-4000153370 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154977 | Open |  |  | VA system is checked and found inactive. | 2.7 | VA alerts checked / analysed | 1485 | AKOLA DEPOT | It is advised to have follow up with vendor and to make VA system active. | SOD | Marketing | WZ | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-09-2000017374ACN-2026-09-4000154977 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154977 | 2026-08-24 | 56.7538 | 394 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154977 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017374ACN-2026-09-4000154977 |  | AUD-2026-09-2000017374ACN-2026-09-4000154977 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154979 | Open |  |  | OISD 2022-23 Total points-20 Complied-20 MDSA 2025-26 Total points-33 Complied-21 SSA 2025-26 Total points-32 Complied-28 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1485 | AKOLA DEPOT | Location to comply the points in time bound manner | SOD | Marketing | WZ | 2026-10-30 |  | 9 |  | S3 | F3 | 2026-10-30 | AUD-2026-09-2000017374ACN-2026-09-4000154979 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154979 | 2026-08-24 | 56.7538 | 424 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154979 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017374ACN-2026-09-4000154979 |  | AUD-2026-09-2000017374ACN-2026-09-4000154979 | 21 |  | 27 | 80 | 3 | 3 | 61
[5 empty] | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154981 | Open |  |  | There is no fixed approach for solar panel at Fire Engine Shed. As per location, movable ladder is being used for solar panel cleaning. It is advised to provide fixed approach to solar panel for cleaning for safe operation. | 6.2 | Access/Approach for Solar Panel | 1485 | AKOLA DEPOT | Location to provide fixed approach to Solar panel at Fire Engine Shed. | SOD | Marketing | WZ | 2026-10-30 |  | 9 |  | S3 | F3 | 2026-10-30 | AUD-2026-09-2000017374ACN-2026-09-4000154981 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154981 | 2026-08-24 | 56.7538 | 424 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154981 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017374ACN-2026-09-4000154981 |  | AUD-2026-09-2000017374ACN-2026-09-4000154981 | 21 |  | 27 | 80 | 3 | 3 | 61
[5 empty] | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154982 | Open |  |  | Color of Air line was found not as per norms | 6.3 | Air line | 1485 | AKOLA DEPOT | To do the coloring as per applicable norms | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017374ACN-2026-09-4000154982 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154982 | 2026-08-24 | 56.7538 | 394 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154982 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017374ACN-2026-09-4000154982 |  | AUD-2026-09-2000017374ACN-2026-09-4000154982 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | FOUZDAR RISHABH | 2026-09-28 | VA alerts are timely closed and all atempts are being made to improve the score. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150985 | Completed | FOUZDAR RISHABH | 2026-09-28 | VA alerts checked | 2.7 | VA alerts checked / analysed | 1155 | ROORKEE DEPOT | VA alerts to be checked and score to be improved | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150985 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150985 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150985 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016863ACN-2026-09-4000150985 |  | AUD-2026-09-2000016863ACN-2026-09-4000150985 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154983 | Open |  |  | Conduted | 1.2 | Performance review conducted | 1554 | MR-II TERMINAL | Painting needs to be started as soon as rains are over, rusting has beginning to apper on structure.5 years period is also overdue | SOD | Marketing | WZ | 2026-10-30 |  | 4 |  | S2 | F2 | 2026-10-30 | AUD-2026-09-2000017375ACN-2026-09-4000154983 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154983 | 2026-10-16 | 3.7538 | 424 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154983 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017375ACN-2026-09-4000154983 |  | AUD-2026-09-2000017375ACN-2026-09-4000154983 | 21 |  | 27 | 80 | 6 | 5 | 61
[5 empty] | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154984 | Open |  |  | Painting of tanks and infrastracture is to be scheduled as facility is 5 years old and visible ruting is seen. | 1.8 | Improvement plans discussed | 1554 | MR-II TERMINAL | Location to have PO in hand to start painting immediately after rains | SOD | Marketing | WZ | 2027-03-31 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-09-2000017375ACN-2026-09-4000154984 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154984 | 2026-10-16 | 3.7538 | 576 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154984 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017375ACN-2026-09-4000154984 |  | AUD-2026-09-2000017375ACN-2026-09-4000154984 | 21 |  | 27 | 80 | 6 | 5 | 83
[5 empty] | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154991 | Open |  |  | YES. VRU MOC still pending approval | 3.17 | MOC status reviewed | 1554 | MR-II TERMINAL | Location to submit to Zone along with VRU operations SOP | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154991 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154991 | 2026-10-16 | 3.7538 | 394 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154991 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017375ACN-2026-09-4000154991 |  | AUD-2026-09-2000017375ACN-2026-09-4000154991 | 21 |  | 27 | 80 | 6 | 5 | 57
[5 empty] | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-09-4000154993 | Open |  |  | Dyke drain hooters not coming to contol room. | 5.2 | Functioning of all Hooters in control room | 1554 | MR-II TERMINAL | Location to rectify | SOD | Marketing | WZ | 2026-12-30 |  | 4 |  | S2 | F2 | 2026-12-30 | AUD-2026-09-2000017375ACN-2026-09-4000154993 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154993 | 2026-10-16 | 3.7538 | 485 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154993 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017375ACN-2026-09-4000154993 |  | AUD-2026-09-2000017375ACN-2026-09-4000154993 | 21 |  | 27 | 80 | 6 | 5 | 70
|  | JANA SUDEEP | 2026-09-28 | As per DG-Solar Synchronization vendor, the synchronization will work when the load on DG exceeds 30% of the total capacity of the DG. Else there is a chance of reverse flow of Solar Power to the DG. Hence, the limit is set at 30% by the vendor. Mail communication with the DG-Solar synchronzation vendor attached. | SR MANAGEMENT INSPECTION Q1FY2627 | 2026-06-19 19:00 | AUD-2026-08-2000016227 | 2026-06-19 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147387 | Completed | JANA SUDEEP | 2026-09-28 | The location currently has a DG–Solar Synchronization Panel that operates at a minimum DG loading of 30%. The location shall explore the feasibility of upgrading to a new DG–Solar Synchronization Panel capable of operating at a minimum DG loading of 5% and which not allow back load on DG from solar panel, with the objective of improving operational efficiency and maximizing solar power utilization | 6.2 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-08-2000016227ACN-2026-08-4000147387 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016227ACN-2026-08-4000147387 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-08-2000016227 - ACN-2026-08-4000147387 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016227ACN-2026-08-4000147387 |  | AUD-2026-08-2000016227ACN-2026-08-4000147387 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154995 | Open |  |  | Checked lux levels in all areas of operation. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1775 | BENGALURU TERMINAL | Few areas need improvement in lux levels. Loction to review as per OISD-STD-244 and comply with the same. | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017758ACN-2026-09-4000154995 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000154995 | 2026-09-24 17:00 | 25.0455 | 486 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000154995 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000154995 |  | AUD-2026-09-2000017758ACN-2026-09-4000154995 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154996 | Open |  |  | Efficient monitoring is done by location. Access control is under revamping. | 2.8 | Access control systems checked | 1775 | BENGALURU TERMINAL | Delicensed/licensed demarkation around MCC & TT calibration shed to be completed at the earliest. | SOD | Marketing | SWZ | 2026-10-31 |  | 3 |  | S3 | F1 | 2026-10-31 | AUD-2026-09-2000017758ACN-2026-09-4000154996 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000154996 | 2026-09-24 17:00 | 25.0455 | 425 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000154996 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000154996 |  | AUD-2026-09-2000017758ACN-2026-09-4000154996 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154997 | Open |  |  | OISD audit 42/42 are complied, 31/31 of SSA are complied ,MDSA 2025-26: 26/32 points are complied target-30.09.2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1775 | BENGALURU TERMINAL | Pending audit points to be complied at the earliest. | SOD | Marketing | SWZ | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017758ACN-2026-09-4000154997 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000154997 | 2026-09-24 17:00 | 25.0455 | 486 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000154997 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000154997 |  | AUD-2026-09-2000017758ACN-2026-09-4000154997 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-09-4000154998 | Open |  |  | Store room near OWS was not maintained. | 4 |  | 1775 | BENGALURU TERMINAL | Store room to be cleaned and put to use. | SOD | Marketing | SWZ | 2026-10-05 |  | 1 |  | S1 | F1 | 2026-10-05 | AUD-2026-09-2000017758ACN-2026-09-4000154998 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000154998 | 2026-09-24 17:00 | 25.0455 | 399 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000154998 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000154998 |  | AUD-2026-09-2000017758ACN-2026-09-4000154998 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154999 | Open |  |  | Cables were not organized near tank 30 in the cable trays. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1775 | BENGALURU TERMINAL | Cables near Tk 30 to be organised and kept in the cable tray with appropriatecovers. | SOD | Marketing | SWZ | 2026-10-14 |  | 1 |  | S1 | F1 | 2026-10-14 | AUD-2026-09-2000017758ACN-2026-09-4000154999 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000154999 | 2026-09-24 17:00 | 25.0455 | 408 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000154999 | 532 | 8294 | 21 | 8294 | 5 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000154999 |  | AUD-2026-09-2000017758ACN-2026-09-4000154999 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155000 | Open |  |  | All actvities are being done with permits and officers are wearing overalls. | 4.2 | Maintenance activities reviewed | 1775 | BENGALURU TERMINAL | Ethanol nitrile hoses were hydrotested however, date to be updated on hoses. | SOD | Marketing | SWZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017758ACN-2026-09-4000155000 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155000 | 2026-09-24 17:00 | 25.0455 | 394 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155000 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155000 |  | AUD-2026-09-2000017758ACN-2026-09-4000155000 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155001 | Open |  |  | In view of CNT outage by 1st weeK of October 2026, facility to be prepared for ATF TT loading. | 4.3 | Project progress reviewed | 1775 | BENGALURU TERMINAL | 1. Proposal to be put up for construction of additional MS tank in Dyke 4. 2. ATF TT loading facility to be commissioned before 30.09.2026 | SOD | Marketing | SWZ | 2026-10-05 |  | 1 |  | S1 | F1 | 2026-10-05 | AUD-2026-09-2000017758ACN-2026-09-4000155001 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155001 | 2026-09-24 17:00 | 25.0455 | 399 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155001 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155001 |  | AUD-2026-09-2000017758ACN-2026-09-4000155001 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155002 | Open |  |  | PM Jobs are being done within timelines. | 4.4 | Quality of PM compliance reviewed | 1775 | BENGALURU TERMINAL | MRPL MS hookup line to be commissioned with PLT. | SOD | Marketing | SWZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017758ACN-2026-09-4000155002 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155002 | 2026-09-24 17:00 | 25.0455 | 425 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155002 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155002 |  | AUD-2026-09-2000017758ACN-2026-09-4000155002 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155003 | Open |  |  | Close monitoring and compliance is required. | 4.5 | Making Location Scrap Free | 1775 | BENGALURU TERMINAL | 1. Co. TT no. KA01AL2468 to be disposed at the earliest. 2. Dyke with 300 mm kerb wall to be prepared for sludge tanks and the tanks to b mounted on pedestal. | SOD | Marketing | SWZ | 2026-12-31 |  | 2 |  | S1 | F2 | 2026-12-31 | AUD-2026-09-2000017758ACN-2026-09-4000155003 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155003 | 2026-09-24 17:00 | 25.0455 | 486 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155003 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155003 |  | AUD-2026-09-2000017758ACN-2026-09-4000155003 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155004 | Open |  |  | Lot of dust was observed on th estructures and cotton waste was found on gantry structures. | 4.5 | Gantry cleanliness to be maintained | 1775 | BENGALURU TERMINAL | Deep cleaning and housekeeping of TT gantry and other facilities to be done. | SOD | Marketing | SWZ | 2026-10-05 |  | 1 |  | S1 | F1 | 2026-10-05 | AUD-2026-09-2000017758ACN-2026-09-4000155004 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155004 | 2026-09-24 17:00 | 25.0455 | 399 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155004 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155004 |  | AUD-2026-09-2000017758ACN-2026-09-4000155004 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | Q2 LOCATION VISIT OF BENGALURU TERMINAL | 2026-09-24 17:00 | AUD-2026-09-2000017758 | 2026-09-23 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155005 | Open |  |  |  | 6.1 |  | 1775 | BENGALURU TERMINAL | Electrical buggy to be made operational. | SOD | Marketing | SWZ | 2026-10-31 |  | 2 |  | S1 | F2 | 2026-10-31 | AUD-2026-09-2000017758ACN-2026-09-4000155005 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017758ACN-2026-09-4000155005 | 2026-09-24 17:00 | 25.0455 | 425 | >20 | AUD-2026-09-2000017758 - ACN-2026-09-4000155005 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017758ACN-2026-09-4000155005 |  | AUD-2026-09-2000017758ACN-2026-09-4000155005 | 21 |  | 27 | 80 | 0 | 0 | 61
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-08-10 | After the Transfer of our Officer Yogesh Bharti shri Sunil Digra is handling all the court cases. | LOCATION VISIT-JAMMU_20-23.05.26 | 2026-05-23 | AUD-2026-07-2000015563 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142606 | Closed | DIGRA SUNIL KUMAR | 2026-08-10 | 1) New Transport Tender and Court Cases | 1.3 | Pending issues reviewed | 1256 | JAMMU DEPOT | XX | SOD | Marketing | NFZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015563ACN-2026-07-4000142606 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015563ACN-2026-07-4000142606 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-07-2000015563 - ACN-2026-07-4000142606 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015563ACN-2026-07-4000142606 | AUD-2026-07-2000015563ACN-2026-07-4000142606 | 21 | 21 | 27 | 80 | 1 | -4 | 44 | 57
|  | DIGRA SUNIL KUMAR | 2026-09-29 | Close monitoring of court cases is being done in coordination with Legal & Zonal Transportation. Before the court hearing LocationOfficers are also going to the Advocate for further detailing of the whole case as per current scenario | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152011 | Completed | DIGRA SUNIL KUMAR | 2026-10-15 | New Transport Tender Court Cases reviewed | 1.3 | Pending issues reviewed | 1256 | JAMMU DEPOT | Close monitoring of cases to be done in coordination with Legal & Zonal Transportation. | SOD | Marketing | NFZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-09-2000017601ACN-2026-09-4000152011 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152011 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152011 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017601ACN-2026-09-4000152011 |  | AUD-2026-09-2000017601ACN-2026-09-4000152011 | 21 |  | 27 | 80 | 1 | -4 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Housekeeping carried on for drain and other areas. Daily rounds are being made. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 QUARTERLY INSPECTION | ACN-2026-08-4000146719 | Closed | JHA RAJAN KUMAR | 2026-09-29 | 1.Dried mud, vegetation growth found in Front drain of TT gantry 2. Storm water drain opposite HSD tank dyke, towards Rly siding found almost covered by vegetation from side 3. Drain beside lube godown, towards STP, found filled with mud 4. Water and dirt accumulation found under strainer of MS pump 1 5. Spilled/ leaky oil found on floor in area where leaky lubes are collected 6. Valves, etc, meant for use, kept in yard beside lube godown, found with vegetation growth, covering these items completely 7. Vegetation found over cable tray infront of HSD Tank on way towards siding. | 6.3 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC, HSE officer and M&I officer to take round of the location, by taking atleast one round daily to detect such conditions and take corrective action | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146719 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146719 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146719 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146719 | AUD-2026-08-2000016222ACN-2026-08-4000146719 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Housekeeping carried on for drain and other areas. Daily rounds are being made. CCTV is also being checked and its record being made. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7QUARTERLY INSPECTION | ACN-2026-08-4000146723 | Closed | JHA RAJAN KUMAR | 2026-09-29 | 1. A shed, on one corner outside dyke of Tk6 found completely covered by vegetation. A JB, nearby, was also found almost covered byvegetation 2.Vegetation fround growing on solar panels 3. At multiple places, creepers found on concertina coils. One CCTV camerapole also found to be covered by creepers for almost entire height 4. Lubricating oil cup of HSD pump 2 of TWPH found empty. 5. Creepers found started covering STP concreet tank top gratings 6. Roof drain outlet of Tk6 found with single gate valve, having end flange removed. 7. Silica gel of Ethanol UG tanks Tk9 and Tk8 found have lost life. 8. Leakage and signs of leakages found from pumps xxx,xxx of TW pump house 9.An ethanol line opposite fabrication yard, found partially covered by green vegetation | 6.7 | Quarterly Inspection | 1723 | PATNA DEPOT | LIC and Safety officer to regularly monitor different areas by CCTV and atleast one physical round of the location daily to note such deviations and take corrective action | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146723 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146723 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146723 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146723 | AUD-2026-08-2000016222ACN-2026-08-4000146723 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Action taken. Nozzles cleaned. Foam pourer tested and working after line clearance. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10QUARTERLY INSPECTION | ACN-2026-08-4000146726 | Closed | JHA RAJAN KUMAR | 2026-09-29 | 1. Sprinkler nozzles 20, 26, 51 of Tk6 found choked. Sprinkler nozzles installed on sprinkler line portions, which have tobe taken away from tank shell to accommodate stairs and have cable trays infront of them are spraying water to hit tank body effectively 2. No foam generator of Tk2 generated adequate foam. One of the foam generators developed leak from gasket of joint also | 6.10 | Quarterly Inspection | 1723 | PATNA DEPOT | 1. Choked nozzles to be cleaned. Srpinkler nozzles which have gone further from tank surface, to to brought nearer the shell by extension pipe 2. Foam generators to be checked and made functional properly. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146726 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146726 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146726 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146726 | AUD-2026-08-2000016222ACN-2026-08-4000146726 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Noted for action. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15QUARTERLY INSPECTION | ACN-2026-08-4000146731 | Closed | JHA RAJAN KUMAR | 2026-09-29 | Around 20 contract workmen of all work areas, were interacted with. Their wellbeing w.r.t wages, amenities were enquired. Expectations of the Organization was explained to them. Areawise observations, during the visit were also shared with them and what they can do to improve upon the observations made, were also told to them. | 6.15 | Quarterly Inspection | 1723 | PATNA DEPOT | Officers to guide and monitor works of contractors so that all works are carried out in the field properly | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146731 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146731 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146731 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146731 | AUD-2026-08-2000016222ACN-2026-08-4000146731 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Noted for action. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17QUARTERLY INSPECTION | ACN-2026-08-4000146733 | Closed | JHA RAJAN KUMAR | 2026-09-29 | KPI parameters were discussed. High TT entry time, which was impacting TT cycle time was discussed with example of unmonitoed TT entry, as was witnessed during the visit, was explained to officers and ways and means to control the same by involvement and coordination of planning officer was also discussed. | 6.17 | Quarterly Inspection | 1723 | PATNA DEPOT | Officers to monitor their respective areas of works in line with discussion and KPI. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146733 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146733 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146733 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146733 | AUD-2026-08-2000016222ACN-2026-08-4000146733 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-08-31 | Entries have been updated. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18QUARTERLY INSPECTION | ACN-2026-08-4000146734 | Closed | JHA RAJAN KUMAR | 2026-08-31 | Random work permit 1. 180000114366 , 2. 180000117473, 3.180000113854 and 4. 180000117493 were checked and found with incomplete entries for Tool Box talk, JSA with missing entries and signature | 6.18 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to have proper signature on work permit closure, Entry of permit reneual , Tool Box Talk sheet to be filled and acknowledged by HPCL officer, JSA to be signed by contractor | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146734 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146734 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146734 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146734 | AUD-2026-08-2000016222ACN-2026-08-4000146734 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Being checked by 2 officers and security guard. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19QUARTERLY INSPECTION | ACN-2026-08-4000146735 | Closed | JHA RAJAN KUMAR | 2026-09-29 | CCTV for empty ethanol tanker checking was done for 20/7/26, 31/7/26, 16/7/26. Only 20th July had 2 officers checking empty ethanolTT. | 6.19 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to ensure all empty ethanol TTs are duly checked by 2 officers before it leaves the Depot premises. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146735 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146735 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146735 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146735 | AUD-2026-08-2000016222ACN-2026-08-4000146735 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Being checked by security guard. Training provided to them. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20QUARTERLY INSPECTION | ACN-2026-08-4000146736 | Closed | JHA RAJAN KUMAR | 2026-09-29 | CCTV checked for 30/7/26 2 tanker with Registraion no. 4609 and 8955 was viewed. Security did not check the cabin from inside. | 6.20 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to advice the security at IN gate to mandatorily check cabin of all TT coming in for loading. | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146736 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146736 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146736 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146736 | AUD-2026-08-2000016222ACN-2026-08-4000146736 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
MONISH KUMAR | 2026-09-29 | JHA RAJAN KUMAR | 2026-09-29 | Monitoring being done for patroling. | PATNA Q2 AUDIT 2026 | 2026-08-03 | AUD-2026-08-2000016222 | 2026-08-03 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22QUARTERLY INSPECTION | ACN-2026-08-4000146738 | Closed | JHA RAJAN KUMAR | 2026-09-29 | CCTV reviewed for 1. 1/7/26 No patrol between 1:00 AM to 4: AM was observed. 2. 2/7/26 No patrol between 11:00 PM to 4:00 AM wasobserved. | 6.22 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to sensitize the guards on Night patrol and ensure itsa done at regular intervals as set by LIC | SOD | Marketing | PZR | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000016222ACN-2026-08-4000146738 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016222ACN-2026-08-4000146738 | 2026-08-03 | 77.7538 | 393 | >20 | AUD-2026-08-2000016222 - ACN-2026-08-4000146738 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016222ACN-2026-08-4000146738 | AUD-2026-08-2000016222ACN-2026-08-4000146738 | 21 | 21 | 27 | 80 | 0 | 0 | 55 | 57
|  | DIGRA SUNIL KUMAR | 2026-09-29 | Painting of pavements, fire engine shed, earthpits, civil repair job at various area around the TT gantry cinil Island repair, repair of pump house stair case, covering the earthing strip across the road near the old pump house and the drain by PCC etc along with grass vutting and area cleaning around the drain area planned and carried out. New Earthpit board stickers along with out side gate vinayl sticker of Jammu IRD has been placed in order. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152019 | Completed | DIGRA SUNIL KUMAR | 2026-09-29 | Housekeeping to be improved. | 6.4 | MCC Room | 1256 | JAMMU DEPOT | Location to take immediate corrective action. | SOD | Marketing | NFZ | 2026-09-10 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-10 | AUD-2026-09-2000017601ACN-2026-09-4000152019 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152019 | 2026-09-04 | 45.7538 | 374 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152019 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017601ACN-2026-09-4000152019 |  | AUD-2026-09-2000017601ACN-2026-09-4000152019 | 21 |  | 27 | 80 | 1 | -4 | 54
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000155016 | Open |  |  | Location to close AR SOD-242294 NWR_VDTL_GETCO HT LINE WORK | 1.3 | Pending issues reviewed | 1410 | VADODARA TERMINAL | Location shall arrange to close AR NWR_VDTL_GETCO HT LINE WORK | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155016 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155016 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155016 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155016 |  | AUD-2026-09-2000017759ACN-2026-09-4000155016 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155020 | Open |  |  | 1. DFMD is functional and however multizone could not be verified. DFMD is not operational at license area gate. 2. Baggage check for all contract workmen, electrician etc shall be ensure 3. Fire engines are working as per priority. One fire engine is under repair. | 2.5 | Emergency response preparedness reviewed | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155020 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155020 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155020 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155020 |  | AUD-2026-09-2000017759ACN-2026-09-4000155020 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155021 | Open |  |  | (a) Total 91 CCTVs are installed. (i) Total 8 out of 91 CCTV cameras were non functional. (ii) The OWS perimeter did not have adequate intrusion prevention/access control. The missing blind spot to be covered in the CCTV /VA survellance (iii) Sample room (Entry/Exit) is not covered under CCTV. (iii) The monitoring records have been prepared on loose sheets, without serial numbers. The records are signed by HSSE officer. Unsafe acts and conditions are being recorded through VA system. (b). unsafe act, unsafe condition observed in the CCTV are recorded as safety observation in Aarohan. (d) Checked randomly, date and CCTV name stamping calibrationshed is found incorrect. Checked visitor gate CCTV for 03-05.08.2026 and observed that frisking of contract workmens is not being done for all workmen. | 2.6 | CCTV functioning checked | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155021 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155021 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155021 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155021 |  | AUD-2026-09-2000017759ACN-2026-09-4000155021 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155022 | Open |  |  | C bacs installed near planning room is non operational. | 2.8 | Access control systems checked | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155022 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155022 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155022 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155022 |  | AUD-2026-09-2000017759ACN-2026-09-4000155022 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155031 | Open |  |  | 1. Pumps, quarterly checks being carried out. Bio Deisel Pump of UG Tank no 107A is undermaintenance. 2. Detailed tank external inspection done in FY 2025-26 for tank during and reports available. Compliance to Recommendation is not available. 3. A structurallyadequate operating platform with safe access, standard handrails and toe guards shall be provided for operation and maintenance of the elevated valve at TWD PH 4. The product pump-house for TT Gantry, UG tank , TWG Loading Pump, Ethanl tank ouside dyke ,containment/drainage arrangement was found open/incomplete and may not reliably route leakage to OWS/ETP. 5. Fire water network is laid inclosed loop as far as possible to ensure multidirectional flow. Location to review the adequacy of fire fighting facility around TTemergency road and solar plant. 6. Sprinkler Checked for tank 101C, choked U54, U55, U58 & U59 and 101A - choked L50 & L52. 7. History card to be maintained for fire extinguisher, HVAC. | 4.2 | Maintenance activities reviewed | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155031 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155031 | 2026-09-10 21:00 | 38.8788 | 424 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155031 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155031 |  | AUD-2026-09-2000017759ACN-2026-09-4000155031 | 21 |  | 27 | 80 | 0 | -26 | 61
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155033 | Open |  |  | Disposal of un-used or damaged assets, misc scrap is to be expedited. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155033 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155033 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155033 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155033 |  | AUD-2026-09-2000017759ACN-2026-09-4000155033 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155034 | Open |  |  | Additional ESD or VHF to be provided to security personnel deployed in TT parking entry gate in security cabin. Unique identification number shall be given to MCP installed at location. | 6 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155034 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155034 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155034 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155034 |  | AUD-2026-09-2000017759ACN-2026-09-4000155034 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155036 | Open |  |  | Alternate approach to sample room & sample room and toilet block behind TT gantry.shall be provided. | 6.2 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155036 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155036 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155036 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155036 |  | AUD-2026-09-2000017759ACN-2026-09-4000155036 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155043 | Open |  |  | Road around dyke has developed cracks and settled at many place. Further side embankment of road is also settled. | 6.9 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155043 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155043 | 2026-09-10 21:00 | 38.8788 | 486 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155043 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155043 |  | AUD-2026-09-2000017759ACN-2026-09-4000155043 | 21 |  | 27 | 80 | 0 | -26 | 70
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155045 | Open |  |  | Height restriction barrier is not provided at road and track crossing. | 6.11 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155045 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155045 | 2026-09-10 21:00 | 38.8788 | 424 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155045 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155045 |  | AUD-2026-09-2000017759ACN-2026-09-4000155045 | 21 |  | 27 | 80 | 0 | -26 | 61
[5 empty] | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155102 | Open |  |  |  | 6.18 |  | 1410 | VADODARA TERMINAL | Location to follow up with GIDC for demand note and make the payment to close the accrual. | SOD | Marketing | NWR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155102 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155102 | 2026-09-10 21:00 | 38.8788 | 424 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155102 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017759ACN-2026-09-4000155102 |  | AUD-2026-09-2000017759ACN-2026-09-4000155102 | 21 |  | 27 | 80 | 0 | -26 | 61
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154526 | Open |  |  | Senior Management Inspection March 2026 - 9/12 - Complied 2. Bay no. 2 to be made functional at the earliest 3. Audit points to be complied in time bound manner Current Status of open points: OISD - 43/43, no Open Points SAFE 100 - 46/47 closed MDSA 2025 - 50/50, no Open Points Comprehensive March 2026 - 23/26 closed T4S audit : 11/23 closed GM SWZ inspection March 2026 :9/12 closed GM Cochin Zone June 2026 : 13/21 closed HLSA : 1 Open point | 1.4 | Earlier action points status checked | 1845 | IRUMPANAM TERMINAL | 1. Pending points to be complied in time bound manner. 2. KSEB started to adjust monthly HT bill towards refund of Rs. 25 lakhs excess Security Deposit - Reco of amount adjusted is to be mainatined w.r.t monthly bills 3. Follow up with CPO for placement of VRU AMC at the ealriest | SOD | Marketing | CZR | 2026-11-30 |  | 4 |  | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017404ACN-2026-09-4000154526 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154526 | 2026-09-02 16:30 | 47.0663 | 455 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154526 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017404ACN-2026-09-4000154526 |  | AUD-2026-09-2000017404ACN-2026-09-4000154526 | 21 |  | 27 | 80 | 1 | -4 | 65
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154528 | Open |  |  | Close monitoring of safety critical equipments, periodic CCTV review, VA simulations, imp. of e- Dairy observations and timely resolution etc. were discussed | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1845 | IRUMPANAM TERMINAL | 1. Standing orders for M&R, Safety, HK material and Routine consumables to be worked out. Efforts are to be made for contributions to Samridhi 2.0 2. Location to work out for CP AMC PO for local pipeline. Quantities of 16 Jetty pipeline from CBOT are to be considered in the tender. CP TRU is to be kept in auto mode | SOD | Marketing | CZR | 2026-12-31 |  | 6 |  | S2 | F3 | 2026-12-31 | AUD-2026-09-2000017404ACN-2026-09-4000154528 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154528 | 2026-09-02 16:30 | 47.0663 | 486 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154528 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017404ACN-2026-09-4000154528 |  | AUD-2026-09-2000017404ACN-2026-09-4000154528 | 21 |  | 27 | 80 | 1 | -4 | 70
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154532 | Open |  |  | Ethanol TTs are being taken in to location premises with Gate pass, in dedicated Ethanol unloading bay 13,16 and 24.The same are being checked for dips with dip rods and certificates, Once unloading is completed the same are being verified for emptiness at old barrel filling shed with two officers and security checks. Simultaneously opening and closing dips of UG tanks are monitored during unloading to ensure proper quantity | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1845 | IRUMPANAM TERMINAL | Turbo additive dosing auto function is to be enabled. Power additive skid is functional in auto mode | SOD | Marketing | CZR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017404ACN-2026-09-4000154532 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154532 | 2026-09-02 16:30 | 47.0663 | 394 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154532 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017404ACN-2026-09-4000154532 |  | AUD-2026-09-2000017404ACN-2026-09-4000154532 | 21 |  | 27 | 80 | 1 | -4 | 57
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154534 | Open |  |  | MFM vs BCU totalizer difference is less than 0.1% in all MS/HSD Bays.Sustence of dip elimination : | 3.11 | MFM vs BCU totalizer comparison checked | 1845 | IRUMPANAM TERMINAL | Expedite to re submit dip elimination file note as per SOP from HQO. Last audit recommendation | SOD | Marketing | CZR | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-09-2000017404ACN-2026-09-4000154534 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154534 | 2026-09-02 16:30 | 47.0663 | 394 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154534 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017404ACN-2026-09-4000154534 |  | AUD-2026-09-2000017404ACN-2026-09-4000154534 | 21 |  | 27 | 80 | 1 | -4 | 57
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154536 | Open |  |  | Current Status of open points: OISD - 43/43, no Open Points SAFE 100 - 46/47 closed MDSA 2025 - 50/50, no Open Points Comprehensive March 2026 - 23/26 closed T4S audit : 11/23 closed GM SWZ inspection March 2026 :9/12 closed GM Cochin Zone June 2026 : 13/21 closed HLSA : 1 Open point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1845 | IRUMPANAM TERMINAL | Audit compliance to be done in time bound manner | SOD | Marketing | CZR | 2026-10-31 |  | 9 |  | S3 | F3 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154536 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154536 | 2026-09-02 16:30 | 47.0663 | 425 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154536 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017404ACN-2026-09-4000154536 |  | AUD-2026-09-2000017404ACN-2026-09-4000154536 | 21 |  | 27 | 80 | 1 | -4 | 61
[5 empty] | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154537 | Open |  |  | Reviewed maintenance of MS tank TK19. | 4.2 | All activies are being performed with Permits and with all PPE in place. | 1845 | IRUMPANAM TERMINAL | Tk19 is to be brought back to regular operations on top most priority, after repairs with all safety measures, as only two tanks are available for regular PLT and loading operations. | SOD | Marketing | CZR | 2026-10-31 |  | 12 |  | S4 | F3 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154537 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154537 | 2026-09-02 16:30 | 47.0663 | 425 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154537 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017404ACN-2026-09-4000154537 |  | AUD-2026-09-2000017404ACN-2026-09-4000154537 | 21 |  | 27 | 80 | 1 | -4 | 61
DINKAR SUMIT | 2026-09-29 | KUMAR GOPESH | 2026-09-28 | 1. Fire Drill Observer & Role Rotation – Complied Observer is being assigned during every fire drill as M&I Sr Manger & Safety manager as chnaged rolls of observer . Roles are rotated among team members, including Combat, Auxiliary and Rescue teams, to ensure cross-functional competency and preparedness. 2. Fire Drill Observation & Improvement – Complied During the latest L2 Fire Drill conducted on 16.09.2026, all MARG team members and the designated observer participated. Observations/improvement points were identified, communicated and necessary corrective actions have been completed. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153014 | Closed | KUMAR GOPESH | 2026-09-28 | Double contingency simulated on 9th Sept. One was leakage scenario in bay 16 and 2nd was fire scenario in pump no. 3 at PH. Mr. Rathore was made as an observer; Observation recorded as below: 1. Equipment worked well and foam generation was good. 2. There were good coordination among team members. 3. Person who attended to check LEL, he should be backed with fire hose in ready condition. He should also be wrapped with rope for pulling him in case of emergency. 4. Security guard needs to direct fire tender and TTs to move properly. 5. Security guard should use whistle for better attention. 6. Location should check drain and ETP for checking of product seepage. 7. Team member didn't tell anything about information given to outsider. | 2.2 | Double contingency scenario simulated; observations recorded | 1281 | AJMER TERMINAL | Pls keep one officer as observer. LIC can also become observer. You may also engage IOC/BPC officer as an observer. Work on improvements. | SOD | Marketing | NWF | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-30 | AUD-2026-09-2000017605ACN-2026-09-4000153014 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153014 | 2026-09-09 17:45 | 40.0143 | 393 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153014 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153014 | AUD-2026-09-2000017605ACN-2026-09-4000153014 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
DINKAR SUMIT | 2026-09-29 | KUMAR GOPESH | 2026-09-28 | Fortnightly night inspections are being conducted and records are maintained. Two designated officers carry out the inspection eachtime to ensure effective monitoring and compliance. also signed every monthaly ragister . | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153015 | Closed | KUMAR GOPESH | 2026-09-28 | Okay. Night inspection record to be maintained. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1281 | AJMER TERMINAL | Surprise night inspection to be done. Record to be maintained | SOD | Marketing | NWF | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153015 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153015 | 2026-09-09 17:45 | 40.0143 | 393 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153015 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153015 | AUD-2026-09-2000017605ACN-2026-09-4000153015 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-29 | KUMAR GOPESH | 2026-09-28 | 1. Fire Brigade Training – Complied Fire Brigade training was conducted at the location on 25.12.2025. The next training has been planned for October 2026, and a formal request letter has been issued for scheduling the training. Training records are maintained. 2. Security Coordination Committee – Complied Security coordination meetings have been conducted with relevant external agencies. A meeting was held on 16.09.2026 with the Sr. Factory Inspector and Ajmer Civil Defence. Coordination was also carried out with CHO Mangliyawas and the Bomb Squad Team on 25.08.2026. Records of the meetings are maintained. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153016 | Closed | KUMAR GOPESH | 2026-09-28 | Reviewed the same. 1. It is advised to get the workforce trained by called personnel from Fire Brigade office. 2. It is also advised to have security coordination committee meeting with Police personnel, mutual aid members and statutory authorities. | 2.5 | Emergency response preparedness reviewed | 1281 | AJMER TERMINAL | Reviewed the same. 1. It is advised to get the workforce trained by called personnel from Fire Brigade office. 2. It is also advised to have security coordination committee meeting with Police personnel, mutual aid members and statutory authorities. | SOD | Marketing | NWF | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153016 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153016 | 2026-09-09 17:45 | 40.0143 | 393 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153016 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153016 | AUD-2026-09-2000017605ACN-2026-09-4000153016 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-29 | KUMAR GOPESH | 2026-09-28 | Quarterly inspection of potential hazard areas has been carried out by Shri Ankur, Shri Vishal, Shri Rajeev Sarawagi, Shri Gopesh Kumar and Shri Divyansh Shukla, including LIC participation, on08.09.2026 & 09.09.2026 , 26.09.2026 and 28.09.2026. During the inspection/training,HLVR testing of fixed type 06 installed in location ,Sprinkaleres on the dyke-02 &03 tested , HVLR systems were tested and operated as per OISD-244 requirements. DCP fire extinguishers and foam monitors were also operated by the officers. Eight hydrant mobile HVLR (2000 GPM) operations were demonstrated in the field, and hands-on training was provided to the officers. Inspectionand training records are maintained. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153018 | Closed | KUMAR GOPESH | 2026-09-28 | 1. . It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area asper OISD 244 checklist and maingtain record. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1281 | AJMER TERMINAL | 1. It is advised to make inspection of two potential hazard areas once in quarter by each officer. They should check that area as per OISD 244 checklist and maingtain record. | SOD | Marketing | NWF | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153018 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153018 | 2026-09-09 17:45 | 40.0143 | 393 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153018 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153018 | AUD-2026-09-2000017605ACN-2026-09-4000153018 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-29 | KUMAR GOPESH | 2026-09-29 | a) All earth pits were checked and found satisfactory. Earth resistance values are within permissible limits as per IS 3043 design and specifications. No abnormality observed. Corrective actions, wherever required, have been completed and the system is found compliant. testing of all in the month june-july2026 . b) Vegetation and grass from the 4-pole structure area were removed in the presence of a qualified electrician. Grass cutting has been completed and the removed vegetation was properly disposed of. Housekeepingactivities were also carried out using 3 manpower. The entire area has been cleaned, is clearly visible, and found in good condition. Status: ✅ Checked and Found OK. All parameters are within acceptable limits and housekeeping is satisfactory. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153031 | Closed | KUMAR GOPESH | 2026-09-29 | 1. Earth pit lay out diagram is not there facility wise. Pls get it installed and displayed. Pls check for the accuracy of earth pit lay out. 2. Many erath pits were found without funnel and mesh. Gap between two erath strips were also observed in few earth pits. | 3.16 | Earth pits / boundary / vegetation control checked | 1281 | AJMER TERMINAL | a) All earth pits to be checked and corrective action to be taken as per IS 3043 design and spec b) Vegetation to be removed from 4-pole structure area in presence of qualified electrician | SOD | Marketing | NWF | 2026-11-30 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017605ACN-2026-09-4000153031 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153031 | 2026-09-09 17:45 | 40.0143 | 393 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153031 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153031 | AUD-2026-09-2000017605ACN-2026-09-4000153031 | 21 | 21 | 27 | 80 | 0 | 0 | 65 | 57
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-09-29 | All the Officer has been advised by LIC for taking daily round of Depot at least twice in shift and check all the area for any pending job/ house keeping etc | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152010 | Closed | DIGRA SUNIL KUMAR | 2026-09-29 | Interacted with all officers of the Location and enquired about their respective areas of operation & issue faced, if any. Special emphasis given on new officers, guiding them how to learn, update, innovate & conduct themselves. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1256 | JAMMU DEPOT | Advised officers to take daily round of the location at lease once a day. LIC to ensure the same. | SOD | Marketing | NFZ | 2026-09-07 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-07 | AUD-2026-09-2000017601ACN-2026-09-4000152010 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152010 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152010 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017601ACN-2026-09-4000152010 | AUD-2026-09-2000017601ACN-2026-09-4000152010 | 21 | 21 | 27 | 80 | 1 | -4 | 53 | 57
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-09-29 | Regular briefing of security is being done to ehance security thrice a week to sensitize all about the safety and security aspect of Depot Operation. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152012 | Closed | DIGRA SUNIL KUMAR | 2026-09-29 | Security briefings not given during first visit. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1256 | JAMMU DEPOT | Advised DSO to train Security personnel for regular briefings. | SOD | Marketing | NFZ | 2026-09-04 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-04 | AUD-2026-09-2000017601ACN-2026-09-4000152012 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152012 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152012 | 532 | 8294 | 21 | 8294 | 45 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017601ACN-2026-09-4000152012 | AUD-2026-09-2000017601ACN-2026-09-4000152012 | 21 | 21 | 27 | 80 | 1 | -4 | 53 | 57
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-09-29 | One of the E0 Officer has been sent for 5 day safety training to Lucknow and hands on trainings are being provided to all the Officers at the location by HSE Officer and LIC. Location. Further we would be sending the Other E) officer also for Safety Training aalong with the Live fire fighting training as well as per the availability of the slot | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | ONE OF THE E0 OFFICER HAS BEEN SENT FOR | ACN-2026-09-4000152013 | Closed | DIGRA SUNIL KUMAR | 2026-09-29 | Fire extinguisher was operated by officer. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1256 | JAMMU DEPOT | All officers to be further trained on firefighting activities. | SOD | Marketing | NFZ | 2026-09-30 | INADEQUATE SAFETY CULTURE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017601ACN-2026-09-4000152013 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152013 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152013 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017601ACN-2026-09-4000152013 | AUD-2026-09-2000017601ACN-2026-09-4000152013 | 21 | 21 | 27 | 80 | 1 | -4 | 57 | 57
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-09-29 | All efforts are being done to ensure the timely topping up of Leh and srinagar by addition of TT's and there smooth induction. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152016 | Closed | DIGRA SUNIL KUMAR | 2026-09-29 | Reviewed the product supply situation in detail and suggested increased coordination & planning. | 6.1 | Product supply situation | 1256 | JAMMU DEPOT | Location to ensure timely topping up of product at Leh & Srinagar. | SOD | Marketing | NFZ | 2026-10-15 | INSUFFICIENT SUPERVISION | 12 | PROCESS SAFETY | S3 | F4 | 2026-10-15 | AUD-2026-09-2000017601ACN-2026-09-4000152016 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152016 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152016 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017601ACN-2026-09-4000152016 | AUD-2026-09-2000017601ACN-2026-09-4000152016 | 21 | 21 | 27 | 80 | 1 | -4 | 59 | 57
GARBYAL LOKENDER | 2026-09-29 | DIGRA SUNIL KUMAR | 2026-09-29 | Induction of second phase of additional TT has already begun and 24 TT's has been inducted. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000152018 | Closed | DIGRA SUNIL KUMAR | 2026-09-29 | Increase in demand of DS to be met religiously. | 6.3 | Direct Sales Supplies | 1256 | JAMMU DEPOT | Location to ensure timely supplies with proper planning once additional TTs are inducted. | SOD | Marketing | NFZ | 2026-09-15 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-15 | AUD-2026-09-2000017601ACN-2026-09-4000152018 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152018 | 2026-09-04 | 45.7538 | 393 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152018 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017601ACN-2026-09-4000152018 | AUD-2026-09-2000017601ACN-2026-09-4000152018 | 21 | 21 | 27 | 80 | 1 | -4 | 55 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | 1."One contract staff (C/S) from the Planning section has been redeployed for Tank Truck Safety Inspection, housekeeping of the Planning Room, document segregation, toll document filing, and other related activities. 2.Updating of checklists in computer/register has been assigned to the security guard in addition to regular security duties, resulting in optimum utilization of available manpower. 3.The existing manpower Purchase Order (PO) is valid up to 31.03.2028, and no additional manpower deployment is proposed during the current contract period. 4.Manpower optimization measures have been implemented under the existing contract ,he existing manpower Purchase Order (PO) is valid up to 31.03.2028 . Future manpower requirements will be assessed based on actual job requirements during the next contract cycle, and the LPR will be prepared accordingly." | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153013 | Closed | KUMAR GOPESH | 2026-09-29 | a. Carried out with all officers and LIC. New officer joined was greeted by me. b. There are 4 contract staffs working inside Admin Building. Two at planning room. Two are working as office boy. Apart from these 4 contract staffs, there is one cook who takes care of meal/tea etc. c. Driver of emergency vehicle can be utilised to maintaiun register in security gate (if he is educated). Thisis my suggestion. d. Jobs related to electrical, maintenance, housekeeping which are done periodically in some fixed intervals (weekly, fortnightly, monthly, quarterly etc) are to be listed by officer. the same to be shared with zone. Convert these jobs on manpower basis. A separate PO to be placed for getting these periodical jobs on job basis instead of manpower basis. e. Electrical maintenance PO needs to be revised. One electrician to be called in each shift. General shift electrician should not be paid on manpower basis. It should be on job basis | 1.1 | Interaction with all officers (1–1.5 hrs) | 1281 | AJMER TERMINAL | 1. It is advised to remove one contract staff from office and planning room. Contract staffs should be increased in housekeeping job. 2. Security guard is presently maintaining register and fill check list in system. Job of security guard is to carry out checksand do the patrolling in field. Updation of check list in computer/register should be carried out through contract staff in stead of DGR security gaurd. This will save cost. 3. Manpower basis jobs to be converted on job basis PO as mentioned in my observation 4. Electrical maintenance PO needs to be revised. One electrician to be called in each shift. General shift electrician should not be paid on manpower basis. It should be on job basis | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 3 | PROCESS SAFETY | S1 | F3 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153013 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153013 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153013 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017605ACN-2026-09-4000153013 | AUD-2026-09-2000017605ACN-2026-09-4000153013 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | "Conducted eyesight screening of 20 TT drivers during the TT crew training session in the conference room. Purchased the Snellen Chart to carry out proper vision testing of drivers, including those using spectacles. eyesight checks performed using available resources and medical fitness records during the TT Crew training ." | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153019 | Closed | KUMAR GOPESH | 2026-09-29 | 1. Pls purchase snellen chart (eye chart) to check whether drivers are able to read through some distance even after wearing spectacle. | 2.16 | Eyesight / colour-blindness awareness checked | 1281 | AJMER TERMINAL | 1. Pls purchase snellen chart (eye chart) to check whether drivers are able to read through some distance even after wearing spectacle. | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153019 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153019 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153019 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153019 | AUD-2026-09-2000017605ACN-2026-09-4000153019 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | All invoices, correspondence documents, gate passes, and other records have been properly segregated and filed by the S&D Officer and team. The documents are now stored systematically in box files and shifted to the designated vacant store area. All files have been kept inside aluminum storage containers, and each container has been properly labeled with serial numbers and document category stickers for easy identification and retrieval. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153030 | Closed | KUMAR GOPESH | 2026-09-29 | 1. Signed Invoices and other correspondences are kept in loose conditions inside Admin building/planning room. Instead of binding it, pls ask office boy to wrap the bundle of invoices (one bundle for one day) by rope. Purchase cartoon and keep the bundles inside cartoon. Write the dates of invoice on body of cartoon. All these jobs should be carried out by contract staff at office/planning room. | 3.15 | Housekeeping & PPE usage checked | 1281 | AJMER TERMINAL | 1. Pls ensure that all invoices are properly kept inside cartoon/GI box. No invoice should be kept loose. Similarly, all correspendences in hard copies, gate pass etc should not be kept loose. | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153030 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153030 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153030 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153030 | AUD-2026-09-2000017605ACN-2026-09-4000153030 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | "Out of the pending Sr. Management Inspection observations, two points have already been completed. The UG-7 Radar system has been made operational and was verified on 27.09.2026. The same has also been reflected in Auto Reconciliation. Further, toll discount implementation has been completed at the identified toll plazas as advised by GM Sir. These were old observations and have already beencovered in the latest audit. The current audit contains three different pending observations, namely: 6.8 Additional Observations - Lube related 6.7 Additional Observations - Toll related 4.3 Infrastructure, Project & M&I Assessment - Bay 12 concreting related" All above points as repaeted in this audit and same to be closed before the traget dates 31.12.2026 . | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153032 | Closed | KUMAR GOPESH | 2026-09-29 | 4 points of Sr. Management Audit is pending. 2 points to be completed by 30.09.2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1281 | AJMER TERMINAL | Sr. Management Inspection points to be complied. For any discussion, location should come forward | SOD | Marketing | NWF | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 8 | PROCESS SAFETY | S2 | F4 | 2026-12-31 | AUD-2026-09-2000017605ACN-2026-09-4000153032 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153032 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153032 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153032 | AUD-2026-09-2000017605ACN-2026-09-4000153032 | 21 | 21 | 27 | 80 | 0 | 0 | 70 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | 1. TT crew uniform compliance ensured through daily instructions and TT crew meetings. 2. TT crew ID card display ensured duringterminal entry, meetings and loading operations. 3. TT In/Out register at locking shed made mandatory; signatures are being recorded and compliance verified by LIC. 4. Safety reporting increased to UA–12, UC–41 and Near Miss–08. Recognition provided to encourage reporting; September 2026 award given to Shri Lalit Kumar for safety reporting/suggestion. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153033 | Closed | KUMAR GOPESH | 2026-09-29 | Interacted with TT crew. It is suggested: 1. TT crew should be asked to wear uniform. 2. They should always keep their ID card and display the same. 3. Driver sign is not being taken in TT In/out register. Respective column was found without signed. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1281 | AJMER TERMINAL | 1. TT crew should be asked to wear uniform. 2. They should always keep their ID card and display the same. 3. Driver sign is notbeing taken in TT In/out register. Respective column was found without signed. 4. No. of UA, US and NM reported from Apr-Aug 2026 are 2, 20 and 2 respectively. It is very less and not acceptable. Suggestion box to be opened on monthly basis and give award to stakeholders for best suggestions. This should be recorded in regsiter/file with photograph. Contract labours, security guards, TT crew are to be motivated to report unsafe acts, unsafe situation and near misses through suggestion scheme. They should be rewarded suitably. | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153033 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153033 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153033 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153033 | AUD-2026-09-2000017605ACN-2026-09-4000153033 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | "An inventory of usable and valuable materials is being maintained by the M&I Officer in an Excel-based record. Materials have beensegregated and monitored as per requirement. As of H1 FY 2026-27, no scrap material is available at the location; hence, no RFD is pending. The status has been reviewed and maintained accordingly. Compliance Status: ✅ Complied | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153037 | Closed | KUMAR GOPESH | 2026-09-29 | Segregation of usable and disposable materials inside store. Make inventory of usable and costly material in excel sheet. Inform Zone. Make RFD for all scrappable materials seen inside store and scrap yard. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1281 | AJMER TERMINAL | Segregation of usable and disposable materials inside store. Make inventory of usable and costly material in excel sheet. Inform Zone. Make RFD for all scrappable materials seen inside store and scrap yard. | SOD | Marketing | NWF | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153037 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153037 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153037 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153037 | AUD-2026-09-2000017605ACN-2026-09-4000153037 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | The VA (Video Analytics) alert display has been configured and implemented at the Security Main Gate. The designated display screenlinked to the Ajmer Terminal VA system (Display URL: 10.2.193.126:90) is functioning properly, and all critical alerts generated inthe plant are displayed as pop-up notifications on the screen for real-time monitoring and prompt response. The observation has been complied with and closed." | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153029 | Closed | KUMAR GOPESH | 2026-09-29 | In case of critical VA alert, audio/visual alert should come on screen placed at security gate. Pls ensure | 3.12 | Critical alarms checked & corrective actions reviewed | 1281 | AJMER TERMINAL | In case of critical VA alert, audio/visual alert should come on screen placed at security gate. Pls ensure | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153029 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153029 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153029 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153029 | AUD-2026-09-2000017605ACN-2026-09-4000153029 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-29 | The branding status of the concerned TTs was verified and valid 3M branding certificates were obtained and reviewed for the following vehicles: TT No. RJ39GA4790 (M/s Guru Kripa Enterprises) - Branding Date: 31.05.2023, Warranty Valid up to 31.05.2028. TT No.RJ09GC9629 (M/s Ladu Singh Rawat) - Branding Date: 25.05.2023, Warranty Valid up to 25.05.2028. TT No. RJ27GD5930 (Nagda HP Fuel Station) - Branding Date: 19.11.2021, Warranty Valid up to 19.11.2026. It was further verified that TT No. RJ18GB4711 belongs to Jaipur Terminal and is not an Ajmer Terminal-based TT. The 3M branding certificates of the above TTs have been validated, records updated, and the observation has been complied with. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153020 | Closed | KUMAR GOPESH | 2026-09-29 | Branding of TT no. RJ37GD5930, RJ09GC9629, RJ39GA4790 RJ18GB4711 are not good. | 3.1 | TT fittings & discipline checked | 1281 | AJMER TERMINAL | Branding of TT no. RJ37GD5930, RJ09GC9629, RJ39GA4790 RJ18GB4711 are not good. To be done. As suggested to ankur, pls note down TT no. running at Ajmer Tml. Write the date on which new 3M sticker pasted on TT. Pls share the same with Zone | SOD | Marketing | NWF | 2026-10-31 | POOR COMMUNICATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153020 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153020 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153020 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153020 | AUD-2026-09-2000017605ACN-2026-09-4000153020 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-30 | A field verification was carried out on 25.09.2026 for three tank trucks at the gantry. Inline temperatures recorded through MFM and actual gasohol temperatures measured using a cup thermometer were cross-checked. The observations confirmed the expected reductionin gasohol temperature due to blending heat loss. The readings were found to be consistent and within the expected operating range. Sr No Bay No TT No MS MFM Temp Eth MFM Temp TT Sample Temp Gasohol Invoice Temp Gasohol 1 14 RJ12GA9909 32.9 34.9 29.5 33 2 15 RJ20GC2123 32.1 34.2 29.25 32.79 3 16 RJ27GD5952 33 34.34 29.25 33.22 | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153024 | Closed | KUMAR GOPESH | 2026-09-30 | Checked for TT no. GJ12BZ9615. Found okay | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1281 | AJMER TERMINAL | 1. It was discussed that there is heat loss during blending of petrol with ethanol. This reduces the temp. of gasohol. The same is not recorded by MFM. It was informed that MFM records gasohol temp at ratio of MS and ethanol line temp. Pls cross check the same for three TTs and share the actual result. Pls also check temp of gasohol in these three TTs using cup thermometer (to ensure minimum delay in measurement of temp.) | SOD | Marketing | NWF | 2026-10-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153024 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153024 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153024 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153024 | AUD-2026-09-2000017605ACN-2026-09-4000153024 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-30 | TT No. RJ09GC9629 was rechecked jointly by the Safety Manager, Gantry Operators, and LIC personnel on multiple occasions. Verification was carried out using the approved calibration chart and physical dip measurement using calibrated inch tapes. The TT was checked on Bay No. 04 on 26.09.2026 and Bay No. 06 on 30.09.2026. Dip measurements were cross-verified with the calibration chart and physical measurements. No significant variation was observed in any compartment. A minor variation of 1 mm was noticed in Compartment No. 02, which is within acceptable limits and does not indicate any calibration issue. All measurements and records were reviewed and found satisfactory. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153021 | Closed | KUMAR GOPESH | 2026-09-30 | Checked dip of following TTs: 1. RJ21GC7557: ok/ok/+2 mm 2. RJ05GA9022: +1 mm/+2mm/+3 mm/+1 mm 3. RJ35GA0999: -1 mm/ok/+2 mm/+1 mm 4. RJ09GC9629: +3/+2/+2/+3 mm 5. RJ39GA4790: +2/+1/ok/ok/ok 6. RJ01GB3189 +1/ok/ok/ok Bay combination: 1 to 8: MS/HSD/Ethanol 9 to 11: Pure HSD 12: Under conversion- MS/HSD/Eth 13 to 16: MS/HSD/Ethanol Bay 11: Having facility to load MS-91 RON, Bio diesel loading in bay no. 7, 10, 13 and 16 | 3.2 | Post-loading dip checks verified | 1281 | AJMER TERMINAL | Variation observed in TT no. RJ09GC9629. To be checked for two times more. If there is issue, pls carry out recalibration | SOD | Marketing | NWF | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153021 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153021 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153021 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153021 | AUD-2026-09-2000017605ACN-2026-09-4000153021 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-30 | 1. UG7 Radar installation has been completed and Auto Reconciliation has been enabled. With the successful commissioning of the radar and integration into the Auto Reconciliation system, the reconciliation performance is expected to improve and consistently achieve above 95% from the next month onward. 2. R3 performance at Ajmer Terminal has been significantly improved and is among the best in NWFZ. The first tank truck is being inducted for loading at 08:30 hrs sharp on a daily basis, and operational controls have been strengthened to ensure the first R3 TT exits before 09:05 hrs, except in unavoidable circumstances. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153026 | Closed | KUMAR GOPESH | 2026-09-30 | It is less than 95%. It needs improvement. Secondly, location needs to work on 1st R3 time. Out of 54 working days in July and Aug 2026, 1st TT was dispatched after 09.10 hr in 34 days. This is very high. Location is supposed to write the reasons for any delay beyond 09.10 hr in 1st TT dispatch on any day. Pls record the reason and send it to Zone. | 3.8 | Auto vs Manual reconciliation checked | 1281 | AJMER TERMINAL | 1. Auto vs manual reco performance to improve. It should be 95%. 2. 1st R3 should be before 09.10 hr on very day except unavoidable case. | SOD | Marketing | NWF | 2026-10-31 | POOR EQUIPMENT MAINTENANCE | 15 | PROCESS SAFETY | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017605ACN-2026-09-4000153026 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153026 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153026 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153026 | AUD-2026-09-2000017605ACN-2026-09-4000153026 | 21 | 21 | 27 | 80 | 0 | 0 | 61 | 57
DINKAR SUMIT | 2026-09-30 | KUMAR GOPESH | 2026-09-30 | UG7 Radar has been rectified and brought into operational condition as of 27.09.2026. The radar is now successfully integrated withthe Auto Reconciliation System and is reflecting Green Status in the Consolidated Tank Auto Reconciliation Report Plan. Additionally, Physical Inventory Document No. 100248002 has been posted without any differences, confirming successful reconciliation. | VISIT TO AJMER TML ON 8TH, 9TH SEPT Q2 | 2026-09-09 17:45 | AUD-2026-09-2000017605 | 2026-09-08 12:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153028 | Closed | KUMAR GOPESH | 2026-09-30 | TFMS vs SAP % is less than 95%. It is mainly due to entry of manual dips. 52 manual dips in July and 32 manual dips in Aug. UG7 is having bio diesel, however, its radar is not in working condition | 3.10 | TFMS/SAP reconciliation checked | 1281 | AJMER TERMINAL | UG7 radar to be brought in running condition | SOD | Marketing | NWF | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017605ACN-2026-09-4000153028 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017605ACN-2026-09-4000153028 | 2026-09-09 17:45 | 40.0143 | 394 | >20 | AUD-2026-09-2000017605 - ACN-2026-09-4000153028 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017605ACN-2026-09-4000153028 | AUD-2026-09-2000017605ACN-2026-09-4000153028 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
|  | CHANGMAI RAHUL | 2026-09-30 | List of critical equipment prepared namely 1.DG set 2. Transformer 3. Earthpit 4.BCU 5. DCV unit 6. UG pumps 7. Fire alarm Panel 8 ESD maintained with regualr checks | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152321 | Completed | CHANGMAI RAHUL | 2026-09-30 | Critical equipment checklist not maintained. | 4.2 | Maintenance activities reviewed. | 1708 | DIMAPUR DEPOT | Critical equipment checklist needs to be maintained with regular checks. | SOD | Marketing | GZR | 2026-09-25 |  | 2 |  | S1 | F2 | 2026-09-25 | AUD-2026-09-2000017853ACN-2026-09-4000152321 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152321 | 2026-09-12 | 37.7538 | 389 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152321 | 532 | 8294 | 21 | 8294 | 24 | 30 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152321 |  | AUD-2026-09-2000017853ACN-2026-09-4000152321 | 21 |  | 27 | 80 | 7 | 7 | 56
|  | CHANGMAI RAHUL | 2026-09-30 | 1.Supply is being done to dealers list as recommended by Finance Department which has maximum profitability. Also with the limitedmanpower regular maintenance and upkeep of location is maintained .2. Critical equipments AMC to be done in co-ordination with Vendors.Quotation is sought from concerned vendors.3. Site based format developed for critical equipments and filled after checking properly.4.All the faulty TAS equipment list are identified and shared to Zone. | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152314 | Completed | CHANGMAI RAHUL | 2026-09-30 | 1.Since inception Depot is not operational due to operational & other issues.It is started now and advised LIC to look for optimal utilisation of assets.2. For Critical equipments AMC not available.3. Details for regular M&I of equipments are not available. 4. TAS equipments are critical for running the Depot and still some equiments are not working. | 1.2 | Performance review conducted | 1708 | DIMAPUR DEPOT | 1.To carryout loading for identified Dealers from Depot.Manpowers are to be utilised optimally for regular maintenance and upkeep of Location.2. Critical equipments AMC to be ensured in co-ordination with Vendors.3. Site based format to be developed for critical equipments and after checking to be filed properly.4.Identify all equipments of TAS and its functionality.Prepare details and send to Zone for taking up with HQO. | SOD | Marketing | GZR | 2026-12-20 |  | 1 |  | S1 | F1 | 2026-12-20 | AUD-2026-09-2000017853ACN-2026-09-4000152314 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152314 | 2026-09-12 | 37.7538 | 475 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152314 | 532 | 8294 | 21 | 8294 | -61 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152314 |  | AUD-2026-09-2000017853ACN-2026-09-4000152314 | 21 |  | 27 | 80 | 7 | 7 | 68
SINGWAL DEEPAK | 2026-09-30 | GEETE DEVASHISH | 2026-09-01 | Since same observation was also made during previous location visit. Therefore, the compliance of this observation is to be referred from particular no. 1.6 of this audit sheet and from the particular no. 4.3 of previous visit report AUD-2026-03-2000011237 | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149448 | Closed | SINGWAL DEEPAK | 2026-09-01 | Yes, TAS Revamp Project is under progress. | 4.3 | Project progress reviewed | 1435 | GWALIOR DEPOT | Location to coordinate with AST for expediting completion of Project at the earliest. | SOD | Marketing | CEN | 2026-10-15 | POOR PLANNING OR RISK ASSESSMENT | 2 | ASSET INTEGRITY | S2 | F1 | 2026-10-15 | AUD-2026-08-2000017055ACN-2026-08-4000149448 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149448 | 2026-08-22 19:00 | 57.9622 | 394 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149448 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017055ACN-2026-08-4000149448 | AUD-2026-08-2000017055ACN-2026-08-4000149448 | 21 | 21 | 27 | 80 | 2 | 2 | 59 | 57
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Periodic reviews being done by Zone. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125531 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Reviewed perfromance of all Officers and officeres were found focussed on the Goals and Targets with emphasis on process/efficiencyimprovement | 1.2 | Performance review conducted | 1991 | CHENNAI TERMINAL | Team to focus on G&T for the year and come up with improvements proces and work efficency | SOD | Marketing | SZ | 2026-03-31 |  | 2 |  | S1 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125531 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125531 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125531 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125531 |  | AUD-2026-03-2000010826ACN-2026-03-4000125531 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Following up with vendor for project closure | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125532 | Completed | G RAMADOSS | 2026-03-22 | Solar project -works related to Solar panels installation under progress. Connection to inverter panel pending. Stabilization period is upto Apr 30 2026. | 1.3 | Pending issues reviewed | 1991 | CHENNAI TERMINAL | To expediate the closure of AR and monitor the solar generation on daily basis for expected output. | SOD | Marketing | SZ | 2026-03-31 |  | 8 |  | S4 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125532 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125532 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125532 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125532 |  | AUD-2026-03-2000010826ACN-2026-03-4000125532 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | All MDSA and SSA audit points which are not in Revamp are being closed. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125533 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | All the ESA Points have been complied for CNT. | 1.4 | Earlier action points status checked | 1991 | CHENNAI TERMINAL | Location to expedite the closure of Pending MDSA/SSA point of Tank inspection except from those which are not under revamp project. | SOD | Marketing | SZ | 2026-03-31 |  | 4 |  | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125533 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125533 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125533 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125533 |  | AUD-2026-03-2000010826ACN-2026-03-4000125533 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Following up with Zone/HQO for minutes of the AR extension for PO placement and closure of the project. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125534 | Completed | G RAMADOSS | 2026-03-22 | Finalization of Revamp and Budget allocation | 1.5 | HQO / Zonal support required identified | 1991 | CHENNAI TERMINAL | Location to continously follow up with HQO/Zone for fund allocation and project approval | SOD | Marketing | SZ | 2026-03-31 |  | 8 |  | S4 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125534 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125534 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125534 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125534 |  | AUD-2026-03-2000010826ACN-2026-03-4000125534 | 21 |  | 26 | 80 | 42 | 42 | 31
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Noted and being adhered to | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151077 | Closed | SHETTY ANURANJAN | 2026-09-30 | Mock drill conducted at around 17:30 hrs on 19.07.2026 in VRU area and observation recorded as below: 1. Equipment worked well andfoam generation was good. 2. Team members are required to know their role clarity as per their location fire organization chart. 3. Stretcher used was not having safety belt, advised to ensure same in future. 4. Location to ensure uninterrupted continuous flowof pressurized water during firefighting, However, there was a drop in pressure initially for a moment. Location to identify and correct route cause for same. 5. Security guard should use whistle for better attention. 6. Tank trucks from TT gantry should be moved only after confirmation from CIC. | 2.2 | Double contingency scenario simulated; observations recorded | 1242 | JAIPUR TERMINAL | This is continuous process of improvments. Location to improve upon in every fire drill | SOD | Marketing | NWF | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 15 | EMERGENCY | S3 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151077 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151077 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151077 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151077 | AUD-2026-09-2000016770ACN-2026-09-4000151077 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Surakshit refresher training provided to all security guards on 17-9-26, continuous process being implemented | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151079 | Closed | SHETTY ANURANJAN | 2026-09-30 | Frisking was not done by security. This shows lack of training by concerned officer. Pls ensure. Lady guard did registration for myself to enter license area. It is good and to be maintained | 2.8 | Access control systems checked | 1242 | JAIPUR TERMINAL | Training of security guard to be enhanced. They are not frisking and not giving safety briefing properly. | SOD | Marketing | NWF | 2026-09-30 | INADEQUATE SAFETY CULTURE | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151079 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151079 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151079 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151079 | AUD-2026-09-2000016770ACN-2026-09-4000151079 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Continuous Activity | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151083 | Closed | SHETTY ANURANJAN | 2026-09-30 | Checked dip of loaded Tts. Results are as below: 1. RJ18GB4711 (Hamara Pump Ozatu)- Load 4 + 4 +8 (power/Gasohol/HSd): 1: ok, 2:+1 mm, 3: ok, 4: ok 2. RJ14GT3385 (Sri Jagdish FS): 4 gasohol+8 HSD 1:+2 mm, 2:+2 mm, 3: +3 mm 3. RJ14GL8062: 1: +2 mm, 2: +1 mm, 3: +1 mm 4. RJ26GA3007: 1: ok, 2: ok, 3: ok 5. RJ14GT4442: 1: +1 mm, 2: ok, 3: ok 6. RJ14GQ1829: 1. +4 mm, 2: +2 mm, 3: +3 mm 7.RJ14GL3493: 1: +1 mm, 2: +1 mm, 3: ok | 3.2 | Post-loading dip checks verified | 1242 | JAIPUR TERMINAL | Variation observed in TT no. RJ14GQ1829 | SOD | Marketing | NWF | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151083 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151083 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151083 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151083 | AUD-2026-09-2000016770ACN-2026-09-4000151083 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Checks done in month of Sep-26 by LIC | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151086 | Closed | SHETTY ANURANJAN | 2026-09-30 | LIC is requested to check at least 30 Tts per week. Report should be shared with zone | 3.5 | EM Lock SOP compliance verified | 1242 | JAIPUR TERMINAL | LIC is requested to check at least 30 Tts per week. Report should be shared with zone | SOD | Marketing | NWF | 2026-11-30 | INSUFFICIENT SUPERVISION | 15 | PROCESS SAFETY | S3 | F5 | 2026-11-30 | AUD-2026-09-2000016770ACN-2026-09-4000151086 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151086 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151086 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151086 | AUD-2026-09-2000016770ACN-2026-09-4000151086 | 21 | 21 | 27 | 80 | 0 | 0 | 65 | 57
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Verification completed by TAS Officer | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151089 | Closed | SHETTY ANURANJAN | 2026-09-30 | Bay-11, LP 25, last k-factor was checked on 17.05.2023. The bay has not been verified for last 3 years. Only stamping is done by W&M officer. This is of MS transmix. As there is no UG tank of MS transmix, hence location is not doing. It is suggested to calibrate MS transmix tank truck in calibration shed. The same TT should act as reference. Calibrate MFM of LP 25 through calibrated TT. You may use master MFM also for verification. | 3.13 | K-factor changes reviewed (if any) | 1242 | JAIPUR TERMINAL | Pls carry out verification of Bay-11, LP 25 as suggested in my observation. | SOD | Marketing | NWF | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151089 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151089 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151089 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151089 | AUD-2026-09-2000016770ACN-2026-09-4000151089 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
SUDHIR KUMAR | 2026-09-30 | SHETTY ANURANJAN | 2026-09-30 | Advise being adhered to and verified in Aug-26 and will be continued monthly | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151300 | Closed | SHETTY ANURANJAN | 2026-09-30 | Despite my instruction in last Sr. management visit, gate pass control was found poor. It is observed that many returnable gate pass of year 2024 to 2026 are reflecting as open. Some returnable gate passes were observed under confirm despatch. Pls carry out confirm espatch of these materials which are already out for repair. Otherwise it will not show in open gate pass menu. Security should verify on monthly basis all returnable gate passes which are open and yet to be returned by vendor. This should be tallied with open RTGP as per online gate pass system. Both should match. Some of the gates pass which are still open are: 11242 R 025916 dt 17.06.26,11242 R 026412 dt 13.08.2026, 11242 R 025476 dt 08.05.2026. There are many other open RTGP. | 6.5 | RTGP monitoring | 1242 | JAIPUR TERMINAL | Monthly monitoring of RTGP by security to be done. Confirm despatch to be done after approving RTGP. | SOD | Marketing | NWF | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 10 | PROCESS SAFETY | S2 | F5 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151300 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151300 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151300 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016770ACN-2026-09-4000151300 | AUD-2026-09-2000016770ACN-2026-09-4000151300 | 21 | 21 | 27 | 80 | 0 | 0 | 57 | 57
|  | CHANGMAI RAHUL | 2026-09-30 | 1.Items are segregated. Scrap items shifted to scrapyard and other working equipment to store room in Admin building 2. Emergency Gate regular open close check is initiated and Security guards to carry the activity twice a week to ensure smooth opening and closing of the gate. 3. Expansion line, PRV is now kept open for all the tanks. 4. Quotation is already sought from 3 vendors for the partition with simillar material like exisiting other partition . i.e Glass,wood and aluminium frame | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152320 | Completed | CHANGMAI RAHUL | 2026-09-30 | Yes. 1.In MCC Room unused items are kept 2. Emergency Gate regular opening not checked. 3. Expansion line found in closed condition. 4. Control room Temp. observed not maintained due to insufficient AC. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1708 | DIMAPUR DEPOT | 1.Items to be kept separately 2. Emergency Gate regular opening needs to be checked. 3. Expansion line to be kept open always. 4. Option to be explored as discussed for partition of Control room equipments to maintain effectiveness of AC | SOD | Marketing | GZR | 2026-10-25 |  | 1 |  | S1 | F1 | 2026-10-25 | AUD-2026-09-2000017853ACN-2026-09-4000152320 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152320 | 2026-09-12 | 37.7538 | 419 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152320 | 532 | 8294 | 21 | 8294 | -5 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152320 |  | AUD-2026-09-2000017853ACN-2026-09-4000152320 | 21 |  | 27 | 80 | 7 | 7 | 60
|  | CHANGMAI RAHUL | 2026-09-30 | VHF GeM Tendering in process by CPO,Kolkata. Prohibited area declaration and No fly zone area permission is freshly applied throughFactory Department. Factory official has communicated its submission to Home Department (Police),Kohima | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152319 | Completed | CHANGMAI RAHUL | 2026-09-30 | Compliance status reviewed . OISD PCSA complied except the VHF procurement.SSA compliance for Prohibited area declearation is pending. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1708 | DIMAPUR DEPOT | All pending point to be complied | SOD | Marketing | GZR | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-09-2000017853ACN-2026-09-4000152319 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152319 | 2026-09-12 | 37.7538 | 485 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152319 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152319 |  | AUD-2026-09-2000017853ACN-2026-09-4000152319 | 21 |  | 27 | 80 | 7 | 7 | 70
|  | CHANGMAI RAHUL | 2026-09-30 | Radar Gauge for TK1 & TK2, Density probe for all the 4 UG tanks and MST and TSI for for all tanks will require AMC PO and also new equipment procurement. In touch with TAS vendor and shall initiate required procurement accordingly basis budget availability | SR MANAGEMENT AUDIT-DIMAPUR 2026-27 | 2026-09-12 | AUD-2026-09-2000017853 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152318 | Completed | CHANGMAI RAHUL | 2026-09-30 | TFMS automation faulty equipments,reco. done on Manual dip. | 3.8 | Auto vs Manual reconciliation checked | 1708 | DIMAPUR DEPOT | To replace faulty items | SOD | Marketing | GZR | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017853ACN-2026-09-4000152318 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017853ACN-2026-09-4000152318 | 2026-09-12 | 37.7538 | 424 | >20 | AUD-2026-09-2000017853 - ACN-2026-09-4000152318 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017853ACN-2026-09-4000152318 |  | AUD-2026-09-2000017853ACN-2026-09-4000152318 | 21 |  | 27 | 80 | 7 | 7 | 61
|  | CHANGMAI RAHUL | 2026-09-30 | HVLR and HCD facility are not applicable as depot storage is UG under 1000KL capacity. ESD are active and integrated to TAS | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127080 | Completed | CHANGMAI RAHUL | 2026-09-30 | HVLR - Not Available HCD - Not Available ESD found as non functional. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1708 | DIMAPUR DEPOT | Location to take up with vendor and get the ESD functional and its integration with TAS as well. | SOD | Marketing | GZR | 2026-04-30 |  | 10 |  | S2 | F5 | 2026-04-30 | AUD-2026-03-2000010729ACN-2026-03-4000127080 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127080 | 2026-09-12 | 37.7538 | 241 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127080 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127080 |  | AUD-2026-03-2000010729ACN-2026-03-4000127080 | 21 |  | 26 | 80 | 7 | 7 | 35
|  | CHANGMAI RAHUL | 2026-09-30 | RH and Tank details mentioned near the tank as suggested | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127081 | Completed | CHANGMAI RAHUL | 2026-09-30 | Physical dip taken for all 4 UG tanks on 11.03.26 and reco done | 3.7 | Inventory physical dip of minimum two tanks taken | 1708 | DIMAPUR DEPOT | RH and Tank details to be mentioned near the tank. | SOD | Marketing | GZR | 2026-03-30 |  | 5 |  | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127081 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127081 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127081 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127081 |  | AUD-2026-03-2000010729ACN-2026-03-4000127081 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-09-30 | TAS PC is up and records are signed | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127083 | Completed | CHANGMAI RAHUL | 2026-09-30 | NA as TT loading not yet started. TAS PC was found non- functional. | 3.13 | K-factor changes reviewed (if any) | 1708 | DIMAPUR DEPOT | To get the TAS PC up and review and sign the record | SOD | Marketing | GZR | 2026-04-15 |  | 5 |  | S1 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127083 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127083 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127083 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127083 |  | AUD-2026-03-2000010729ACN-2026-03-4000127083 | 21 |  | 26 | 80 | 7 | 7 | 33
|  | CHANGMAI RAHUL | 2026-09-30 | Housekeeping &PPE usages is improved | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127084 | Completed | CHANGMAI RAHUL | 2026-09-30 | Housekeeping &PPE usages needs to be more strengthened. | 3.15 | Housekeeping & PPE usage checked | 1708 | DIMAPUR DEPOT | Housekeeping &PPE usages needs to be more strengthened. | SOD | Marketing | GZR | 2026-03-30 | INADEQUATE SAFETY CULTURE | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127084 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127084 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127084 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127084 |  | AUD-2026-03-2000010729ACN-2026-03-4000127084 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-09-30 | Earthpit maintenance done • EP-22 – UG Tank Body • EP-23 – UG Tank Body • EP-24 – UG Tank Electrical • EP-27 – UG Tank Electrical EP-17 - Earth Pit was covered by vegetation is found and maintenance done. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127085 | Completed | CHANGMAI RAHUL | 2026-09-30 | As per thte earthpit report resistance of the following earthpit found outside limit and no corrective action taken as on date. •EP-22 – UG Tank Body • EP-23 – UG Tank Body • EP-24 – UG Tank Electrical • EP-27 – UG Tank Electrical EP-17 - Earth Pit was not found during inspection. It appears to be buried under debris. | 3.16 | Earth pits / boundary / vegetation control checked | 1708 | DIMAPUR DEPOT | Immediate corrective action to be taken | SOD | Marketing | GZR | 2026-04-15 | POOR EQUIPMENT MAINTENANCE | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127085 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127085 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127085 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127085 |  | AUD-2026-03-2000010729ACN-2026-03-4000127085 | 21 |  | 26 | 80 | 7 | 7 | 33
|  | CHANGMAI RAHUL | 2026-09-30 | All SSA points are complied except the Prohibited Area notifcation which has been already applied to Home Department (Police), Kohima. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127086 | Completed | CHANGMAI RAHUL | 2026-09-30 | SSA- 3 points are open as on date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1708 | DIMAPUR DEPOT | LIC to ensure close monitoring and SAP closure for SSA Observations. | SOD | Marketing | GZR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010729ACN-2026-03-4000127086 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127086 | 2026-09-12 | 37.7538 | 241 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127086 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127086 |  | AUD-2026-03-2000010729ACN-2026-03-4000127086 | 21 |  | 26 | 80 | 7 | 7 | 35
MEENA HEMANT KUMAR | 2026-09-30 |  |  | HVLR made functional | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153120 | Closed | MEENA HEMANT KUMAR | 2026-09-30 | 1. HVLR near TWPH is under repair. It was starting in auto mode without command. Vendor was on the job. Pls get it repaired. 2. ESD 14 checked and found okay 3. DVPI of Dyke 4 checked and found okay. Local hooter sounded along with indication at control room. 4. HVLR-2 checked and found okay. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1233 | BHARATPUR TERMINAL | HVLR near TWPH to be repaired | SOD | Marketing | NWF | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-09-2000017503ACN-2026-09-4000153120 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153120 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153120 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153120 | AUD-2026-09-2000017503ACN-2026-09-4000153120 | 21 | 21 | 27 | 80 | 2 | 1 | 57 | 57
MEENA HEMANT KUMAR | 2026-09-30 |  |  | C-bacs is currently functional | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153118 | Closed | MEENA HEMANT KUMAR | 2026-09-30 | Access contriol system (C-Bac system) in licence area gate is not functional. To be repaired. | 2.8 | Access control systems checked | 1233 | BHARATPUR TERMINAL | Access contriol system (C-Bac system) in licence area gate is not functional. To be repaired. | SOD | Marketing | NWF | 2026-10-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153118 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153118 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153118 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153118 | AUD-2026-09-2000017503ACN-2026-09-4000153118 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 57
|  | CHANGMAI RAHUL | 2026-09-30 | One FLP light installed near Tank Firm area and now the Lux level is meeting criteria UG Tank farm : Required 100 and observed 110 | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127077 | Completed | CHANGMAI RAHUL | 2026-09-30 | Lux level checked : TT gantry : Required : 60 and observed : 90-145 Secondary roads : Required 10 and observed 25 UG Tank farm: Required 100 and observed 15 to 45 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1708 | DIMAPUR DEPOT | It is advised to improve the lighting in UG Tank farm as per the requirement | SOD | Marketing | GZR | 2026-04-15 |  | 10 |  | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127077 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127077 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127077 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127077 |  | AUD-2026-03-2000010729ACN-2026-03-4000127077 | 21 |  | 26 | 80 | 7 | 7 | 33
|  | CHANGMAI RAHUL | 2026-09-30 | 1. Housekeeping in UG Tank farm improved 2. Many Project Surplus lying in the MCC room in an unorganised manner are shifted to scrapyard and store room 3. SOP adherence is ensured | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127087 | Completed | CHANGMAI RAHUL | 2026-09-30 | Full Field round completed and following are the observations : 1. Housekeeping in UG Tank farm to be improved 2. Many Project Surplus lying in the MCC room in an unorganised manner 3. SOP adherence to be ensured | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1708 | DIMAPUR DEPOT | Corrective action to be taken immediately | SOD | Marketing | GZR | 2026-04-07 |  | 5 |  | S1 | F5 | 2026-04-07 | AUD-2026-03-2000010729ACN-2026-03-4000127087 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127087 | 2026-09-12 | 37.7538 | 218 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127087 | 532 | 8294 | 21 | 8294 | 195 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127087 |  | AUD-2026-03-2000010729ACN-2026-03-4000127087 | 21 |  | 26 | 80 | 7 | 7 | 32
MEENA HEMANT KUMAR | 2026-09-30 |  |  | Contract workmen, security guards and TT crew have been advised to increase UA, Near Miss and unsafe condition. And reporting in past few days has been increased. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153130 | Closed | MEENA HEMANT KUMAR | 2026-09-30 | Done on 16th Sept with TT crew, contract workman and security guards. They were encouraged to suggest for UA, US and NM. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1233 | BHARATPUR TERMINAL | No. of UA, US and NM reported from Apr-Aug 2026 are 2, 20 and 2 respectively. It is very less and not acceptable. Suggestion box to be opened on monthly basis and give award to stakeholders for best suggestions. This should be recorded in regsiter/file with photograph. Contract labours, security guards, TT crew are to be motivated to report unsafe acts, unsafe situation and near misses through suggestion scheme. They should be rewarded suitably. | SOD | Marketing | NWF | 2026-10-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153130 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153130 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153130 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153130 | AUD-2026-09-2000017503ACN-2026-09-4000153130 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 57
DINESH KUMAR | 2026-09-30 |  |  | Checked and Found OK | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151906 | Closed | DINESH KUMAR | 2026-09-30 | Hoses & Earthing strips found old & torn. | 6.3 | Safety at Unloading Gantry | 1254 | JALANDHAR DEPOT | Continuity of Hose & Earthing strips to be rechecked. | SOD | Marketing | NFZ | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-15 | AUD-2026-09-2000017550ACN-2026-09-4000151906 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151906 | 2026-08-21 | 59.7538 | 394 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151906 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017550ACN-2026-09-4000151906 | AUD-2026-09-2000017550ACN-2026-09-4000151906 | 21 | 21 | 27 | 80 | 0 | -21 | 55 | 57
DINESH KUMAR | 2026-09-30 |  |  | Proposal sent for further action | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151905 | Closed | DINESH KUMAR | 2026-09-30 | PCB approval is pending due to VRU non-availability at the Location | 6.2 | Pending PCB approval | 1254 | JALANDHAR DEPOT | Proposal for VRU installation to be sent immediately for budget allocation. | SOD | Marketing | NFZ | 2026-09-07 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-07 | AUD-2026-09-2000017550ACN-2026-09-4000151905 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151905 | 2026-08-21 | 59.7538 | 394 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151905 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017550ACN-2026-09-4000151905 | AUD-2026-09-2000017550ACN-2026-09-4000151905 | 21 | 21 | 27 | 80 | 0 | -21 | 53 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Distribution of the work has been finalised with each officer categorically looking into the parameters and aim to improve the areaof focus | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150976 | Closed | FOUZDAR RISHABH | 2026-09-28 | Interaction done | 1.1 | Interaction with all officers (1–1.5 hrs) | 1155 | ROORKEE DEPOT | All officers (1+4+E0+contract engineer+GAT) available at depot to redistribute the work among themselves and to focus more on TT inspections, TT gaurdian, Novex,VTS and TAS issues | SOD | Marketing | NUZ | 2026-09-10 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-10 | AUD-2026-09-2000016863ACN-2026-09-4000150976 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150976 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150976 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150976 | AUD-2026-09-2000016863ACN-2026-09-4000150976 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Bay reallocation is being reduced with cordination with TAS officer and improvement in COLA and OLA. OLA - 95.98 % in Aug'26 and 96.82 % in Sept'26 | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150977 | Closed | FOUZDAR RISHABH | 2026-09-28 | AOP targets discussed. | 1.2 | Performance review conducted | 1155 | ROORKEE DEPOT | Bay reallocation numbers to be reduced, COLA OLA percentage to be improved as Good Number of trucks available at location | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150977 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150977 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150977 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150977 | AUD-2026-09-2000016863ACN-2026-09-4000150977 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | HVLR installation completed | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150979 | Closed | FOUZDAR RISHABH | 2026-09-28 | Last audit point - OISD & MDSA compliance pending. (Capital in nature, projects in progress.) | 1.4 | Earlier action points status checked | 1155 | ROORKEE DEPOT | To follow up with vendor for HVLR installation | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150979 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150979 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150979 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016863ACN-2026-09-4000150979 | AUD-2026-09-2000016863ACN-2026-09-4000150979 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Budget expenditure is being booked appropriately | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150980 | Closed | FOUZDAR RISHABH | 2026-09-28 |  | 1.5 | HQO / Zonal support required identified | 1155 | ROORKEE DEPOT | MEB budget | SOD | Marketing | NUZ | 2026-09-15 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-15 | AUD-2026-09-2000016863ACN-2026-09-4000150980 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150980 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150980 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150980 | AUD-2026-09-2000016863ACN-2026-09-4000150980 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Security has been instructed to conform all alerts with field and inform officer of its status. Same is being followed now | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150987 | Closed | FOUZDAR RISHABH | 2026-09-28 | HCD test carried out at TK-11 dyke for 20% hydrocarbon film. Indication and hooter automatically came at controll room. Alarm message received from Planning. No alert message received from security | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1155 | ROORKEE DEPOT | All alarms to be notified to all depot employees by security / planning office / control room. Presently, security is not notifyingthe alerts to all. | SOD | Marketing | NUZ | 2026-09-05 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-05 | AUD-2026-09-2000016863ACN-2026-09-4000150987 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150987 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150987 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150987 | AUD-2026-09-2000016863ACN-2026-09-4000150987 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | New TREM cards have been distributed and training on them have been provided as part of Daily safety talks | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150989 | Closed | FOUZDAR RISHABH | 2026-09-28 | Discussed at TT gantry with drivers. TREM card was availble with TT Driver UK08CA9734 but the driver was unable to correctly tell the numbers for different emergency services. | 2.15 | TT crew roadside emergency procedures checked | 1155 | ROORKEE DEPOT | Training of TREM card to be given to drivers | SOD | Marketing | NUZ | 2026-09-20 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-20 | AUD-2026-09-2000016863ACN-2026-09-4000150989 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150989 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150989 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150989 | AUD-2026-09-2000016863ACN-2026-09-4000150989 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | New TREM cards have been distributed and training on them have been provided as part of Daily safety talks | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150983 | Closed | FOUZDAR RISHABH | 2026-09-28 | Doc of TT UK17CA6545 AND UK08CA9734 were checked and it was found that necessary documents were available with the crew. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1155 | ROORKEE DEPOT | TREM card training to be given to drivers to be able to identify the points | SOD | Marketing | NUZ | 2026-09-20 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-20 | AUD-2026-09-2000016863ACN-2026-09-4000150983 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150983 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150983 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150983 | AUD-2026-09-2000016863ACN-2026-09-4000150983 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | All Officers have been trained to check CCTV footages | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150984 | Closed | FOUZDAR RISHABH | 2026-09-28 | Yes functioning. | 2.6 | CCTV functioning checked | 1155 | ROORKEE DEPOT | all new officers to be trained to check the 90 days back up | SOD | Marketing | NUZ | 2026-09-05 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-05 | AUD-2026-09-2000016863ACN-2026-09-4000150984 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150984 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150984 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150984 | AUD-2026-09-2000016863ACN-2026-09-4000150984 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | CBACs report is being taken daily. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150986 | Closed | FOUZDAR RISHABH | 2026-09-28 | Checked at security room and licence entry area | 2.8 | Access control systems checked | 1155 | ROORKEE DEPOT | cbacs working at both places. manpower numbers report t o be checked on daily basis | SOD | Marketing | NUZ | 2026-09-10 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-09-10 | AUD-2026-09-2000016863ACN-2026-09-4000150986 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150986 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150986 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016863ACN-2026-09-4000150986 | AUD-2026-09-2000016863ACN-2026-09-4000150986 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Control sheet for vehicles is being maintained by Officer for implementation and tracking | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150990 | Closed | FOUZDAR RISHABH | 2026-09-28 | TT UK08CA9734 was checked. The hole where locking rod gets inside the valve box was having larger dia than required as per locking rod. | 3.1 | TT fittings & discipline checked | 1155 | ROORKEE DEPOT | Location to check all the trucks considering valve box, EM locks and overall fittings. Excel to maintained and tracked. | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150990 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150990 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150990 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150990 | AUD-2026-09-2000016863ACN-2026-09-4000150990 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | 100% TFMS/SAP reco is maintained. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150992 | Closed | FOUZDAR RISHABH | 2026-09-28 | TFMS / SAP reconciliation being done regularly. | 3.10 | TFMS/SAP reconciliation checked | 1155 | ROORKEE DEPOT | 100% TFMS/SAP reco to be maintained. | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150992 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150992 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150992 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150992 | AUD-2026-09-2000016863ACN-2026-09-4000150992 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Difference of readings for BCU and MFM readings are matching | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150993 | Closed | FOUZDAR RISHABH | 2026-09-28 | BCU vs MFM data available at location. BCU and MFM readings are not matching. | 3.11 | MFM vs BCU totalizer comparison checked | 1155 | ROORKEE DEPOT | Location to ensure the BCU and MFM readings are matching (same). | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150993 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150993 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150993 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150993 | AUD-2026-09-2000016863ACN-2026-09-4000150993 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Security has been instructed to conform all alerts with field and inform officer of its status. Same is being followed now | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150994 | Closed | FOUZDAR RISHABH | 2026-09-28 | HCD alarm checked. Working fine. However, no message came from securty regarding the same. | 3.12 | Critical alarms checked & corrective actions reviewed | 1155 | ROORKEE DEPOT | Training to be imparted to security to notify regarding critical alarms in depot premises. | SOD | Marketing | NUZ | 2026-09-05 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-05 | AUD-2026-09-2000016863ACN-2026-09-4000150994 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150994 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150994 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150994 | AUD-2026-09-2000016863ACN-2026-09-4000150994 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Register for same is being maintained to ensure different reading for fire engine and DGs are maintained | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150995 | Closed | FOUZDAR RISHABH | 2026-09-28 | Local loading reports available at location. | 3.14 | Local loading checks (if applicable) | 1155 | ROORKEE DEPOT | checked and found recorded with reason such as filling for DG and fe | SOD | Marketing | NUZ | 2026-09-05 | LACK OF TRAINING OR COMPETENCY | 9 | PROCESS SAFETY | S3 | F3 | 2026-09-05 | AUD-2026-09-2000016863ACN-2026-09-4000150995 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150995 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150995 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016863ACN-2026-09-4000150995 | AUD-2026-09-2000016863ACN-2026-09-4000150995 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | All drains are cleaned and kept free from blocakages | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150996 | Closed | FOUZDAR RISHABH | 2026-09-28 | Housekeeping and PPE usage checked and found to be in good condition | 3.15 | Housekeeping & PPE usage checked | 1155 | ROORKEE DEPOT | Location to ensure drains are clean and free from any blockages | SOD | Marketing | NUZ | 2026-09-15 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S2 | F3 | 2026-09-15 | AUD-2026-09-2000016863ACN-2026-09-4000150996 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150996 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150996 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016863ACN-2026-09-4000150996 | AUD-2026-09-2000016863ACN-2026-09-4000150996 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Compliacne is underway. Closing as repeat with 1.2 | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150997 | Closed | FOUZDAR RISHABH | 2026-09-28 | Compliances are reviewed | 3.18 | OISD/MDSA/SSA compliance reviewed | 1155 | ROORKEE DEPOT | Location to comply the pending points in time bound manner. Also, the already complied points to be checked and verified. | SOD | Marketing | NUZ | 2026-12-30 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-12-30 | AUD-2026-09-2000016863ACN-2026-09-4000150997 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150997 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150997 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000016863ACN-2026-09-4000150997 | AUD-2026-09-2000016863ACN-2026-09-4000150997 | 21 | 21 | 27 | 80 | 2 | 2 | 70 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Trem card trainign has been given to drivers | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150998 | Closed | FOUZDAR RISHABH | 2026-09-28 | Interacted with UK08CA9734 and UK17CA6545. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1155 | ROORKEE DEPOT | found knowledgabale operated the Fire extinguisher well. emergency phone numbers details | SOD | Marketing | NUZ | 2026-09-20 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-09-20 | AUD-2026-09-2000016863ACN-2026-09-4000150998 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150998 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150998 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150998 | AUD-2026-09-2000016863ACN-2026-09-4000150998 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | VTS score pattern is being monitored by dedicated officer and is projected to improve the score from 83.77 in first week of Sept to85.77% for the rest of Sept. | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150991 | Closed | FOUZDAR RISHABH | 2026-09-28 | Novex and VTS portal reviewed | 3.3 | VTS deviations reviewed | 1155 | ROORKEE DEPOT | VTS score pattern and reasons for the low score to be evaluated | SOD | Marketing | NUZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016863ACN-2026-09-4000150991 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150991 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150991 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150991 | AUD-2026-09-2000016863ACN-2026-09-4000150991 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Local and remote status are being checked fortnightly | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150999 | Closed | FOUZDAR RISHABH | 2026-09-28 | Field inspection done at location at gantry, tank farm, pump hosue, control room, security cabon, admin, planning room. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1155 | ROORKEE DEPOT | Monitor, HCD, sprinklers and MEFG operated and checked all working fine. DBBV and ROSOV local and remote status to be checked | SOD | Marketing | NUZ | 2026-09-15 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-09-15 | AUD-2026-09-2000016863ACN-2026-09-4000150999 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000150999 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000150999 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000150999 | AUD-2026-09-2000016863ACN-2026-09-4000150999 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Local and remote status are being checked fortnightly | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151200 | Closed | FOUZDAR RISHABH | 2026-09-28 | Remote and Local status of ROSOV and DBBV | 6.1 | Remote and Local status of ROSOV and DBBV | 1155 | ROORKEE DEPOT | Remote and Local status of ROSOV and DBBV to be checked frequently by officer | SOD | Marketing | NUZ | 2026-09-15 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-15 | AUD-2026-09-2000016863ACN-2026-09-4000151200 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000151200 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000151200 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000151200 | AUD-2026-09-2000016863ACN-2026-09-4000151200 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | Silica Gel filled completely | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151201 | Closed | FOUZDAR RISHABH | 2026-09-28 | Silica gel of TK04 was not completely filled | 6.2 | Silica gel container on TK04 | 1155 | ROORKEE DEPOT | Silica gel of TK04 to be filled completely. | SOD | Marketing | NUZ | 2026-09-10 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-10 | AUD-2026-09-2000016863ACN-2026-09-4000151201 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000151201 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000151201 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000151201 | AUD-2026-09-2000016863ACN-2026-09-4000151201 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 57
MANOJ KUMAR | 2026-09-30 | FOUZDAR RISHABH | 2026-09-28 | All registers are being reviewed daily by HSSE officer | ZONAL HEAD INSPECTION Q2 26-27 | 2026-09-03 | AUD-2026-09-2000016863 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151202 | Closed | FOUZDAR RISHABH | 2026-09-28 | RTGP gate pass register not reviewed for month of Aug'26to be reviewed by HSSE officer. Fuel consumption register to be re-verified with theroteical consumption of Fire engine and DGs with its run time | 6.3 | Review of Registers | 1155 | ROORKEE DEPOT | All security register to be reviewed by HSSE officer and fuel consumption register | SOD | Marketing | NUZ | 2026-09-10 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-10 | AUD-2026-09-2000016863ACN-2026-09-4000151202 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016863ACN-2026-09-4000151202 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-09-2000016863 - ACN-2026-09-4000151202 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000016863ACN-2026-09-4000151202 | AUD-2026-09-2000016863ACN-2026-09-4000151202 | 21 | 21 | 27 | 80 | 2 | 2 | 54 | 57
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154493 | Open |  |  | Interacted with officers present on the day. All found active and involved | 1.1 | Interaction with all officers (1–1.5 hrs) | 1128 | MATHURA TERMINAL | New joined officers to be trained for terminal jobs | SOD | Marketing | NUZ | 2026-12-31 |  | 4 |  | S1 | F4 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154493 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154493 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154493 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000154493 |  | AUD-2026-09-2000017615ACN-2026-09-4000154493 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154494 | Open |  |  | Earlier action points were discussed with team | 1.4 | Earlier action points status checked | 1128 | MATHURA TERMINAL | To be complied in time bound manner. | SOD | Marketing | NUZ | 2026-12-31 |  | 4 |  | S1 | F4 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154494 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154494 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154494 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000154494 |  | AUD-2026-09-2000017615ACN-2026-09-4000154494 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154495 | Open |  |  | Major repair of tank TK4 & TK5 . 10inch Product pipeline required for surge line replacement. Revamping of gantry and TT parking. | 1.5 | HQO / Zonal support required identified | 1128 | MATHURA TERMINAL | Tank repair tenders to be floated immediately and next the revamp project details and budget to be proposed immediately | SOD | Marketing | NUZ | 2026-12-31 |  | 3 |  | S3 | F1 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154495 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154495 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154495 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000154495 |  | AUD-2026-09-2000017615ACN-2026-09-4000154495 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154496 | Open |  |  | Refer Annexure 1 | 1.8 | Improvement plans discussed | 1128 | MATHURA TERMINAL | As per discussion of CGM VC on pipeline interconnection with BPCL and IOCL to be submitted. And Revamp project to be submitted considering Bharatpur tankages. | SOD | Marketing | NUZ | 2026-12-31 |  | 4 |  | S1 | F4 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154496 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154496 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154496 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000154496 |  | AUD-2026-09-2000017615ACN-2026-09-4000154496 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154499 | Open |  |  | Yes | 2.7 | VA alerts checked / analysed | 1128 | MATHURA TERMINAL | Novex scores to be checked by TAS officer and same to be analysed. | SOD | Marketing | NUZ | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154499 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154499 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154499 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000154499 |  | AUD-2026-09-2000017615ACN-2026-09-4000154499 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155353 | Open |  |  | Yes | 3.18 | OISD/MDSA/SSA compliance reviewed | 1128 | MATHURA TERMINAL | Pending poitns to be complied in time bound manner. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155353 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155353 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155353 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155353 |  | AUD-2026-09-2000017615ACN-2026-09-4000155353 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155354 | Open |  |  | Yes | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1128 | MATHURA TERMINAL | All clamps to be identified and on regular basis these clamps to be replaced with the spool piece line. check for any leaks at the clamps regularly | SOD | Marketing | NUZ | 2026-12-31 |  | 15 |  | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000155354 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155354 | 2026-09-18 | 31.7538 | 486 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155354 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017615ACN-2026-09-4000155354 |  | AUD-2026-09-2000017615ACN-2026-09-4000155354 | 21 |  | 27 | 80 | 14 | 13 | 70
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155355 | Open |  |  | Yes, Sprinkler Job is going on. | 4.3 | Project progress reviewed | 1128 | MATHURA TERMINAL | Tank repair is the main project jobs to be taken up and complete as per the time lines with safety inside the terminal premises | SOD | Marketing | NUZ | 2027-12-31 |  | 6 |  | S3 | F2 | 2027-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000155355 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155355 | 2026-09-18 | 31.7538 | 851 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155355 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017615ACN-2026-09-4000155355 |  | AUD-2026-09-2000017615ACN-2026-09-4000155355 | 21 |  | 27 | 80 | 14 | 13 | 122
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155356 | Open |  |  | yes, working | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1128 | MATHURA TERMINAL | All scrap to be disposed off. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155356 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155356 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155356 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155356 |  | AUD-2026-09-2000017615ACN-2026-09-4000155356 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155357 | Open |  |  | Prover unloading is with hoses and is obstructing trucks movement | 6.1 |  | 1128 | MATHURA TERMINAL | permanent arrangement to be made | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155357 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155357 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155357 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155357 |  | AUD-2026-09-2000017615ACN-2026-09-4000155357 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155358 | Open |  |  | many places pedestals are corroded or broken clearance with ground is not meeting | 6.2 | NIL | 1128 | MATHURA TERMINAL | To place new pedestals with the in house scrap if possible so as clearance from ground is maintained. | SOD | Marketing | NUZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017615ACN-2026-09-4000155358 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155358 | 2026-09-18 | 31.7538 | 394 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155358 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155358 |  | AUD-2026-09-2000017615ACN-2026-09-4000155358 | 21 |  | 27 | 80 | 14 | 13 | 57
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155359 | Open |  |  | many places product pipelines also corroded at bottom , may develop leaks too | 6.3 | NIL | 1128 | MATHURA TERMINAL | Immediate steps such as paintaing . Replacing of portion of pipeline to be done to arrest any leaks. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155359 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155359 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155359 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155359 |  | AUD-2026-09-2000017615ACN-2026-09-4000155359 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155360 | Open |  |  | inside terminal many places found cross overs are corroded and not safe to walk on | 6.4 | NIL | 1128 | MATHURA TERMINAL | Hence pls arrange for the new cross overs or paint the cross overs immediately. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155360 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155360 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155360 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155360 |  | AUD-2026-09-2000017615ACN-2026-09-4000155360 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155362 | Open |  |  | Valve box drawing review, completion of checking of valve box fittings- status to be shared by 30th June with action plan. | 6.6 | NIL | 1128 | MATHURA TERMINAL | Valve box drawing review, completion of checking of valve box fittings- status to be shared by 30th June with action plan. | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155362 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155362 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155362 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155362 |  | AUD-2026-09-2000017615ACN-2026-09-4000155362 | 21 |  | 27 | 80 | 14 | 13 | 83
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155363 | Open |  |  | Letter to R S Bulk Carrier for not providing TT against 9615(18KL), process file note with compliance of previous file note | 6.7 | NIL | 1128 | MATHURA TERMINAL | Letter to R S Bulk Carrier for not providing TT against 9615(18KL), process file note with compliance of previous file note | SOD | Marketing | NUZ | 2027-03-31 |  | 4 |  | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155363 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155363 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155363 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155363 |  | AUD-2026-09-2000017615ACN-2026-09-4000155363 | 21 |  | 27 | 80 | 14 | 13 | 83
VASU ABHISHEK KUMAR | 2026-09-30 |  |  | Noted and updated. History cards to be maintained. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153137 | Closed | VASU ABHISHEK KUMAR | 2026-09-30 | History card was not found updated for costly equipment like CAMC of RSFPS, Fire engine, HVLR, Pumps, Tank etc. Location should update all visit details in History card. If any parts are replaced (even if cost is not borne by HPCL), pls mention that in history card. | 6.4 | History card | 1233 | BHARATPUR TERMINAL | Pls update all details including visit of OEM, any servicing done, any filter changed. Even if material changed is under the scope of CAMC vendor, pls write name of material changed and associated cost | SOD | Marketing | NWF | 2026-10-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153137 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153137 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153137 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153137 | AUD-2026-09-2000017503ACN-2026-09-4000153137 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 57
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154676 | Open |  |  | 2 no of IRRs are pending for clouser. Both of them are pending with internal audit team. | 1.3 | Pending issues reviewed | 1146 | MEERUT DEPOT | Location to take up with internal audit team for clouser of pending IRR at the earliest | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154676 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154676 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154676 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154676 |  | AUD-2026-09-2000017511ACN-2026-09-4000154676 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154677 | Open |  |  | Stock loss , opex, cycle time, project closure, solar generation, RFDs to be monitored. | 1.8 | Improvement plans discussed | 1146 | MEERUT DEPOT | Location to focus on stock loss issue , location is advise to witness all rakes at loading location. Till further advise from zonalteam. | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154677 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154677 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154677 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154677 |  | AUD-2026-09-2000017511ACN-2026-09-4000154677 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154678 | Open |  |  | Done ,Location shared ERDMP with HQO however board approval copy of ERDMP not available with location. Even though location following up with HSSE-HQO on regular basis. | 2.5 | Emergency response preparedness reviewed | 1146 | MEERUT DEPOT | The location shall take up the matter with HQO for obtaining Board approval of the ERDMP. | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154678 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154678 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154678 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154678 |  | AUD-2026-09-2000017511ACN-2026-09-4000154678 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154679 | Open |  |  | TT no: UP35BT6383 of Ethanol supply, checked at exit gae and found completely Empty. On surprise dip check at locking shed for TT no: UP11BT3479, UP81BT9260, and variation observed. | 3.2 | Post-loading dip checks verified | 1146 | MEERUT DEPOT | Location to advise carry out 100% dip check for loaded TT. | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154679 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154679 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154679 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154679 |  | AUD-2026-09-2000017511ACN-2026-09-4000154679 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154680 | Open |  |  | OISD : Total point 22, Pending point: 3, EDC: 31.12.2027 MDSA: Total point 41, Pending point: 4, EDC: 31.12.2027 SSA: Totalpoint 17, Pending point: 2, EDC: 31.03.2027 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1146 | MEERUT DEPOT | arrange to close all pending points | SOD | Marketing | NUZ | 2027-12-31 |  | 1 |  | S1 | F1 | 2027-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154680 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154680 | 2026-09-25 19:00 | 23.9622 | 851 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154680 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154680 |  | AUD-2026-09-2000017511ACN-2026-09-4000154680 | 21 |  | 27 | 80 | 0 | 0 | 122
[5 empty] | SENIOR MANAGEMENT INSPECTION-Q2, 26-27 | 2026-09-25 19:00 | AUD-2026-09-2000017511 | 2026-09-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154681 | Open |  |  | The entrance area of depot to be handled so as trucks reporting /emergency vehicle/fire tender can report to depot with out any issue. | 6.1 | Additional Observations | 1146 | MEERUT DEPOT | Corrective action to be taken. | SOD | Marketing | NUZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017511ACN-2026-09-4000154681 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017511ACN-2026-09-4000154681 | 2026-09-25 19:00 | 23.9622 | 486 | >20 | AUD-2026-09-2000017511 - ACN-2026-09-4000154681 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017511ACN-2026-09-4000154681 |  | AUD-2026-09-2000017511ACN-2026-09-4000154681 | 21 |  | 27 | 80 | 0 | 0 | 70
VASU ABHISHEK KUMAR | 2026-09-30 |  |  | Noted, CAT-A analysis being submitted to Zone. R3 monitoring started and to continue. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153131 | Closed | VASU ABHISHEK KUMAR | 2026-09-30 | CAT-A performance is not meeting target. 1st R3 and last R3 to be improved | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1233 | BHARATPUR TERMINAL | 1. Pls analyse reason of non execution of CAT-A indents and maintain it >95% in cming months. It is 82.5% in July 2026 and 84% in Aug 2026. 2. 1st R3 time and last R3 time were checked. Pls refer my email dt 17.09.2026. 1st R3 is beyond 09.10 hr in 41 days out of total 67 working days of July, Aug and Sept 2026. This needs to be improved. Performance is 39%. Similarly, last R3 is beyond 18.00 hrs in 13 days despite when TT loading is less. Location needs to maintain reason of delay in 1st R3 (1st TT is dispatched beyond09.10 hr) and last R3 (last TT is dispatched after 18.00 hr). | SOD | Marketing | NWF | 2026-10-31 | POOR COMMUNICATION | 15 | PROCESS SAFETY | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153131 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153131 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153131 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153131 | AUD-2026-09-2000017503ACN-2026-09-4000153131 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 57
VASU ABHISHEK KUMAR | 2026-09-30 |  |  | Already 3 locks sent for TPI. Location has completed checking of TT's and shared with zone. ITDG action as and when needed will be taken as per clauses. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153125 | Closed | VASU ABHISHEK KUMAR | 2026-09-30 | Location is checking EM lock through intelligent key. Some of the locks are blinking. Three locks have been sent to 3rd party for checking of any tampering. These 3 locks were identified as suspected in presence of vigilance officer. Location to keep on sending few locks for checking of these suspected locks by 3rd party. This will give message to defaulters and will reduce cases of tamperingof EM lock. Ation to be taken as per ITDG for tampering cases. Location is also requested to monitor VTS of these transporters whose locks have been sent to 3rd party. Letter to be issued for any deviation | 3.5 | EM Lock SOP compliance verified | 1233 | BHARATPUR TERMINAL | Location is checking EM lock through intelligent key. Some of the locks are blinking. Three locks have been sent to 3rd party for checking of any tampering. These 3 locks were identified as suspected in presence of vigilance officer. Location to keep on sending few locks for checking of these suspected locks by 3rd party. This will give message to defaulters and will reduce cases of tamperingof EM lock. Ation to be taken as per ITDG for tampering cases. Location is also requested to monitor VTS of these transporters whose locks have been sent to 3rd party. Letter to be issued for any deviation | SOD | Marketing | NWF | 2026-11-30 | OUTDATED OR COMPLEX SOPS | 15 | PROCESS SAFETY | S3 | F5 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153125 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153125 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153125 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153125 | AUD-2026-09-2000017503ACN-2026-09-4000153125 | 21 | 21 | 27 | 80 | 2 | 1 | 65 | 57
VASU ABHISHEK KUMAR | 2026-09-30 |  |  | Ethanol TT calibration verification done and report shared with zone. Prover testing being done. Gasohol TT loading temperature and invoice temperature data checked and shared with Zone. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153126 | Closed | VASU ABHISHEK KUMAR | 2026-09-30 | Auto vs manual reconciliation checked and found okay. However, there is loss of 0.412% in ethanol which is much higher than target (0%). There is loss of 26 kl in ethanol as on 31.08.2026. | 3.8 | Auto vs Manual reconciliation checked | 1233 | BHARATPUR TERMINAL | 1. Location is maintaining opening and closing dip reading of ethanol tank under receipt before and after ethanol TT unloading. However, location is not maintaining the gain loss TT wise. Ethanol receipt loss to be maintained. 2. Open dome cover of one TT on weekly basis and observations to be recorded in regsiter. 3. Calibrate few chambers of one ethanol Tt per month and observationsto be recorded. Fittings of ethanol TT is also required to be checked. 4. Ethanol flow meter to be checked by using mobile prover tank. Record to be maintained. 5. It was discussed that there is heat loss during blending of petrol with ethanol. This reduces the temp. of gasohol. The same is not recorded by MFM. It was info:med that MFM records gasohol temp at ratio of MS and ethanol line temp. Pls cross check the same for three TTs and share the actual result. Pls also check temp of gasohol in these three TTs usingcup thermometer (to ensure minimum delay in measurement of temp.) 6. It was informed during vigilance audit (conducted in last week of Aug 2026) that location is receiving ethanol at 5-10 deg higher temp than actual receipt temp. mentioned in register maintained by them. This is not acceptable. Location needs to follow SOP and refrain from any wrong practice. | SOD | Marketing | NWF | 2026-10-31 | OUTDATED OR COMPLEX SOPS | 15 | PROCESS SAFETY | S3 | F5 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153126 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153126 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153126 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153126 | AUD-2026-09-2000017503ACN-2026-09-4000153126 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 57
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154819 | Open |  |  | Nil Pending ESA Recommendations. Discussed regarding the open items. Regarding swapping of bonded and duty paid ATF tanks at location, it was informed by location that as New excise Commissioner has taken charge at Coimbatore range, Location is pursuing the matter with him and following up for issual of required Certificates. | 1.4 | Earlier action points status checked | 1856 | COIMBATORE DEPOT | Location to follow up for tank conversion from Excise department | SOD | Marketing | SZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154819 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154819 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154819 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154819 |  | AUD-2026-09-2000017811ACN-2026-09-4000154819 | 21 |  | 27 | 80 | 0 | 1 | 65
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154820 | Open |  |  | HQO support in GST consignment note issue. AHS assets to be reclassifed into assets to be taken up with HQO commercial. EM locks & keys shortage were discussed | 1.5 | HQO / Zonal support required identified | 1856 | COIMBATORE DEPOT | To be taken up with HQO for resolution of the issue. | SOD | Marketing | SZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154820 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154820 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154820 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154820 |  | AUD-2026-09-2000017811ACN-2026-09-4000154820 | 21 |  | 27 | 80 | 0 | 1 | 65
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154823 | Open |  |  | CCTV Infrastructure: Out of 53 total cameras, only 51 cameras fully operational and monitored daily by LIC and Safety Officer. | 2.6 | CCTV functioning checked | 1856 | COIMBATORE DEPOT | Location to take it up with CCTV vendor and make all cameras into operational. | SOD | Marketing | SZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154823 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154823 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154823 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154823 |  | AUD-2026-09-2000017811ACN-2026-09-4000154823 | 21 |  | 27 | 80 | 0 | 1 | 61
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154824 | Open |  |  | VA alerts checked- No alerts active. 35 out of 37 VA cameras are functional. | 2.7 | VA alerts checked / analysed | 1856 | COIMBATORE DEPOT | Location to follw up with VA vendor and ensure all cameras are functional in VA. | SOD | Marketing | SZ | 2026-10-31 |  | 2 |  | S1 | F2 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154824 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154824 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154824 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154824 |  | AUD-2026-09-2000017811ACN-2026-09-4000154824 | 21 |  | 27 | 80 | 0 | 1 | 61
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154825 | Open |  |  | Location has conducted eye check up camp on 11.11.2025 and Fit for road campaign for all the TT Crew and none found with color blindness. | 2.16 | Eyesight / colour-blindness awareness checked | 1856 | COIMBATORE DEPOT | Location to cover all TT crew in fit for road campaign and ensure proper recrods are maintained. | SOD | Marketing | SZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017811ACN-2026-09-4000154825 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154825 | 2026-08-28 17:00 | 52.0455 | 486 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154825 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154825 |  | AUD-2026-09-2000017811ACN-2026-09-4000154825 | 21 |  | 27 | 80 | 0 | 1 | 70
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154826 | Open |  |  | Two TTs(TN73AH4971 ,TN52D2649 dip verified and both found with in tolerance limit. Details being entered in SAP for 5% of the Tank trucks. | 3.2 | Post-loading dip checks verified | 1856 | COIMBATORE DEPOT | Location to get dip elimination file note approval at the earliest. | SOD | Marketing | SZ | 2026-11-30 |  | 2 |  | S1 | F2 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154826 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154826 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154826 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154826 |  | AUD-2026-09-2000017811ACN-2026-09-4000154826 | 21 |  | 27 | 80 | 0 | 1 | 65
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154827 | Open |  |  | Location is randomly selecting 5 TPT TTs & 2 DCT TTs daily for reviewing the entire route in the VTS system for any deviations andentering the same in VTS Monitoring portal. Deviations if any, is taken up on case-to-case basis with the Transporter/TT Crew, randomly after establishing valid reasons the TTs are allotted further loads. Any requirement of Route corrections are also promptly takenup with the concerned Sales Officer. Records for the same are being maintained. Also, Novex alerts generated are beingreviewed and actions are being taken. | 3.3 | VTS deviations reviewed | 1856 | COIMBATORE DEPOT | TT crew and Transporters to be counselled and TTs to be released only with proper justification. | SOD | Marketing | SZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154827 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154827 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154827 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154827 |  | AUD-2026-09-2000017811ACN-2026-09-4000154827 | 21 |  | 27 | 80 | 0 | 1 | 65
[5 empty] | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154831 | Open |  |  | Scrap seggregation is under progress in warehouse. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1856 | COIMBATORE DEPOT | Location to identify the assets and initiate immediate action for disposal in FY 26-27. | SOD | Marketing | SZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154831 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154831 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154831 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154831 |  | AUD-2026-09-2000017811ACN-2026-09-4000154831 | 21 |  | 27 | 80 | 0 | 1 | 65
VASU ABHISHEK KUMAR | 2026-09-30 |  |  | PLT Gain loss shared with Zone. Analysis being shred with zone. Any case of abnormal gain loss as advised in TT's will be shared with Zone. Cycle count completed monthly for September also. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153127 | Closed | VASU ABHISHEK KUMAR | 2026-09-30 | a. There were cases of abnormal loss/gain. Location is not maintaining PLT receipt loss gain report. It needs to be maintained batch wise and product wise. Pls note the MFM opening and closing readings as well as opening and closing dip/temp. readings of tank under receipt. Gain loss to be evaluated batch wise. b. Location should also carry out cycle count of material on monthly basis. c.For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informed to Zone. If there is shortage of more than 0.6% in any TT, location needs to take action inline with circular. | 3.9 | Abnormal variations / unused assets reviewed | 1233 | BHARATPUR TERMINAL | a. Location needs to maintain PLT loss gain report regularly and should share the report on monthly basis batch wise, product wise. b. Location should also carry out cycle count of material on monthly basis. c. For any loss/gain more than 5 KL in any product, location needs to inform zone with reason. If there is shortage of more than 200 litre in any ethanol TT, it needs to be informed toZone. If there is shortage of more than 6% in any TT, location needs to take action inline with circular. | SOD | Marketing | NWF | 2026-09-30 | OUTDATED OR COMPLEX SOPS | 15 | PROCESS SAFETY | S3 | F5 | 2026-09-30 | AUD-2026-09-2000017503ACN-2026-09-4000153127 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153127 | 2026-09-16 17:45 | 33.0143 | 394 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153127 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153127 | AUD-2026-09-2000017503ACN-2026-09-4000153127 | 21 | 21 | 27 | 80 | 2 | 1 | 57 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154835 | Open |  |  | Re-routing of Bitumen pipeline in view of re-routing required due to culvert work by Chennai Port Authority. | 1.3 | Pending issues reviewed | 1973 | CASSIMODE BLACK OIL TERMINAL | Location to coordinate with ChPA and ensure that tendering be done and ensure that PO is in place at our end for re-routing works. | SOD | Marketing | SZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017812ACN-2026-09-4000154835 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154835 | 2026-09-22 17:00 | 27.0455 | 486 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154835 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154835 |  | AUD-2026-09-2000017812ACN-2026-09-4000154835 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154836 | Open |  |  | CCTV Infrastructure: Out of 28 total cameras, 4nos of camera not working and monitored daily. Location is maintaining register for CCTV monitoring. | 2.6 | CCTV functioning checked | 1973 | CASSIMODE BLACK OIL TERMINAL | Four CCTV cameras were observed to be non-functional, resulting in gaps in surveillance coverage within the terminal area. | SOD | Marketing | SZ | 2026-10-30 |  | 2 |  | S1 | F2 | 2026-10-30 | AUD-2026-09-2000017812ACN-2026-09-4000154836 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154836 | 2026-09-22 17:00 | 27.0455 | 424 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154836 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154836 |  | AUD-2026-09-2000017812ACN-2026-09-4000154836 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154837 | Open |  |  | Location has 79 barrels of FO sludge collected from cleaning of TK2 4500kl which has to be disposed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1973 | CASSIMODE BLACK OIL TERMINAL | Scrap disposal process to be initiated and completed as per prescribed guidelines and safety measures. | SOD | Marketing | SZ | 2026-11-05 |  | 4 |  | S2 | F2 | 2026-11-05 | AUD-2026-09-2000017812ACN-2026-09-4000154837 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154837 | 2026-09-22 17:00 | 27.0455 | 430 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154837 | 532 | 8294 | 21 | 8294 | -16 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154837 |  | AUD-2026-09-2000017812ACN-2026-09-4000154837 | 21 |  | 27 | 80 | 0 | 0 | 62
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154838 | Open |  |  | Vegetation growth was observed in the tank farm area. Excessive vegetation may contribute to fire load and affect housekeeping and accessibility. | 6.1 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | Location to ensure that vegetation is pruned regularly. | SOD | Marketing | SZ | 2026-10-05 |  | 1 |  | S1 | F1 | 2026-10-05 | AUD-2026-09-2000017812ACN-2026-09-4000154838 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154838 | 2026-09-22 17:00 | 27.0455 | 399 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154838 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154838 |  | AUD-2026-09-2000017812ACN-2026-09-4000154838 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154839 | Open |  |  | During routine testing, water from the eye washer shower was observed not draining properly, leading to water accumulation in the bowl/ basin. | 6.2 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To repair | SOD | Marketing | SZ | 2026-10-05 |  | 1 |  | S1 | F1 | 2026-10-05 | AUD-2026-09-2000017812ACN-2026-09-4000154839 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154839 | 2026-09-22 17:00 | 27.0455 | 399 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154839 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154839 |  | AUD-2026-09-2000017812ACN-2026-09-4000154839 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154840 | Open |  |  | Housekeeping in the Electrical Room was observed to be inadequate. | 6.3 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | Location to ensure cleanliness. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154840 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154840 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154840 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154840 |  | AUD-2026-09-2000017812ACN-2026-09-4000154840 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154841 | Open |  |  | The Driver Rest Room was observed to require painting, indicating the need for improvement in the condition and appearance of the facility. | 6.5 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To rectify | SOD | Marketing | SZ | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017812ACN-2026-09-4000154841 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154841 | 2026-09-22 17:00 | 27.0455 | 409 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154841 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154841 |  | AUD-2026-09-2000017812ACN-2026-09-4000154841 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154842 | Open |  |  | Solar panels removed from above the Admin Building were observed to be kept at the existing location and have not yet been shifted to the designated/concerned location. | 6.6 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To be shifted to designated location. Balance solar panel to be shifted to Hassan Terminal as per plan. | SOD | Marketing | SZ | 2026-10-10 |  | 1 |  | S1 | F1 | 2026-10-10 | AUD-2026-09-2000017812ACN-2026-09-4000154842 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154842 | 2026-09-22 17:00 | 27.0455 | 404 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154842 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154842 |  | AUD-2026-09-2000017812ACN-2026-09-4000154842 | 21 |  | 27 | 80 | 0 | 0 | 58
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154843 | Open |  |  | A vehicle movement route map for the terminal has not been prepared/displayed. Clear identification of designated vehicle routes isrequired for safe movement within the terminal. | 6.7 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To attend on priority | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154843 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154843 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154843 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154843 |  | AUD-2026-09-2000017812ACN-2026-09-4000154843 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154844 | Open |  |  | A dispenser unit was observed to be kept in the parking area, which may obstruct vehicle movement and create an unsafe condition. | 6.8 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To maintain clear path | SOD | Marketing | SZ | 2026-10-15 |  | 1 |  | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017812ACN-2026-09-4000154844 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154844 | 2026-09-22 17:00 | 27.0455 | 409 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154844 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154844 |  | AUD-2026-09-2000017812ACN-2026-09-4000154844 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154845 | Open |  |  | During inspection, it was observed that the CCTV camera view outside the Main Gate was obstructed by overgrown tree branches. | 6.10 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To prune the tree branch for clear camera view. | SOD | Marketing | SZ | [6 empty] | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154845 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154845 | 2026-09-22 17:00 | 27.0455 |  |  | AUD-2026-09-2000017812 - ACN-2026-09-4000154845 | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 |  | AUD-2026-09-2000017812ACN-2026-09-4000154845 |  | AUD-2026-09-2000017812ACN-2026-09-4000154845 |  |  | 27 | 80 | 0 | 0
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154846 | Open |  |  | Oil spillage was observed in the TT Gantry Pump House area. The presence of spilled oil can create slip hazards, increase the risk of fire, and indicate potential leakage from equipment or pipelines. | 6.11 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To maintain meticulous housekeeping. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154846 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154846 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154846 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154846 |  | AUD-2026-09-2000017812ACN-2026-09-4000154846 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154847 | Open |  |  | The safety harness provided at the TT Loading Gantry was found to be in an unhygienic and deteriorated condition. | 6.12 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To replace | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154847 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154847 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154847 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154847 |  | AUD-2026-09-2000017812ACN-2026-09-4000154847 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154848 | Open |  |  | The nomenclature/identification board for the Fire Water Engine was found missing. Absence of proper equipment identification may lead to confusion during operation, inspection, maintenance, and emergency response activities. | 6.13 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To ensure it is painted and is clearly visible. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154848 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154848 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154848 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154848 |  | AUD-2026-09-2000017812ACN-2026-09-4000154848 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | CASSIMODE_Q2_FY26_SR.MGMT INSPECTION | 2026-09-22 17:00 | AUD-2026-09-2000017812 | 2026-09-22 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154849 | Open |  |  | The wind sock was observed to be damaged condition and requires replacement. | 6.14 |  | 1973 | CASSIMODE BLACK OIL TERMINAL | To replace at the earliest. | SOD | Marketing | SZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-09-2000017812ACN-2026-09-4000154849 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017812ACN-2026-09-4000154849 | 2026-09-22 17:00 | 27.0455 | 394 | >20 | AUD-2026-09-2000017812 - ACN-2026-09-4000154849 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017812ACN-2026-09-4000154849 |  | AUD-2026-09-2000017812ACN-2026-09-4000154849 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Officers were motivated for delivering their best to Corporation and New Officers were advised to learn from Seniors at workplace. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125535 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Officers were advised that execptional perfromance is expected out the team. | 1.6 | Expectations clearly communicated to officers | 1991 | CHENNAI TERMINAL | Officers were emphasized for high compliance standards and fostering a culture of proactive learning among the new officers. | SOD | Marketing | SZ | 2026-03-31 |  | 4 |  | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125535 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125535 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125535 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125535 |  | AUD-2026-03-2000010826ACN-2026-03-4000125535 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | New Officers and JEOs were advised to ensure to go through SOD SOPs and ensure compliance to the same. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125536 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Location is found following circulars and maintaining records in CCTV monitoring, VTS monitoring, TT checks, Ethanol blending Etc. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1991 | CHENNAI TERMINAL | Newly joined junior officers were motivated and advised to focusing on career progression pathways and alignment with the latest HQO/Zonal circulars. | SOD | Marketing | SZ | 2026-03-31 |  | 4 |  | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125536 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125536 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125536 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125536 |  | AUD-2026-03-2000010826ACN-2026-03-4000125536 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | CCTV to be rectified and made 100% Operations | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125537 | Completed | G RAMADOSS | 2026-03-22 | CCTV Infrastructure: Out of 52 total cameras, 45 units are fully operational and monitored daily. Totally there are 82 Cameras and 6 units are currently offline. Out of the 6 CCTVs 2 poles were corroded completely and the same have been replaced. Vendor visit is pending along with mapping of these CCTVs in Video Analytics | 2.6 | CCTV functioning checked | 1991 | CHENNAI TERMINAL | Location to put back the non functional cameras into operation in coordination with Vendors as early as possible. | SOD | Marketing | SZ | 2026-03-31 |  | 6 |  | S2 | F3 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125537 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125537 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125537 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125537 |  | AUD-2026-03-2000010826ACN-2026-03-4000125537 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Non functional cameras in VA have been rectified | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125538 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | VA alerts checked- No alerts active. 45 out of 52 VA cameras are functional. | 2.7 | VA alerts checked / analysed | 1991 | CHENNAI TERMINAL | Location to follow up with vendor for functioning of all VA enabled cameras in working condition. | SOD | Marketing | SZ | 2026-03-31 |  | 6 |  | S2 | F3 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125538 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125538 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125538 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125538 |  | AUD-2026-03-2000010826ACN-2026-03-4000125538 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Location is taking steps to speed up grass cutting and will complete by mid April. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125540 | Completed | G RAMADOSS | 2026-03-22 | Satisfactory housekeeping standards are maintained, and all personnel were observed utilizing proper PPE. | 3.15 | Housekeeping & PPE usage checked | 1991 | CHENNAI TERMINAL | Location to cut the dry grass across premises and ensure that the same is disposed off immediately | SOD | Marketing | SZ | 2026-03-31 |  | 4 |  | S2 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125540 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125540 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125540 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125540 |  | AUD-2026-03-2000010826ACN-2026-03-4000125540 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Status of all the Audits have been updated and action plan has been given till May for closure of all points | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125541 | Completed | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | All OISD points are complied. Pending MDSA/SSA points are complied as target dates except for the points which require to be carried out under Terminal revamp project | 3.18 | OISD/MDSA/SSA compliance reviewed | 1991 | CHENNAI TERMINAL | Location to expedite the closure of Pending MDSA/SSA point of Tank inspection. | SOD | Marketing | SZ | 2026-03-31 |  | 6 |  | S3 | F2 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125541 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125541 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125541 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125541 |  | AUD-2026-03-2000010826ACN-2026-03-4000125541 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Both the suspected 2 Nos EM Locks have been sent to M/s Sterna Coimbatore for further investigation. Based on Sterna report, actionwill be taken in line with ITDG | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125539 | Completed | G RAMADOSS | 2026-03-22 | 100 % TTs for delivered supplies are being sent with EM locks and compliance to the circular SOD/EM Lock dtd 22.12.2022 is being ensured. EM locking Checked with Intelligent Key: a) TT No. TN03AA3746 - EM Lock No.s HE15541, HE15542 with Intelligent Key and checked b) TT No. TN50AP2016 - EM Lock Nos. HE22626, HE29996 with Intelligent Key. Both were found un-tampered. c) TT no. TN88D8319- EM Lock no. HE33111 and HE 33112 when checked with intelligent key. During checking, light was unsteady and blinking thus concluding the possibility of Lock having Abused or Malfunctioning. | 3.5 | EM Lock SOP compliance verified | 1991 | CHENNAI TERMINAL | For TT no. TN88D8319, Location to immediately raise a Panchnama and send the locks to M/s. Sterna for further investigations. Upon feedback received from vendor, location to take action as per ITDG guidleines. | SOD | Marketing | SZ | 2026-03-31 |  | 3 |  | S1 | F3 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125539 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125539 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125539 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125539 |  | AUD-2026-03-2000010826ACN-2026-03-4000125539 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Revamp is under Board Approval, once this is done the Tank Repair shall be done. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125542 | Completed | G RAMADOSS | 2026-03-22 | Field visit was undertaken covering all the areas of gantry/tank farm/jetty/pump house/siding/control room/security/admin. Housekeeping and grass cutting are not upto the mark and needs to improve. TK nos. 2,5,7,9,12,19,20 is under outage for Repair. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1991 | CHENNAI TERMINAL | Location needs to focus on improving housekeeping and grasscutting by making the available resources to give more output on daily basis with effective supervision. | SOD | Marketing | SZ | 2026-03-31 |  | 12 |  | S3 | F4 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125542 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125542 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125542 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010826ACN-2026-03-4000125542 |  | AUD-2026-03-2000010826ACN-2026-03-4000125542 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | 1)Once approval is done, funds shall be surrendered 2)Fire Extinguishers project shall be closed in this month. 3) Replacement offire hydrant network , pipelines have been ordered,EDD is 16.03.26. | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125543 | Completed | G RAMADOSS | 2026-03-22 | 1.) 3 Tank Upgradation - Fund transfer request under Approval. ETC: 20.03.2026 2.) Fire Extinguser: awaiting for the replacement of Fire extinguiser. 3.)CCTV Replacement at Chennai New Terminal - VA Commissioning Under progress ETC 31.03.2026 4.) Replacement of Fire Network: RO 5400372863 placed for procurement of Materials. Expected Delivery date of Material at site 16.03.2026 | 4.3 | Project progress reviewed | 1991 | CHENNAI TERMINAL | To complete the projects on time and ensure close out with nil time overruns. | SOD | Marketing | SZ | 2026-03-31 |  | 2 |  | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125543 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125543 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125543 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125543 |  | AUD-2026-03-2000010826ACN-2026-03-4000125543 | 21 |  | 26 | 80 | 42 | 42 | 31
|  | MAYEE VIKRAM PRADYUMNA | 2026-09-30 | Awaiting Delivery Order from MSTC | UPLOADING OF CNT VISIT REPORT IN SAP | 2026-03-10 18:00 | AUD-2026-03-2000010826 | 2026-03-10 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125544 | Completed | G RAMADOSS | 2026-03-22 | Location Already disposed Scrap Worth of 5.3Lakhs also planned to dispose the remaining scrap worth of 4.55 Lakhs before March 31 waiting for Delivery note from MSTC. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1991 | CHENNAI TERMINAL | Location to be made scrap free by 31.03.26 | SOD | Marketing | SZ | 2026-03-31 |  | 1 |  | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010826ACN-2026-03-4000125544 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010826ACN-2026-03-4000125544 | 2026-06-27 | 114.7538 | 211 | >20 | AUD-2026-03-2000010826 - ACN-2026-03-4000125544 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010826ACN-2026-03-4000125544 |  | AUD-2026-03-2000010826ACN-2026-03-4000125544 | 21 |  | 26 | 80 | 42 | 42 | 31
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155079 | Open |  |  | Interacted with both officers of the location and discussed importance of safety in operations. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1265 | LEH DEPOT | New officer to be trained more on safety & operations. | SOD | Marketing | NFZ | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-10-2000017660ACN-2026-10-4000155079 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155079 | 2026-10-07 09:00 | 12.3788 | 486 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155079 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155079 |  | AUD-2026-10-2000017660ACN-2026-10-4000155079 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155080 | Open |  |  | Yes PPE are used by location. Housekeeping of the location not found satisfactory at Pump House, near Sample Room & Admin Building. | 3.15 | Housekeeping & PPE usage checked | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-10-2000017660ACN-2026-10-4000155080 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155080 | 2026-10-07 09:00 | 12.3788 | 425 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155080 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155080 |  | AUD-2026-10-2000017660ACN-2026-10-4000155080 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155081 | Open |  |  | No unwanted vegetation is seen in depot. Earth pits test date not changed in the display. | 3.16 | Earth pits / boundary / vegetation control checked | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-10-10 |  | 8 |  | S2 | F4 | 2026-10-10 | AUD-2026-10-2000017660ACN-2026-10-4000155081 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155081 | 2026-10-07 09:00 | 12.3788 | 404 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155081 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155081 |  | AUD-2026-10-2000017660ACN-2026-10-4000155081 | 21 |  | 27 | 80 | 0 | 0 | 58