[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155082 | Open |  |  | OISD compliances reviewed.Location is advised to complete the points at the earliest. All necessary support shall be extended by Zone. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-12-31 |  | 12 |  | S3 | F4 | 2026-12-31 | AUD-2026-10-2000017660ACN-2026-10-4000155082 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155082 | 2026-10-07 09:00 | 12.3788 | 486 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155082 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155082 |  | AUD-2026-10-2000017660ACN-2026-10-4000155082 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155083 | Open |  |  | Location to segregate scrap material from surplus & expedite disposal of old transformer, DG & other miscellaneous scrap. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-11-30 |  | 12 |  | S3 | F4 | 2026-11-30 | AUD-2026-10-2000017660ACN-2026-10-4000155083 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155083 | 2026-10-07 09:00 | 12.3788 | 455 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155083 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155083 |  | AUD-2026-10-2000017660ACN-2026-10-4000155083 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000155084 | Open |  |  | Found in damaged & bad condition from several places. Needs repair & rearrangement. | 6.1 | Admin Building | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-10-2000017660ACN-2026-10-4000155084 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155084 | 2026-10-07 09:00 | 12.3788 | 486 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155084 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155084 |  | AUD-2026-10-2000017660ACN-2026-10-4000155084 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | LOCATION VISIT-LEH_16-18.09.26 | 2026-09-18 11:15 | AUD-2026-10-2000017660 | 2026-09-16 16:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000155085 | Open |  |  | Alternative mode of communication to be ensured at Security all the times. | 6.2 | Communication | 1265 | LEH DEPOT | Corrective action to be taken by Location. | SOD | Marketing | NFZ | 2026-10-15 |  | 8 |  | S2 | F4 | 2026-10-15 | AUD-2026-10-2000017660ACN-2026-10-4000155085 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017660ACN-2026-10-4000155085 | 2026-10-07 09:00 | 12.3788 | 409 | >20 | AUD-2026-10-2000017660 - ACN-2026-10-4000155085 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017660ACN-2026-10-4000155085 |  | AUD-2026-10-2000017660ACN-2026-10-4000155085 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154540 | Open |  |  | Tank 102 commissioning is pending | 1.3 | Pending issues reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Tank 102 commissioning to be completed. | SOD | Marketing | SCR | 2026-10-15 |  | 5 |  | S1 | F5 | 2026-10-15 | AUD-2026-10-2000017705ACN-2026-10-4000154540 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154540 | 2026-09-17 20:00 | 31.9205 | 409 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154540 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017705ACN-2026-10-4000154540 |  | AUD-2026-10-2000017705ACN-2026-10-4000154540 | 21 |  | 27 | 80 | 3 | 2 | 59
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154541 | Open |  |  | Complied 11/13 and 19/22 action points of previous Senior Management Inspection observations. | 1.4 | Earlier action points status checked | 1992 | VISAKH WHITE OIL TERMINAL | Pending audit observations to be complied as per the given target dates | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-10-2000017705ACN-2026-10-4000154541 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154541 | 2026-09-17 20:00 | 31.9205 | 425 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154541 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017705ACN-2026-10-4000154541 |  | AUD-2026-10-2000017705ACN-2026-10-4000154541 | 21 |  | 27 | 80 | 3 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154542 | Open |  |  | Action to be taken on shifting of Lube inventory lying in the VNWOT to Guntur Warehouse. | 1.8 | Improvement plans discussed | 1992 | VISAKH WHITE OIL TERMINAL | Shifting of Lube inventory to Guntur Warehouse to be expedited | SOD | Marketing | SCR | 2026-11-30 |  | 5 |  | S1 | F5 | 2026-11-30 | AUD-2026-10-2000017705ACN-2026-10-4000154542 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154542 | 2026-09-17 20:00 | 31.9205 | 455 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154542 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017705ACN-2026-10-4000154542 |  | AUD-2026-10-2000017705ACN-2026-10-4000154542 | 21 |  | 27 | 80 | 3 | 2 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154544 | Open |  |  | Lux levels checked. Lux level at TT Gantry 86 , Tank 104 manifold -156, ROSOV 62,TWG -220 , PPH-75, Road opposite PPH-13.0, MCC Room -116 , Security cabin - 310, Control room - 410, Minor road behind MCC room - 2 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1992 | VISAKH WHITE OIL TERMINAL | Location to take action for improvement of Lux levels on minor roads not meeting the lux level requirements | SOD | Marketing | SCR | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-10-2000017705ACN-2026-10-4000154544 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154544 | 2026-09-17 20:00 | 31.9205 | 455 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154544 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000154544 |  | AUD-2026-10-2000017705ACN-2026-10-4000154544 | 21 |  | 27 | 80 | 3 | 2 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154546 | Open |  |  | All 86 cameras are working, however camera no 173 TWG End more coverage of area to be ensured | 2.6 | CCTV functioning checked | 1992 | VISAKH WHITE OIL TERMINAL | Corrective action to be taken for CCTV nos mentioned in observation. | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017705ACN-2026-10-4000154546 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154546 | 2026-09-17 20:00 | 31.9205 | 394 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154546 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000154546 |  | AUD-2026-10-2000017705ACN-2026-10-4000154546 | 21 |  | 27 | 80 | 3 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154548 | Open |  |  | Post Loading dip checks verified for TTs i) AP31TG8959 Compartment 1 +3mm, 2 +4mm, 3 +5mm , 4 +3mm(BCU over run -compartment 3 - 5005, 4 - 5004) ii) Bay 13 - TT no AP31 TE 1139 Compartment 1 +5mm, 2 +4mm, 3 +2mm , 4 +2mm iii) Bay 10 - AP39 UG 5329 Compartment 1 +4mm, 2 +1,2cm, 3 +1.5cm , | 3.2 | Post-loading dip checks verified | 1992 | VISAKH WHITE OIL TERMINAL | To take up with TAS vendor and Corrective action to be expedited wherever variations beyond permitted limit is observed | SOD | Marketing | SCR | 2026-10-30 |  | 8 |  | S2 | F4 | 2026-10-30 | AUD-2026-10-2000017705ACN-2026-10-4000154548 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154548 | 2026-09-17 20:00 | 31.9205 | 424 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154548 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000154548 |  | AUD-2026-10-2000017705ACN-2026-10-4000154548 | 21 |  | 27 | 80 | 3 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155500 | Open |  |  | Critical alarms were reviewed. | 3.12 | Critical alarms checked & corrective actions reviewed | 1992 | VISAKH WHITE OIL TERMINAL | All critical alarms to be checked , root cause to be analysed , recorded before closing the alerts. | SOD | Marketing | SCR | 2026-10-30 |  | 8 |  | S2 | F4 | 2026-10-30 | AUD-2026-10-2000017705ACN-2026-10-4000155500 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000155500 | 2026-09-17 20:00 | 31.9205 | 424 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000155500 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000155500 |  | AUD-2026-10-2000017705ACN-2026-10-4000155500 | 21 |  | 27 | 80 | 3 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155501 | Open |  |  | Compliance status reviewed : OISD 47/47, MDSA - 100/116, SSA - 40/43 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Pending audit observations to be complied as per the given target dates | SOD | Marketing | SCR | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-10-2000017705ACN-2026-10-4000155501 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000155501 | 2026-09-17 20:00 | 31.9205 | 455 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000155501 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000155501 |  | AUD-2026-10-2000017705ACN-2026-10-4000155501 | 21 |  | 27 | 80 | 3 | 2 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-10-4000155502 | Open |  |  | Fire Engine Sequence checked - S2, E, C, B, A. Observed that RPM in Digital display was reflecting 1450 RPM for FE B against 1500 RPM on the FE Panel. All FEs LLOP logic to be rechecked and ensure non stoppage of FE with LLOP. Water leakage observed for FE A | 4.2 | Maintenance activities reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Location to take necessary rectification job. | SOD | Marketing | SCR | 2026-10-30 |  | 8 |  | S2 | F4 | 2026-10-30 | AUD-2026-10-2000017705ACN-2026-10-4000155502 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000155502 | 2026-09-17 20:00 | 31.9205 | 424 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000155502 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000155502 |  | AUD-2026-10-2000017705ACN-2026-10-4000155502 | 21 |  | 27 | 80 | 3 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-10-4000155503 | Open |  |  | Marine Loading arm project PO time extension pending | 4.3 | Project progress reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Location to initiate E-File Note for PO Time extension | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017705ACN-2026-10-4000155503 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000155503 | 2026-09-17 20:00 | 31.9205 | 394 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000155503 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017705ACN-2026-10-4000155503 |  | AUD-2026-10-2000017705ACN-2026-10-4000155503 | 21 |  | 27 | 80 | 3 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | INFRASTRUCTURE, PROJECT & M&I ASSESSMENT | ACN-2026-10-4000155504 | Open |  |  | Cut pieces of plates , pipes, old DCP FEs lying in scrap yard | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1992 | VISAKH WHITE OIL TERMINAL | Scrap to be liquidated. RFDs to be initiated on priority | SOD | Marketing | SCR | 2026-12-31 |  | 5 |  | S1 | F5 | 2026-12-31 | AUD-2026-10-2000017705ACN-2026-10-4000155504 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000155504 | 2026-09-17 20:00 | 31.9205 | 486 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000155504 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017705ACN-2026-10-4000155504 |  | AUD-2026-10-2000017705ACN-2026-10-4000155504 | 21 |  | 27 | 80 | 3 | 2 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-16 16:00 | AUD-2026-10-2000017706 | 2026-09-16 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155505 | Open |  |  | Pending Issues reviewed . PESO Initial approval received for conversion of Class A tanks to Class C Tanks. Application to be submitted for final approval | 1.3 | Pending issues reviewed | 3693 | KAKINADA TML | Application to be submitted to PESO Nagpur for final approval | SOD | Marketing | SCR | 2026-10-15 |  | 5 |  | S1 | F5 | 2026-10-15 | AUD-2026-10-2000017706ACN-2026-10-4000155505 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017706ACN-2026-10-4000155505 | 2026-09-16 16:00 | 33.0872 | 409 | >20 | AUD-2026-10-2000017706 - ACN-2026-10-4000155505 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017706ACN-2026-10-4000155505 |  | AUD-2026-10-2000017706ACN-2026-10-4000155505 | 21 |  | 27 | 80 | 0 | 0 | 59
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-16 16:00 | AUD-2026-10-2000017706 | 2026-09-16 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155506 | Open |  |  | Pressure guages calibration is due. | 4.2 | Maintenance activities reviewed | 3693 | KAKINADA TML | Pressure guages calibration to be carried out | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017706ACN-2026-10-4000155506 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017706ACN-2026-10-4000155506 | 2026-09-16 16:00 | 33.0872 | 394 | >20 | AUD-2026-10-2000017706 - ACN-2026-10-4000155506 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017706ACN-2026-10-4000155506 |  | AUD-2026-10-2000017706ACN-2026-10-4000155506 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-16 16:00 | AUD-2026-10-2000017706 | 2026-09-16 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155507 | Open |  |  | Lux levels AR to be closed in time | 4.3 | Project progress reviewed | 3693 | KAKINADA TML | Lux levels AR to be closed in time | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017706ACN-2026-10-4000155507 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017706ACN-2026-10-4000155507 | 2026-09-16 16:00 | 33.0872 | 394 | >20 | AUD-2026-10-2000017706 - ACN-2026-10-4000155507 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017706ACN-2026-10-4000155507 |  | AUD-2026-10-2000017706ACN-2026-10-4000155507 | 21 |  | 27 | 80 | 0 | 0 | 57
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155508 | Open |  |  | The compliance status of pending audit recommendations, Critical issues concerning KSEB, Railways, Assets held for sale, maintenance issues were discussed for expediting the compliance at the earliest possible time. | 1.3 | Pending issues reviewed | 1892 | KOZHIKODE DEPOT | Comply all audit recommendations in a time bound manner. 1. KSEB arrears issue is to be taken up with SZ Legal 2. MS tank UG pump repairs are to be handled urgently. AMC for AMC of pumps is to be worked out. Advise to review and take action for AMC of all critical equipments viz. Pumps, VFDs | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-10-2000017709ACN-2026-10-4000155508 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155508 | 2026-09-17 16:00 | 32.0872 | 486 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155508 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155508 |  | AUD-2026-10-2000017709ACN-2026-10-4000155508 | 21 |  | 27 | 80 | 2 | -4 | 70
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155509 | Open |  |  | Earlier action points and advised to take action on the pending points such as 1. Field observations in E dairy portal as per KPIfor the year 2. Dip elimination file note renewal as per HQO circular 3. Unwanted and scrap items are to be stored at one place. Take action for timely disposal, from depo premises and rly siding area as wel 4. Take up with PESO for night operations 5. UG pump repairs are to be handled urgently. AMC for all critical equipments are to be worked out | 1.4 | Earlier action points status checked | 1892 | KOZHIKODE DEPOT | Location to take action on pending points of Q1 | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-10-2000017709ACN-2026-10-4000155509 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155509 | 2026-09-17 16:00 | 32.0872 | 486 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155509 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155509 |  | AUD-2026-10-2000017709ACN-2026-10-4000155509 | 21 |  | 27 | 80 | 2 | -4 | 70
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155510 | Open |  |  | Budget required for attending Earth pit repair / revamp works, painting works as recommended in Technical Audit. | 1.5 | HQO / Zonal support required identified | 1892 | KOZHIKODE DEPOT | Location to float tender and provide estimate for one time maintenance works | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-10-2000017709ACN-2026-10-4000155510 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155510 | 2026-09-17 16:00 | 32.0872 | 486 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155510 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155510 |  | AUD-2026-10-2000017709ACN-2026-10-4000155510 | 21 |  | 27 | 80 | 2 | -4 | 70
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155511 | Open |  |  | Compliances reviewed and complied. 1. Location to take action on Open Q1 observation points 2. Submit Monthly Highlights on timew.r.t key AOP targets within the timelines | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1892 | KOZHIKODE DEPOT | 1. Railway siding maintenance - Develop mechanism for periodic joint inspection of the siding facilities involving Railway authorities and carry out the maintenance works for all identified issues. 2. Water bottom to be avoided in all storage tanks as recommended in Internal audit 3. Close controls on Stock accounting - as per agreement with MRPL and SOPs. Any abnormal variations are to be handled with utmost serousness and urgency | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155511 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155511 | 2026-09-17 16:00 | 32.0872 | 425 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155511 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155511 |  | AUD-2026-10-2000017709ACN-2026-10-4000155511 | 21 |  | 27 | 80 | 2 | -4 | 61
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155512 | Open |  |  | Discussed about target completion in view of Half yearly closing. | 1.8 | Improvement plans discussed | 1892 | KOZHIKODE DEPOT | 1. Kasargod indents are being rerouted on a daily basis from Kozhikode IRD. Instead, provision to place indents directly in IMS at Kasargod MRPL Depot will help avoid rereouting of indents on a daily basis. 2. Explore the possbility of catering Power indents through MRPL Kasargod depot for all the ROs attached to it, thereby the requirement of power indents from Kozhikode IRD is eliminated. 3. QC Index for the local is to be monitored to achive AOP target | SOD | Marketing | CZR | 2026-10-31 |  | 6 |  | S2 | F3 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155512 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155512 | 2026-09-17 16:00 | 32.0872 | 425 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155512 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017709ACN-2026-10-4000155512 |  | AUD-2026-10-2000017709ACN-2026-10-4000155512 | 21 |  | 27 | 80 | 2 | -4 | 61
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155514 | Open |  |  | Location informed that Light repair works are in progress in railway siding area, The job of providing canopy, to avoid water ingress, on overlights in completed. The job for lux level improvement is in progress. Location to complete lux level improvement and take up with PESO application for operations after sunset - Q1 observation | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1892 | KOZHIKODE DEPOT | Location to complete lux level improvement and take up with PESO application for operations after sunset | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155514 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155514 | 2026-09-17 16:00 | 32.0872 | 425 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155514 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155514 |  | AUD-2026-10-2000017709ACN-2026-10-4000155514 | 21 |  | 27 | 80 | 2 | -4 | 61
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155520 | Open |  |  | EM Locks not available for Kasargod MRPL loads. EM locks for MRPL loads through Kasargod depot. KMS box, Card readers , internet connection are provided. Balance works are to be handled urgently to ensure all loads pf Kasargod MRPL are with EM locks. Q1 point | 3.5 | EM Lock SOP compliance verified | 1892 | KOZHIKODE DEPOT | EM lock implementation at MRPL Kasargod : The set up for hardware and LAN connections are completed. To expdite trail run and implementation for all TTs | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155520 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155520 | 2026-09-17 16:00 | 32.0872 | 425 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155520 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155520 |  | AUD-2026-10-2000017709ACN-2026-10-4000155520 | 21 |  | 27 | 80 | 2 | -4 | 61
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155521 | Open |  |  | Bay reallocation issues and lane markings are discussed | 3.7 | Gantry operations | 1892 | KOZHIKODE DEPOT | Discussed on Bay reallocation issues and advised to avoid bay reallocation Lane marking / painting at Gantry is faded and advisedto provide markings suitably | SOD | Marketing | CZR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155521 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155521 | 2026-09-17 16:00 | 32.0872 | 425 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155521 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155521 |  | AUD-2026-10-2000017709ACN-2026-10-4000155521 | 21 |  | 27 | 80 | 2 | -4 | 61
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155522 | Open |  |  | Open audit recommendations are reviewed and advised for time bound compliance | 3.18 | OISD/MDSA/SSA compliance reviewed | 1892 | KOZHIKODE DEPOT | Location to comply all audit recommendations in a time bound manner. OISD 2024 : 1/34 Open T4S : 10/10 Open. Comprehensive audit 2025 : 7/101 open Comprehensive audit 2026 : 42/70 open Safe 100 : 2/43 Open HLSA : 0/12 Open GM SWZ visit Q4 : 3/14 Open GM Cochin visit Q1 : 8/174 Open Iternal Audit 2026 : 7/17 open Technical audit : 7/14 open Location to make efforts to be close audit recommendtaionsin time bound manner and ensure that no auidt point remains open more than a year | SOD | Marketing | CZR | 2026-12-31 |  | 2 |  | S2 | F1 | 2026-12-31 | AUD-2026-10-2000017709ACN-2026-10-4000155522 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155522 | 2026-09-17 16:00 | 32.0872 | 486 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155522 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155522 |  | AUD-2026-10-2000017709ACN-2026-10-4000155522 | 21 |  | 27 | 80 | 2 | -4 | 70
[5 empty] | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155524 | Open |  |  | Localtion has disposed some scrap in Q1 | 4.5 | scrap disposal progress reviewed/scrap free environment checked. | 1892 | KOZHIKODE DEPOT | 1. Assets held for disposal is to be handled on priority 2. Complete FA verification | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-10-2000017709ACN-2026-10-4000155524 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155524 | 2026-09-17 16:00 | 32.0872 | 486 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155524 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017709ACN-2026-10-4000155524 |  | AUD-2026-10-2000017709ACN-2026-10-4000155524 | 21 |  | 27 | 80 | 2 | -4 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154682 | Open |  |  | CP System not working. PO placed . | 1.3 | Pending issues reviewed | 3708 | VISAKH NBOT | To follow up with the vendor and expedite work completion | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154682 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154682 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154682 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154682 |  | AUD-2026-10-2000017512ACN-2026-10-4000154682 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154683 | Open |  |  | TT fleet is reduced due to Black listed TTs | 1.8 | Improvement plans discussed | 3708 | VISAKH NBOT | New TT induction thru local advertisement to make up for TT shortfall due to Black listed TTs | SOD | Marketing | SCR | 2026-11-30 |  | 5 |  | S1 | F5 | 2026-11-30 | AUD-2026-10-2000017512ACN-2026-10-4000154683 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154683 | 2026-09-18 17:30 | 31.0247 | 455 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154683 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154683 |  | AUD-2026-10-2000017512ACN-2026-10-4000154683 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154684 | Open |  |  | Following points were observed during the security check at visitor entry gate: 1. Bag Checking was not done before DFMD. 2. DFMD not working properly 3. No Frisking was done by security while entering to the terminal | 2.4 | Security alertness checked (night-halt / surprise checks) | 3708 | VISAKH NBOT | Following points to be ensured during the security check at visitor entry gate: 1.Bag Checking to be done before DFMD. 2. DFMD tobe rectified 3. Frisking to be done by security for all vistors before entering to the terminal | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154684 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154684 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154684 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017512ACN-2026-10-4000154684 |  | AUD-2026-10-2000017512ACN-2026-10-4000154684 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154685 | Open |  |  | 1. Operated three Foam monitors and found ok & checked performance of fire engines & jockey pumps. 2. Checked Emergency kit trollley and found ok | 2.5 | Emergency response preparedness reviewed | 3708 | VISAKH NBOT | 1. Fire engine display of all three fire engines not configured properly. FE34S stopped for overspeed alarm, CWP 2.3 against the given range of 1-2 kg/s.cm | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154685 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154685 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154685 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017512ACN-2026-10-4000154685 |  | AUD-2026-10-2000017512ACN-2026-10-4000154685 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154686 | Open |  |  | CCTV functioning checked. 1. All the CCTV cameras are working. 2. CCTV camera 147 near watchtower angle to be adjusted and PTZ camera no 176 to be cleaned as it is not clear. | 2.6 | CCTV functioning checked | 3708 | VISAKH NBOT | Corrective action to be taken for 2. | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154686 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154686 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154686 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154686 |  | AUD-2026-10-2000017512ACN-2026-10-4000154686 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154687 | Open |  |  | 1. TK105 TAS Dips 1555.3/33/32.3C TK105 Manual Dips 1555.7/29/33 C 2. TK205 TAS Dips 1423.7.8/36.5/50.8 C TK205 Manual Dips 1424.0/36.0/49.5C | 3.7 | Inventory physical dip of minimum two tanks taken | 3708 | VISAKH NBOT | Corretive action to be taken for variation in water dips for TK105 | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154687 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154687 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154687 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154687 |  | AUD-2026-10-2000017512ACN-2026-10-4000154687 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154688 | Open |  |  | Auto vs Manual reconciliation checked. Approx 31% reco is done on manual dips for tanks 12A , 12B , 101, 203 and 212 tank reco is done on manual dips daily, | 3.8 | Auto vs Manual reconciliation checked | 3708 | VISAKH NBOT | 12A , 12B , 101, 203 and 212 to be put in AIM HOLD exception with the help of zone | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154688 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154688 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154688 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154688 |  | AUD-2026-10-2000017512ACN-2026-10-4000154688 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154689 | Open |  |  | No Abnormal variations / unused assets like bio diesel tanks to be offered to needy locations | 3.9 | Abnormal variations / unused assets reviewed | 3708 | VISAKH NBOT | As bio diesel tanks are idling , to be declared in surplus portal . | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154689 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154689 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154689 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154689 |  | AUD-2026-10-2000017512ACN-2026-10-4000154689 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154690 | Open |  |  | TFMS/SAP reconciliation checked & performance is approx 69% vs target of 95% | 3.10 | TFMS/SAP reconciliation checked | 3708 | VISAKH NBOT | Empty tank & Tank under VR use to be put in AIM HOLD exception with the help of zone to maximize the TFMS/SAP reconciliation % | SOD | Marketing | SCR | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154690 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154690 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154690 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154690 |  | AUD-2026-10-2000017512ACN-2026-10-4000154690 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154691 | Open |  |  | 1. Earthpit No: 183 (Dyke 2 , TK206) checked and observed values IR 2.85 OHMS GR 3.54 OHMS. , Earth Pit no 182 (Dyke 2 , TK206) checked and observed values IR 1.6 OHMS GR0.03 OHMS. 2. Emergency Gate checked , Cables outside the emergency cradle found hanging at the exit of the gate 3. Vegetation control checked , found ok | 3.16 | Earth pits / boundary / vegetation control checked | 3708 | VISAKH NBOT | 1, 2) Corrective action to be taken | SOD | Marketing | SCR | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017512ACN-2026-10-4000154691 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154691 | 2026-09-18 17:30 | 31.0247 | 394 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154691 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017512ACN-2026-10-4000154691 |  | AUD-2026-10-2000017512ACN-2026-10-4000154691 | 21 |  | 27 | 80 | 2 | 1 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154692 | Open |  |  | MDSA/SSA/HLSA/Sr.Mgmt Inspection pending observations reviewed. | 3.18 | OISD/MDSA/SSA compliance reviewed | 3708 | VISAKH NBOT | All pending points to be complied in a time bound manner | SOD | Marketing | SCR | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-10-2000017512ACN-2026-10-4000154692 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154692 | 2026-09-18 17:30 | 31.0247 | 455 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154692 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017512ACN-2026-10-4000154692 |  | AUD-2026-10-2000017512ACN-2026-10-4000154692 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000154693 | Open |  |  | CP system revamping, New Weigh Bridges, Sludge pit, Steam system projects to be expedited | 4.3 | Project progress reviewed | 3708 | VISAKH NBOT | All NPCB projects to be completed without time overruns | SOD | Marketing | SCR | 2026-11-30 |  | 5 |  | S1 | F5 | 2026-11-30 | AUD-2026-10-2000017512ACN-2026-10-4000154693 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154693 | 2026-09-18 17:30 | 31.0247 | 455 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154693 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154693 |  | AUD-2026-10-2000017512ACN-2026-10-4000154693 | 21 |  | 27 | 80 | 2 | 1 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-09-18 17:30 | AUD-2026-10-2000017512 | 2026-09-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000154694 | Open |  |  | Old Fire engines and miscellaneous iron scrap lying in scrap yard | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 3708 | VISAKH NBOT | RFD processing to be expedited | SOD | Marketing | SCR | 2026-10-30 |  | 5 |  | S1 | F5 | 2026-10-30 | AUD-2026-10-2000017512ACN-2026-10-4000154694 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017512ACN-2026-10-4000154694 | 2026-09-18 17:30 | 31.0247 | 424 | >20 | AUD-2026-10-2000017512 - ACN-2026-10-4000154694 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017512ACN-2026-10-4000154694 |  | AUD-2026-10-2000017512ACN-2026-10-4000154694 | 21 |  | 27 | 80 | 2 | 1 | 61
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154891 | Open |  |  | Pending Toll payments to be done. | 1.3 | Pending issues reviewed | 1164 | BHATINDA TERMINAL | Corrective action to be done as per HQO advice. | SOD | Marketing | NFZ | 2026-10-15 |  | 8 |  | S2 | F4 | 2026-10-15 | AUD-2026-10-2000017465ACN-2026-10-4000154891 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154891 | 2026-09-28 19:00 | 20.9622 | 409 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154891 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154891 |  | AUD-2026-10-2000017465ACN-2026-10-4000154891 | 21 |  | 27 | 80 | 1 | -2 | 59
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154892 | Open |  |  | Stock loss in Ethanol & SKO for the location is above limit, needs to be reversed. Reconciliation with HMEL for safekeeping is pending. | 3.2 | Inventory verification- physical dip of minimum two AG tanks ,reconciliation (Auto vs Manual), abnormal variation-unsued assets. | 1164 | BHATINDA TERMINAL | Location to take corrective action. Reconciliation with HMEL to be completed. | SOD | Marketing | NFZ | 2026-10-05 |  | 10 |  | S2 | F5 | 2026-10-05 | AUD-2026-10-2000017465ACN-2026-10-4000154892 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154892 | 2026-09-28 19:00 | 20.9622 | 399 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154892 | 532 | 8294 | 21 | 8294 | 14 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154892 |  | AUD-2026-10-2000017465ACN-2026-10-4000154892 | 21 |  | 27 | 80 | 1 | -2 | 57
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154893 | Open |  |  | Housekeeping not found in order. Pending compliances of OISD held in December were reviewed & necessary advice given for expeditingthe same. | 3.4 | HSE- Housekeeping practices, PPE usage ,earth pits, boundry condition,vegetation control ,MOC status, OISD/MDSA/SSA compliance | 1164 | BHATINDA TERMINAL | Location to improve housekeeping. OISD compliances to be expedited immediately. | SOD | Marketing | NFZ | 2026-11-15 |  | 12 |  | S3 | F4 | 2026-11-15 | AUD-2026-10-2000017465ACN-2026-10-4000154893 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154893 | 2026-09-28 19:00 | 20.9622 | 440 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154893 | 532 | 8294 | 21 | 8294 | -26 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154893 |  | AUD-2026-10-2000017465ACN-2026-10-4000154893 | 21 |  | 27 | 80 | 1 | -2 | 63
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000154894 | Open |  |  | Lot of scrap present in old siding area, including that of Retail & Pipeline. | 4.3 | Progress on scrap disposal and unkeep of location to maintain a scrap-free environment | 1164 | BHATINDA TERMINAL | Location to take immediate corrective action for the disposal of scrap. | SOD | Marketing | NFZ | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-10-2000017465ACN-2026-10-4000154894 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154894 | 2026-09-28 19:00 | 20.9622 | 455 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154894 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154894 |  | AUD-2026-10-2000017465ACN-2026-10-4000154894 | 21 |  | 27 | 80 | 1 | -2 | 65
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000154895 | Open |  |  | Refer email dated 21.07.26, it was advised to clear all vegetation/plants from TT Gantry, however, no action was taken as there arestill lot of plants available. | 5.0999999999999996 | Vegetation in TT Gantry | 1164 | BHATINDA TERMINAL | Location to take immediate corrective action for clearing the plants/vegetation at TT Gantry & confirm. | SOD | Marketing | NFZ | 2026-10-10 |  | 8 |  | S2 | F4 | 2026-10-10 | AUD-2026-10-2000017465ACN-2026-10-4000154895 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154895 | 2026-09-28 19:00 | 20.9622 | 404 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154895 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154895 |  | AUD-2026-10-2000017465ACN-2026-10-4000154895 | 21 |  | 27 | 80 | 1 | -2 | 58
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000154896 | Open |  |  | 15 cameras not working | 5.2 | CCTV Cameras | 1164 | BHATINDA TERMINAL | Location to take corrective action. | SOD | Marketing | NFZ | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-10-2000017465ACN-2026-10-4000154896 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154896 | 2026-09-28 19:00 | 20.9622 | 425 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154896 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154896 |  | AUD-2026-10-2000017465ACN-2026-10-4000154896 | 21 |  | 27 | 80 | 1 | -2 | 61
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 5.3 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000154897 | Open |  |  | There is lot of plants & vegetation in Solar Plant area to the extent that there is no access to the panels. | 5.3 | Solar Plant | 1164 | BHATINDA TERMINAL | Location to take corrective action. | SOD | Marketing | NFZ | 2026-10-10 |  | 10 |  | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017465ACN-2026-10-4000154897 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154897 | 2026-09-28 19:00 | 20.9622 | 404 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154897 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154897 |  | AUD-2026-10-2000017465ACN-2026-10-4000154897 | 21 |  | 27 | 80 | 1 | -2 | 58
[5 empty] | LOCATION VISIT-BATHINDA_28.09.26 | 2026-09-28 19:00 | AUD-2026-10-2000017465 | 2026-09-28 09:25 | Confirmed | I1815 | PM - Senior Management Inspection | 5.4 ADDITIONAL OBSERVATIONS | ACN-2026-10-4000154898 | Open |  |  | This asset is lying idle. | 5.4 | Organic Waste Decomposer | 1164 | BHATINDA TERMINAL | Location to take corrective action. | SOD | Marketing | NFZ | 2026-11-30 |  | 10 |  | S2 | F5 | 2026-11-30 | AUD-2026-10-2000017465ACN-2026-10-4000154898 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017465ACN-2026-10-4000154898 | 2026-09-28 19:00 | 20.9622 | 455 | >20 | AUD-2026-10-2000017465 - ACN-2026-10-4000154898 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017465ACN-2026-10-4000154898 |  | AUD-2026-10-2000017465ACN-2026-10-4000154898 | 21 |  | 27 | 80 | 1 | -2 | 65
[5 empty] | LOCATION VISIT-HMEL BITUMEN TML_29.09.26 | 2026-09-29 17:00 | AUD-2026-10-2000017466 | 2026-09-29 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154899 | Open |  |  | Interacted with LIC & new joinee. Advised new officer to take initiative & learn fast. | 1.1 | Interaction with all officers (1–1.5 hrs) | 3129 | BATHINDA BIT HMEL | LIC advised to nominate new officer for SAP & other function training at the earliest. | SOD | Marketing | NFZ | 2026-11-30 |  | 8 |  | S2 | F4 | 2026-11-30 | AUD-2026-10-2000017466ACN-2026-10-4000154899 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017466ACN-2026-10-4000154899 | 2026-09-29 17:00 | 20.0455 | 455 | >20 | AUD-2026-10-2000017466 - ACN-2026-10-4000154899 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017466ACN-2026-10-4000154899 |  | AUD-2026-10-2000017466ACN-2026-10-4000154899 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | LOCATION VISIT-HMEL MKTG TML_29.09.26 | 2026-09-29 13:30 | AUD-2026-10-2000017467 | 2026-09-29 09:45 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155550 | Open |  |  | Interacted with LIC & all officers of the Location. Held detailed discussion with new joinee and guided him to learn, take initiative and contribute positively. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1187 | HMEL WHITE OIL TERMINAL | LIC to monitor suitable formal training & ensure proper mentoring of the new officer. | SOD | Marketing | NFZ | 2026-12-31 |  | 8 |  | S2 | F4 | 2026-12-31 | AUD-2026-10-2000017467ACN-2026-10-4000155550 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017467ACN-2026-10-4000155550 | 2026-09-29 13:30 | 20.1913 | 486 | >20 | AUD-2026-10-2000017467 - ACN-2026-10-4000155550 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017467ACN-2026-10-4000155550 |  | AUD-2026-10-2000017467ACN-2026-10-4000155550 | 21 |  | 27 | 80 | 0 | 0 | 70
MANDAL PRATAPKUMAR | 2026-10-01 | NILABH | 2026-10-01 | Mock drill on Medical emergency ( snake bite) conducted on 29.09.2026 | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150271 | Closed | NILABH | 2026-10-01 | Last Level-II Fire Mock drill was conducted on 07.07.2026. The overall drill was found to be satisfactory. However, observers recommended to conduct Mock drill on Medical emergency prepardness as well. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1305 | KANPUR TERMINAL | Conduct Mock drill on medical emergency and comply. | SOD | Marketing | NCR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-08-2000017157ACN-2026-08-4000150271 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150271 | 2026-08-26 17:00 | 54.0455 | 395 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150271 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017157ACN-2026-08-4000150271 | AUD-2026-08-2000017157ACN-2026-08-4000150271 | 21 | 21 | 27 | 80 | 4 | 4 | 57 | 57
|  | SINGH KUNAL | 2026-10-01 | Surpise/Night inspection is being carried out regularly by officer/LIC. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145971 | Completed | SINGH KUNAL | 2026-10-01 | Surprise night inspection is not being done regularly by location. Ethanol empty TT check is not being done 2 officers. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145971 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145971 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145971 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145971 |  | AUD-2026-07-2000016256ACN-2026-07-4000145971 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | RFD has been approved and forwarded to CPO for MSTC auction. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145972 | Completed | SINGH KUNAL | 2026-10-01 | Location to ensure disposal of scrap material and shifting of surplus material to required location. | 1.8 | Improvement plans discussed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145972 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145972 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145972 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145972 |  | AUD-2026-07-2000016256ACN-2026-07-4000145972 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | TT helper Shri Mohsin Rathod has been identified and nominated as trained personnel with HVD/HZA endorsement to mobilise TT as per the instructions of Officer in charge. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145978 | Completed | SINGH KUNAL | 2026-10-01 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145978 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145978 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145978 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145978 |  | AUD-2026-07-2000016256ACN-2026-07-4000145978 | 21 |  | 27 | 80 | 0 | -26 | 50
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | The point is already mentioned in the q1 2026 senior management audit. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125847 | Closed | SRIJIN S | 2026-10-01 | The compliance status of MDSA,SSA peniding points are reviewed.Location to comply at the earliest lighting jobs for PESO permissionto be completed on priority. | 1.3 | Pending issues reviewed | 1833 | COCHIN BLACK TERMINAL | Location to comply at the earliest lighting jobs for PESO permission to be completed on priority. | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 8 | OCCUPATIONAL HEALTH | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125847 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125847 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125847 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125847 | AUD-2026-03-2000011134ACN-2026-03-4000125847 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-04-21 | All the NPCB projects with march`26 deadline are closed | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125849 | Closed | SRIJIN S | 2026-04-21 | Discussed about targets completion in view of FY end. Seven nos NPCB projects reviewed and advised to close the ARs before 31st March.. | 1.8 | Improvement plans discussed | 1833 | COCHIN BLACK TERMINAL | Location to close all NPCB projects within timelines. | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125849 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125849 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125849 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011134ACN-2026-03-4000125849 | AUD-2026-03-2000011134ACN-2026-03-4000125849 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-09-28 | FIT FOR CAMPAIGN COMPLETED FOR ALL THE CONTRACT WORKMAN AND TT CREW. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125854 | Closed | SRIJIN S | 2026-09-28 | Checked during fit for road campaign. Medical checkup done for all TT crew once in 6 months. Last medical check done on 18-09-2025. | 2.16 | Eyesight / colour-blindness awareness checked | 1833 | COCHIN BLACK TERMINAL | Fit for road campaign to be conducted in March'26 and soft forms to be maintained for better monitoring | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 8 | OCCUPATIONAL HEALTH | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125854 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125854 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125854 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125854 | AUD-2026-03-2000011134ACN-2026-03-4000125854 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | The point is already mentioned in the q1 2026 senior management audit. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125856 | Closed | SRIJIN S | 2026-10-01 | TFMS/SAP integration not implemented at the location.TFMS system is under observation, response of vendor Honeywell is not satisfactory. | 3.10 | TFMS/SAP reconciliation checked | 1833 | COCHIN BLACK TERMINAL | Location to follow up with TFMS vendor on continuous basis | SOD | Marketing | CZR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125856 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125856 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125856 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125856 | AUD-2026-03-2000011134ACN-2026-03-4000125856 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | The point is already mentioned in the q1 2026 senior management audit. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125859 | Closed | SRIJIN S | 2026-10-01 | MDSA 2025-26 :Total 28 points, 2 complied. MDSA 2024-25 :Total 70 points, 64 complied. SSA 2025, total 61 points, 54 complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1833 | COCHIN BLACK TERMINAL | To be complied at the earliest | SOD | Marketing | CZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 2 | OCCUPATIONAL HEALTH | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011134ACN-2026-03-4000125859 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125859 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125859 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011134ACN-2026-03-4000125859 | AUD-2026-03-2000011134ACN-2026-03-4000125859 | 21 | 21 | 26 | 80 | 2 | 0 | 44 | 57
BUDAMPATI GOPALA KRISHNA | 2026-10-01 | MALLELA AMARA REDDY | 2026-10-01 | PT vents, PG Meter, Temp Transmitter, PSV Calibration completed. | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016174 | 2026-06-19 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000148664 | Closed | MALLELA AMARA REDDY | 2026-10-01 | Functionality checked HVLR 3 for TK 205 & TK206, Rim Seal of TK 206, MEFG of TK 206, HCD of MS 011 Pump & Ethanol 061A pump, found ok. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1992 | VISAKH WHITE OIL TERMINAL | PT vents, PG Meter, Temp Transmitter, PSV Calibration pending. Last due since Feb'26. Tender floated with due date 26/06/2026 | SOD | Marketing | SCR | 2026-08-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-08-30 | AUD-2026-08-2000016174ACN-2026-08-4000148664 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016174ACN-2026-08-4000148664 | 2026-09-17 20:00 | 31.9205 | 395 | >20 | AUD-2026-08-2000016174 - ACN-2026-08-4000148664 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016174ACN-2026-08-4000148664 | AUD-2026-08-2000016174ACN-2026-08-4000148664 | 21 | 21 | 27 | 80 | 3 | 2 | 52 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | All the NPCB projects were executed within approved timelines. Continuous followup is being made with RGE for completion of solar project. presently solar project is being carried out at irumpanam terminal. After that cochin terminal project will be completed. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130117 | Closed | SRIJIN S | 2026-10-01 | Capitalization of all the physically completed projects completed. To expedite balance open Projects | 4.3 | 2 projects to be completed for which tendering is under progress | 1833 | COCHIN BLACK TERMINAL | All the NPCB projects are to be executed well within approved timelines and approved budget. Coordinate with RGE on completion of Solar project by sorting out issues between PMC and Contractor. | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130117 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130117 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130117 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130117 | AUD-2026-05-2000012202ACN-2026-05-4000130117 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 57
|  | SINGH KUNAL | 2026-10-01 | Colour blindness has been verified for all TT crew and contract workmen during Half yearly health check carried out at Vadodara Terminal Premises | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145979 | Completed | SINGH KUNAL | 2026-10-01 | Facility not available. | 2.16 | Eyesight / colour-blindness awareness checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145979 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145979 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145979 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145979 |  | AUD-2026-07-2000016256ACN-2026-07-4000145979 | 21 |  | 27 | 80 | 0 | -26 | 50
|  | SINGH KUNAL | 2026-10-01 | All contract workmen are being checked with breath analyser and records are being maintained | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145973 | Completed | SINGH KUNAL | 2026-10-01 | Security guards and electricians in night shift to be checked with breath analyzer and records to be maintained. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145973 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145973 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145973 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145973 |  | AUD-2026-07-2000016256ACN-2026-07-4000145973 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | SOP boards for emergency exit gate are provided. Fire engine testing can be carried out with portable monitor. Fire engine B is repaired. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145974 | Completed | SINGH KUNAL | 2026-10-01 | Yes observed to be satisfactory 1. MCP-6 in Control Room Admin building was tested and found to be working properly with audio visual alarm and paging announcement. 2. Inside the License Area, only assembly point boards are shown and no signboard found available indicating the route direction for the emergency exit gate. 3. Fire Engines F, E, D, and A were tested and all units started successfully in the programmed priority sequence with rated RPM of 1500 and nil deficiencies observed. FE-F: Started in auto mode. RPM observed: 1499–1509. FE-E: Started in auto mode. RPM observed: 1497–1500. FE-D: Started in auto mode. RPM observed: 1495–1503. FE-A: Started in auto mode. RPM observed: 1495–1504. All fire engines operated satisfactorily during testing. Fire engine testing shall be carried out without opening the hydrant. Fire Engine B is taken out for repairs, the same to be put back into operations at the earliest. | 2.5 | Emergency response preparedness reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145974 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145974 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145974 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145974 |  | AUD-2026-07-2000016256ACN-2026-07-4000145974 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | Repaired camera are received from Honeywell and installed at site. Few other camera have gone down now due to network issues. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000145975 | Completed | SINGH KUNAL | 2026-10-01 | 79 cameras out of 91 are currently working. 6 CCTV is sent to M/s. Honeywell for repair which shall be repaired by 30.07.2026. 6 CCTV is having power issue which shall be repaired by 20.06.2026. | 2.6 | CCTV functioning checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145975 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145975 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145975 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145975 |  | AUD-2026-07-2000016256ACN-2026-07-4000145975 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | Locks has been sent to Sterna for further verification. Further action shall be initiated as per SOP for EM-locking after receipt of TPI report from the vendor. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145980 | Completed | SINGH KUNAL | 2026-10-01 | Following TTs checked by intelligent key . 1. Lock ids HE31671 and HE26764 of TT-GJ01FT4489 has checked and found lock id is HE31671 is good and lock id HE26764 is suspected. 2. Lock ids HE35242 and HE35241 of TT-GJ17XX8383 has checked and found both locks are good locks. 3. Lock ids HE553 and HE11287 of TT-GJ35T9726 has checked and found both locks are good locks. 4. Lock ids HE13361 andHE13362 of TT-GJ06BX0277 has checked and both locks have been found suspected. 5. Lock ids HE13155 and HE13156 of TT-GJ06BV5559 has checked and both locks have been found suspected. TT inspection/discipline observation: Checked for TT GJ20J8833 & GJ04W9549 and found ok | 3.1 | TT fittings & discipline checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145980 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145980 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145980 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145980 |  | AUD-2026-07-2000016256ACN-2026-07-4000145980 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | TT crew has been sensitized on mandatory usage of PPE in licensed area premises. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145983 | Completed | SINGH KUNAL | 2026-10-01 | Helmet was not used by helper of TT GJ16AV9886 | 3.15 | Housekeeping & PPE usage checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145983 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145983 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145983 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145983 |  | AUD-2026-07-2000016256ACN-2026-07-4000145983 | 21 |  | 27 | 80 | 0 | -26 | 50
|  | SINGH KUNAL | 2026-10-01 | Discarded earthpits has been identified and highlighted for easy identification with cross mark. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145984 | Completed | SINGH KUNAL | 2026-10-01 | Earthpit near admin building (fire engine side) has been tested. Following are the observation: (a) No identification board was available. (b) Electrode -2.62 ohm (c) Grid-0.18 ohm. It is later observed that the earth-pit has already been discarded and new earthipts have been constructed. Earthpit no -108 near Fire Engine Shed was tested. Following are the observation: (a) No board available. (b) Electrode -1.57 ohm (c)Grid-0.2 ohm | 3.16 | Earth pits / boundary / vegetation control checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145984 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145984 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145984 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145984 |  | AUD-2026-07-2000016256ACN-2026-07-4000145984 | 21 |  | 27 | 80 | 0 | -26 | 50
|  | SINGH KUNAL | 2026-10-01 | TT crew has been sensitised on mandatory usage of PPE in licensed area premises. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145986 | Completed | SINGH KUNAL | 2026-10-01 | • Training to be given to be TT Crew for usage of PPE. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145986 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145986 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145986 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145986 |  | AUD-2026-07-2000016256ACN-2026-07-4000145986 | 21 |  | 27 | 80 | 0 | -26 | 50
|  | SINGH KUNAL | 2026-10-01 | SST is regularly being conducted with TT crew on complaince to ITDG norms while driving TT enroute. Reduction in VTS deviations hasbeen observed. Disciplinary actions are being ensured against the TT crew if deviations are legitimate. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145981 | Completed | SINGH KUNAL | 2026-10-01 | Location to strengthen control to ensure nil deviation | 3.3 | VTS deviations reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145981 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145981 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145981 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145981 |  | AUD-2026-07-2000016256ACN-2026-07-4000145981 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | Concertina coil behind Weighbridge is repaired. | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145990 | Completed | SINGH KUNAL | 2026-10-01 | Concertina coil installed over wall behind TT gantry & near weigh bridge found damaged. | 6.2 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145990 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145990 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145990 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145990 |  | AUD-2026-07-2000016256ACN-2026-07-4000145990 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | Additional support has been provided | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145991 | Completed | SINGH KUNAL | 2026-10-01 | Ethanol sagged near TT gantry. | 6.3 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 |  | 1 |  | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145991 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145991 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145991 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145991 |  | AUD-2026-07-2000016256ACN-2026-07-4000145991 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | Additional support has been provided | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000145992 | Open | SINGH KUNAL | 2026-10-01 | Pipe line support for line less than 6 inch is not at 3 meter distance near TTG | 6.4 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016256ACN-2026-07-4000145992 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145992 | 2026-09-10 21:00 | 38.8788 | 363 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145992 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145992 |  | AUD-2026-07-2000016256ACN-2026-07-4000145992 | 21 |  | 27 | 80 | 0 | -26 | 52
|  | SINGH KUNAL | 2026-10-01 | MOC has been initiated for ATF works | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 17:00 | AUD-2026-07-2000016256 | 2026-06-24 09:00 | Deletion Flag | I1810 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000145985 | Completed | SINGH KUNAL | 2026-10-01 | Location to check and confirm availability of MOC for project works. | 3.17 | MOC status reviewed | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-07-2000016256ACN-2026-07-4000145985 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016256ACN-2026-07-4000145985 | 2026-09-10 21:00 | 38.8788 | 348 | >20 | AUD-2026-07-2000016256 - ACN-2026-07-4000145985 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016256ACN-2026-07-4000145985 |  | AUD-2026-07-2000016256ACN-2026-07-4000145985 | 21 |  | 27 | 80 | 0 | -26 | 50
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | Already the point is mentioned in q2 senior managment inspection audit. | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130113 | Closed | SRIJIN S | 2026-10-01 | TFMS/SAP integration not implemented at the location.TFMS system is under observation, response of vendor Honeywell is not satisfactory. | 3.10 | TFMS/SAP reconciliation checked | 1833 | COCHIN BLACK TERMINAL | TFMS/SAP integrationto be completed at the location by Aug 2026 | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-09-30 | AUD-2026-05-2000012202ACN-2026-05-4000130113 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130113 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130113 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130113 | AUD-2026-05-2000012202ACN-2026-05-4000130113 | 21 | 21 | 27 | 80 | 2 | 0 | 57 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | Already the point is mentioned in q2 senior management inspection audit | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130115 | Closed | SRIJIN S | 2026-10-01 | MDSA 2025-26 :Total 28 points, 3 complied. MDSA 2024-25 :Total 70 points, 64 complied. SSA 2025, total 61 points, 54 complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1833 | COCHIN BLACK TERMINAL | All the points to be complied in time bound manner | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 2 | OCCUPATIONAL HEALTH | S2 | F1 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130115 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130115 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130115 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012202ACN-2026-05-4000130115 | AUD-2026-05-2000012202ACN-2026-05-4000130115 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | already the point is mentioned in q2 senior management audit- 2026 | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130119 | Closed | SRIJIN S | 2026-10-01 | RFD for two company owned jeeps completed | 4.5 | scrap disposal progress reviwed/scrap free environment checked. | 1833 | COCHIN BLACK TERMINAL | Old drums and scrap items near emergency gate are to be handled suitably | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130119 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130119 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130119 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-05-2000012202ACN-2026-05-4000130119 | AUD-2026-05-2000012202ACN-2026-05-4000130119 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | repetetive point. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152407 | Closed | SRIJIN S | 2026-10-01 |  | 1.3 | Pending issues reviewed | 1833 | COCHIN BLACK TERMINAL | Location to comply all audit recommendations in a time bound manner. | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152407 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152407 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152407 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152407 | AUD-2026-09-2000017851ACN-2026-09-4000152407 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | 1. All the NPCB projects closed. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152411 | Closed | SRIJIN S | 2026-10-01 | Discussed about targets completion in view of Half yearly closing. 1. 2 nos open ongoing NPCB projects were reviewed, advised to close the ARs before 30th September without any further extension. 2. Restoration of water pipeline connection from Cochin Corporation. Discussed activities for cost saving / samriddhi initiatives. 3. Cost sharing with zone for power /canteen services etc. to beworked out | 1.8 | Improvement plans discussed | 1833 | COCHIN BLACK TERMINAL | 1. Location to close all NPCB within timelines - september 2026 without any further extensions 2. Cost savings on account of restoration of water pipeline connection from Cochin Corporation to be worked out and submitted in monthly MIS 3. QC index is to be monitored inline with AOP targets | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S2 | F3 | 2026-09-30 | AUD-2026-09-2000017851ACN-2026-09-4000152411 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152411 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152411 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017851ACN-2026-09-4000152411 | AUD-2026-09-2000017851ACN-2026-09-4000152411 | 21 | 21 | 27 | 80 | 2 | 0 | 57 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | transportation po extended for another 6 months. new transportation tender is under progress. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152416 | Closed | SRIJIN S | 2026-10-01 | All interacted TT crew were aware about the roadside emergency procedure | 2.15 | TT crew roadside emergency procedures checked | 1833 | COCHIN BLACK TERMINAL | 1. Follow up is to be made to get new FO transportation tender at the earliest. 2. Take action for extension of existing transportation PO in view of delay in placement of new PO | SOD | Marketing | CZR | 2026-11-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017851ACN-2026-09-4000152416 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152416 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152416 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152416 | AUD-2026-09-2000017851ACN-2026-09-4000152416 | 21 | 21 | 27 | 80 | 2 | 0 | 65 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | Medical health checkup completed | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152417 | Closed | SRIJIN S | 2026-10-01 | Medical checkup is to be carried out for all TT crew once in 6 months. Last medical check done on 18-09-2025. | 2.16 | Eyesight / color-blindness awareness checked | 1833 | COCHIN BLACK TERMINAL | Medical checkup to be done for all TT crew once in 6 months. | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017851ACN-2026-09-4000152417 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152417 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152417 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152417 | AUD-2026-09-2000017851ACN-2026-09-4000152417 | 21 | 21 | 27 | 80 | 2 | 0 | 57 | 57
ALBY ABRAHAM ARACKAL | 2026-10-01 | SRIJIN S | 2026-10-01 | inspected foreshore jetty site. Housekeeping and grass cutting carried out. Court case is being monitored closely in coordination with legal dept. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152423 | Closed | SRIJIN S | 2026-10-01 | Location has conducted meeting with factory inspector on 04-12-2025. Court case of Foreshore jetty | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1833 | COCHIN BLACK TERMINAL | Location to inspect foreshore jetty site, maintain upkeep of the facilities. Court case is to be monitored closely in coordinationwith legal dept. | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 2 | OCCUPATIONAL HEALTH | S2 | F1 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152423 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152423 | 2026-09-08 16:00 | 41.0872 | 395 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152423 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152423 | AUD-2026-09-2000017851ACN-2026-09-4000152423 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 57
BUDAMPATI GOPALA KRISHNA | 2026-10-01 | PULI JYOTSNA LATHA | 2026-10-01 | Ensured compliance of observations mentioned in future mock drills. | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154543 | Closed | PULI JYOTSNA LATHA | 2026-10-01 | Mock Drill conducted on 18.08.2026 with Double contingency scenario. Mock Drill Observations for improvement i) Security personnel should be contacted and mobilized promptly to carry out the required emergency evacuation activity. | 2.2 | Double contingency scenario simulated; observations recorded | 1992 | VISAKH WHITE OIL TERMINAL | The compliance of observations mentioned to be ensured in future mock drills. | SOD | Marketing | SCR | 2026-09-30 | POOR COMMUNICATION | 8 | EMERGENCY | S2 | F4 | 2026-09-30 | AUD-2026-10-2000017705ACN-2026-10-4000154543 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154543 | 2026-09-17 20:00 | 31.9205 | 395 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154543 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017705ACN-2026-10-4000154543 | AUD-2026-10-2000017705ACN-2026-10-4000154543 | 21 | 21 | 27 | 80 | 3 | 2 | 57 | 57
BUDAMPATI GOPALA KRISHNA | 2026-10-01 | PULI JYOTSNA LATHA | 2026-10-01 | Location to ensuring frisking is done for all visitors and regular employees/ workmen before entry to the premises. And VMS is properly maintained and filed. | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154545 | Closed | PULI JYOTSNA LATHA | 2026-10-01 | Night surprise check was not done. Proper Hand frisking to be done by the security before permitting entry to the premises. VisitorManagement Passes not properly maintained. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1992 | VISAKH WHITE OIL TERMINAL | Location to ensure proper frisking is done for all visitors and regular employees/ workmen before entry to the premises. And VMS isproperly maintained and filed. | SOD | Marketing | SCR | 2026-09-20 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-10-2000017705ACN-2026-10-4000154545 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154545 | 2026-09-17 20:00 | 31.9205 | 395 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154545 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017705ACN-2026-10-4000154545 | AUD-2026-10-2000017705ACN-2026-10-4000154545 | 21 | 21 | 27 | 80 | 3 | 2 | 55 | 57
BUDAMPATI GOPALA KRISHNA | 2026-10-01 | PULI JYOTSNA LATHA | 2026-10-01 | Ensuring closure ofCC alerts within timeframe to avoid escalation | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000154549 | Closed | PULI JYOTSNA LATHA | 2026-10-01 | Ensure closure of OCC alerts within timeframe to avoid escalation | 3.3 | VTS deviations reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Ensure closure of OCC alerts within timeframe to avoid escalation | SOD | Marketing | SCR | 2026-09-20 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-20 | AUD-2026-10-2000017705ACN-2026-10-4000154549 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154549 | 2026-09-17 20:00 | 31.9205 | 395 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154549 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017705ACN-2026-10-4000154549 | AUD-2026-10-2000017705ACN-2026-10-4000154549 | 21 | 21 | 27 | 80 | 3 | 2 | 55 | 57
BUDAMPATI GOPALA KRISHNA | 2026-10-01 | PULI JYOTSNA LATHA | 2026-10-01 | Ensuring periodic testing and refill of Fire cylinders of TTs | AUDIT UPLOAD IN SAP | 2026-09-17 20:00 | AUD-2026-10-2000017705 | 2026-09-17 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000154547 | Closed | PULI JYOTSNA LATHA | 2026-10-01 | TT Driver - V. Prabhakar operated two Fire extingusher of TT no AP31TG8959, one FE not functioned , second FE performance found OK.TT driver B.Srinivas Rao operated FE of TT no AP39UG3688, performance found OK | 2.14 | TT crew fire extinguisher usage checked | 1992 | VISAKH WHITE OIL TERMINAL | Ensure periodic testing and refill of Fire Cylinders of all TTs | SOD | Marketing | SCR | 2026-10-15 | POOR COMMUNICATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-15 | AUD-2026-10-2000017705ACN-2026-10-4000154547 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017705ACN-2026-10-4000154547 | 2026-09-17 20:00 | 31.9205 | 395 | >20 | AUD-2026-10-2000017705 - ACN-2026-10-4000154547 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017705ACN-2026-10-4000154547 | AUD-2026-10-2000017705ACN-2026-10-4000154547 | 21 | 21 | 27 | 80 | 3 | 2 | 59 | 57
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154695 | Open |  |  | Day-to-day operational activities were reviewed. Officers were advised to get engaged in field for TT dip checking / TT fittings checking. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1644 | KOLKATA-I TERMINAL | Location to control TDG violation, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration. LIC to carry out surprise check of loaded TTs. TTs. All safety fittings of TTs to be checked thoroughly. All the officerswere advised to have hands on training and operational knowledge of all the safety critical equipment. All officers to start reporting of Near misses, UCs, UAs in SAP Officers and workmen to wear cotton coverall all the time when they are in operational area. | SOD | Marketing | EZ | 2026-10-31 |  | 10 |  | S2 | F5 | 2026-10-31 | AUD-2026-10-2000017513ACN-2026-10-4000154695 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000154695 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000154695 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017513ACN-2026-10-4000154695 |  | AUD-2026-10-2000017513ACN-2026-10-4000154695 | 21 |  | 27 | 80 | 0 | -7 | 61
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154696 | Open |  |  | Individual review of officer carried out with respect to KPI and overall location performance | 1.2 | Performance review conducted | 1644 | KOLKATA-I TERMINAL | Officers were advised to have hand on exercise for operating all the fire fighting equipment. DSO to provided the safety training as per OISD 154 to the newly transferred officer. Further, all officers should have the knowledge w.r.t positioning of all the safetycritical equipment and ESD. LIC to closely monitor the losses booked in ethanol & MS and to arrest the losses by suitable actions. Officer handling ethanol must ensure that the ethanol loss in each TT is booked in SAP. Officer to be extra vigilant on qty./ temp etc while processing ethanol GRN. | SOD | Marketing | EZ | 2026-10-15 |  | 5 |  | S1 | F5 | 2026-10-15 | AUD-2026-10-2000017513ACN-2026-10-4000154696 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000154696 | 2026-09-18 | 31.7538 | 409 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000154696 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000154696 |  | AUD-2026-10-2000017513ACN-2026-10-4000154696 | 21 |  | 27 | 80 | 0 | -7 | 59
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154697 | Open |  |  | 1.Security PO to be expedited in close coordination with CPO. 2. Regular E M Lock checking by LIC Master key and records to be maintained 3. Adequate E M Locks & Key inventory at location to be maintained 4. EBMS 20% blending check at TT Gantry to be ensured and records to be maintained 5. Off Spec FO/ LDO to be liquidated. MTO Hexane also to be liquidated. LSHFHSD to be supplied to DS customers in coordination DS RM. TK210 to be put in service after PESO approval. 6. Score BG issue to be resolved in close coordination with IFS custodian. | 1.3 | Pending issues reviewed | 1644 | KOLKATA-I TERMINAL | Expeditious action / compliance to be taken | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000154697 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000154697 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000154697 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000154697 |  | AUD-2026-10-2000017513ACN-2026-10-4000154697 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154698 | Open |  |  | 1. TT Dip elimination file note approval - Pending (This point was also discussed in last inspection) 2. Near Miss, UCs and UAs are being recorded at location. The numbers should increase basis field visits (This point was also discussed in last inspection) 3. TFMS SAP integration file note approval - Pending. TFMS project to be completed at the earliest followed by TFMS SAP integration file note approval. 4. DGR security PO to be expedited in close coordination with CPO | 1.4 | Earlier action points status checked | 1644 | KOLKATA-I TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2027-03-31 |  | 5 |  | S1 | F5 | 2027-03-31 | AUD-2026-10-2000017513ACN-2026-10-4000154698 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000154698 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000154698 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000154698 |  | AUD-2026-10-2000017513ACN-2026-10-4000154698 | 21 |  | 27 | 80 | 0 | -7 | 83
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000154699 | Open |  |  | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1644 | KOLKATA-I TERMINAL | 1. Location to upload the 100%TT dip checking data in SAP. 2. Location to ensure the recovery w.r.t VTS equipment charges 3. Location to monitor and take action line with ITDG for the deviations (route/ speed/ night halting etc). 4. All open HLSA points to beclosed 5. ERDMP of BB-II is due in Feb'27. All purchase activity to be done well in advance. (Repeat Point) 6. Tank to Tank transfer document in SAP to be processed only for physical transfers. LIC to regularly review the tank to tank transfer documents having qty. less than 5 KL 7. Manual allocation of TT in IMS to be minimised and records with justification to be maintained for all such cases. 8. EM lock handling and Monitoring : Part load must not be executed without prior approval of zonal O&D head, Post decantation OTP to be ensured, programming key usages to be ensured for all TT within a period of max. 1 month. 9. All RTGPs to be reviewed periodically and closed 10. All Framework order, Misc. PR, PRF to be approved only after proper review by LIC. NIL cases of scope change in any AR to be done without prior approval. 11. EM locking exception approval to be done (specially TT outisde RO radius) only after due verification. | SOD | Marketing | EZ | 2026-10-10 |  | 10 |  | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000154699 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000154699 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000154699 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017513ACN-2026-10-4000154699 |  | AUD-2026-10-2000017513ACN-2026-10-4000154699 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155650 | Open |  |  | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1644 | KOLKATA-I TERMINAL | 1. CBAC to be made operational in Tank Farm, TT Gantry.(This was also observed in last inspection) 2. Calibration verification forTTs to be done and records maintained. 3. Baggage Scanner fouund non functional. To be rectified immediately in close coordination with vendor. 4. Feild boards/ SLD in feild got faded. To be rectified. 5. Due date of cleaning for water tank in BB-II to be corrected / updated 6. Grass observed b/w tank shell and ground to be removed. 7. Dehn India visit to be ensured so as to investigate the root case of damage for KMS box due to lightening. 8. LPS EPS to be tested and data to be updated on the board | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155650 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155650 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155650 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155650 |  | AUD-2026-10-2000017513ACN-2026-10-4000155650 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155653 | Open |  |  | Location has total of 110 CCTV Camera and 94 found as functional. Random video recording of the CCTV at main gate area were checked. CCTV back up of only 60 days was found. [Repeat Point] | 2.6 | CCTV functioning checked | 1644 | KOLKATA-I TERMINAL | 1. Installation of new CCTV job to be completed in all aspect ans AR to be closed. 2. CCTV back up of 92 days must be ensured without fail 3. Security check at TT in gate to be strengthened 4. Monitoring on safe movement of the Incoming Lube TTs inside the TT gantry area for weighment to be ensured. As on date of inspection, there in no gate pass system implemented for this activity. JointMOC approval from O&D and Lubes to be taken for all such cases. [repeat Point] | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155653 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155653 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155653 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155653 |  | AUD-2026-10-2000017513ACN-2026-10-4000155653 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155654 | Open |  |  | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. | 2.7 | VA alerts checked / analysed | 1644 | KOLKATA-I TERMINAL | All SOP must be followed with NIL exception. | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155654 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155654 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155654 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155654 |  | AUD-2026-10-2000017513ACN-2026-10-4000155654 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155655 | Open |  |  | Access control system at Tank farm, TTG found to be non functional. (This was also observed during last inspection) It was also noted that the VMS service is not operational. Baggage Scanner at Main Gate was found non functional. | 2.8 | Access control systems checked | 1644 | KOLKATA-I TERMINAL | Location to closely coordinate with M/s Godrej and ensure 100% functionality of the access control system VMS to be implemented. Nil case of visitors entry without VMS to be ensured. Baggage scanner to be made functional. | SOD | Marketing | EZ | 2026-10-15 |  | 5 |  | S1 | F5 | 2026-10-15 | AUD-2026-10-2000017513ACN-2026-10-4000155655 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155655 | 2026-09-18 | 31.7538 | 409 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155655 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155655 |  | AUD-2026-10-2000017513ACN-2026-10-4000155655 | 21 |  | 27 | 80 | 0 | -7 | 59
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155657 | Open |  |  | Random checking of the dip for TT no. WB19L2980, NL04D9660, WB19R3295 post loading done and found minimal variation. | 3.2 | Post-loading dip checks verified | 1644 | KOLKATA-I TERMINAL | Gantry officer to encure all TTs are dip checked post loading and any abnormal vairaion is reported to LIC followed by caliberationverification of that TT | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155657 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155657 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155657 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155657 |  | AUD-2026-10-2000017513ACN-2026-10-4000155657 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155658 | Open |  |  | Location is taking action on VTS deviation basis mail received from zone and from OCC. Location to take extra attention on route deviation/ unauthorised stopages by trucks. Prompt actions to be taken on erring transporters as per ITDG.5 if applicable. Spotsidentified where multiple TTs are stopping unauthorisedly to be initimated to the police station under which the location is identified. Regualr feedback to be shared with zone on action taken on such cases. | 3.3 | VTS deviations reviewed | 1644 | KOLKATA-I TERMINAL | Location is advised to create the secondary route wherever applicable and action to be taken as per ITDG wherever deemed fit. TT blocked by Novex to be investigated thoroughly and records mainatined. | SOD | Marketing | EZ | 2026-10-10 |  | 8 |  | S2 | F4 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155658 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155658 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155658 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017513ACN-2026-10-4000155658 |  | AUD-2026-10-2000017513ACN-2026-10-4000155658 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155659 | Open |  |  | Random checking of EBP done from the all level sample of TT WB19J6194 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1644 | KOLKATA-I TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155659 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155659 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155659 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155659 |  | AUD-2026-10-2000017513ACN-2026-10-4000155659 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155660 | Open |  |  | Ethanol/Bio Diesel receipt SOPs to be strictly adhered to and concerned Officers to be well conversant of same. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1644 | KOLKATA-I TERMINAL | Necessary records to be maintained for each TTs unloaded for assessing the receipt quantity. | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155660 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155660 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155660 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155660 |  | AUD-2026-10-2000017513ACN-2026-10-4000155660 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155661 | Open |  |  | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1644 | KOLKATA-I TERMINAL | MS and Ethanol losses to be brought under control | SOD | Marketing | EZ | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-10-2000017513ACN-2026-10-4000155661 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155661 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155661 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155661 |  | AUD-2026-10-2000017513ACN-2026-10-4000155661 | 21 |  | 27 | 80 | 0 | -7 | 61
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155664 | Open |  |  | Local loading report reviewd and found that local loading being done for own use in DG/ Fire Engine. Local loading being also done for Budge Budge lube and Ramnagar lubes. Two TT was made sick in TAS in FY 26-27 for which records are maintained at location. | 3.14 | Local loading checks (if applicable) | 1644 | KOLKATA-I TERMINAL | Planning Officer to be extra vigilant and must consult the officer hadnling TAS before making any TT as Sick in TAS. Strict control measures to be ensured for all local loading/ Sick TT/ User Access Mtrix, local order entry and other critical TAS parameters. | SOD | Marketing | EZ | 2026-10-10 |  | 10 |  | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155664 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155664 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155664 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017513ACN-2026-10-4000155664 |  | AUD-2026-10-2000017513ACN-2026-10-4000155664 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155665 | Open |  |  | Housekeeping & PPE usage checked | 3.15 | Housekeeping & PPE usage checked | 1644 | KOLKATA-I TERMINAL | House keeping in Admin Area Water Tank farm to be improved. Project surplus must be removed. Long grass observed behind the VRU area. To be removed immediately. | SOD | Marketing | EZ | 2026-10-10 |  | 5 |  | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155665 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155665 | 2026-09-18 | 31.7538 | 404 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155665 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155665 |  | AUD-2026-10-2000017513ACN-2026-10-4000155665 | 21 |  | 27 | 80 | 0 | -7 | 58
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155667 | Open |  |  | OISD - NIL pending Point HLSA : 1 pending points T4S : 14 pending points SSA - 1 Pending point (Repeat Point) Comprehensive Audit - 4 pending points Premonsoon Checks for tanks : 11 pending points (Repeat Point) Sr. management Inspection in Q4 FY 25-26 : 7 pending points (Repeat Point) Sr. management Inspection in Q1 FY 26-27 : 11 pending point) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1644 | KOLKATA-I TERMINAL | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-10-2000017513ACN-2026-10-4000155667 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155667 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155667 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-10-2000017513ACN-2026-10-4000155667 |  | AUD-2026-10-2000017513ACN-2026-10-4000155667 | 21 |  | 27 | 80 | 0 | -7 | 61
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155669 | Open |  |  | 1. CCTV Installation job to be expedited 2. BB-II close loop line project to be closed at the earliest 3. TFMS project PO to be expedited followed by field work | 4.3 | Project progress reviewed | 1644 | KOLKATA-I TERMINAL | To be expedited | SOD | Marketing | EZ | 2026-10-31 |  | 4 |  | S1 | F4 | 2026-10-31 | AUD-2026-10-2000017513ACN-2026-10-4000155669 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155669 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155669 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155669 |  | AUD-2026-10-2000017513ACN-2026-10-4000155669 | 21 |  | 27 | 80 | 0 | -7 | 61
[5 empty] | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155670 | Open |  |  | Scrap Disposal to be expedited. Scrap in BB-I : Cables, Cable Trays, Old valves and other assets scrap lying. Sludge : Approx. 30 drums of sludge found lying in BB-I tank farm area. Uniddentifed scrap [Fire Extingusher, Unloading hose] found in Kolkata Terminal-II. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1644 | KOLKATA-I TERMINAL | All scrap items to be identified by H-1 and disposal in H-2 | SOD | Marketing | EZ | 2026-10-31 |  | 4 |  | S1 | F4 | 2026-10-31 | AUD-2026-10-2000017513ACN-2026-10-4000155670 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155670 | 2026-09-18 | 31.7538 | 425 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155670 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017513ACN-2026-10-4000155670 |  | AUD-2026-10-2000017513ACN-2026-10-4000155670 | 21 |  | 27 | 80 | 0 | -7 | 61
KAPIL DEV | 2026-10-01 | SINGH KUNAL | 2026-10-01 | TT helper Shri Mohsin Rathod has been identified and nominated as trained personnel with HVD/HZA endorsement to mobilise TT as per the instructions of Officer in charge. | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155024 | Closed | SINGH KUNAL | 2026-10-01 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155024 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155024 | 2026-09-10 21:00 | 38.8788 | 395 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155024 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155024 | AUD-2026-09-2000017759ACN-2026-09-4000155024 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 57
KAPIL DEV | 2026-10-01 | SINGH KUNAL | 2026-10-01 | ZCC proposal for ATF budget appropriation has been approved and tender been forwarded to CPO for placement of PO. | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000155032 | Closed | SINGH KUNAL | 2026-10-01 | ZCC proposal for ATF budget appropriation to be submitted and follow up shall be made with CPO for PO placement. | 4.3 | Project progress reviewed | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-15 | AUD-2026-09-2000017759ACN-2026-09-4000155032 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155032 | 2026-09-10 21:00 | 38.8788 | 395 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155032 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155032 | AUD-2026-09-2000017759ACN-2026-09-4000155032 | 21 | 21 | 27 | 80 | 0 | -26 | 59 | 57
KAPIL DEV | 2026-10-01 | SINGH KUNAL | 2026-10-01 | Approved SOP is available | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155037 | Closed | SINGH KUNAL | 2026-10-01 | DG Fire engine fuel top up SOP not approved by Zone. | 6.3 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155037 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155037 | 2026-09-10 21:00 | 38.8788 | 395 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155037 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155037 | AUD-2026-09-2000017759ACN-2026-09-4000155037 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 57
HARINIVAS S | 2026-10-01 | JOSVIN SUNNY | 2026-10-01 | OISD audit 2024 total 34 points, 33 complied. MDSA 2025, total 76 points, 74complied SSA 2025, total 43 points, 41 complied. The points are mentioned in Q2 FY 27 senior management | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122292 | Closed | JOSVIN SUNNY | 2026-10-01 | OISD audit 2024 total 34 points, 29 are complied. MDSA 2025, total 76 points, 54 complied. SSA 2025, total 43 points, 31 complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1892 | KOZHIKODE DEPOT | To be complied at the earliest | SOD | Marketing | CZR | 2026-03-31 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122292 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122292 | 2026-09-17 16:00 | 32.0872 | 395 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122292 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122292 | AUD-2026-02-2000010911ACN-2026-03-4000122292 | 21 | 21 | 26 | 80 | 2 | -4 | 31 | 57
HARINIVAS S | 2026-10-01 | JOSVIN SUNNY | 2026-10-01 | officer provided | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122284 | Closed | JOSVIN SUNNY | 2026-10-01 | One officer is required as replacement for the Assistant Manager M& I who is going on study leave. | 1.5 | HQO / Zonal support required identified | 1892 | KOZHIKODE DEPOT | One experienced Officer required. | SOD | Marketing | CZR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 6 | PROCESS SAFETY | S3 | F2 | 2026-02-28 | AUD-2026-02-2000010911ACN-2026-03-4000122284 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122284 | 2026-09-17 16:00 | 32.0872 | 395 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122284 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000010911ACN-2026-03-4000122284 | AUD-2026-02-2000010911ACN-2026-03-4000122284 | 21 | 21 | 26 | 80 | 2 | -4 | 26 | 57
HARINIVAS S | 2026-10-01 | JOSVIN SUNNY | 2026-10-01 | HSLA Audit recommendation are complied and night inspections are carried | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000137542 | Closed | JOSVIN SUNNY | 2026-10-01 | Interacted with security and their awareness on emergency preparedness found to be satisfactory. Documentation in gate found satisfactory. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1892 | KOZHIKODE DEPOT | Advise to carry out security gap assessement w.r.t dedicated HLSA team as per HQO email for all applicable points and draw action plan for timely compliances. Advised to carry out surprise night inspection and maintain records with corrective actions. | SOD | Marketing | CZR | 2026-07-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-30 | AUD-2026-06-2000013060ACN-2026-06-4000137542 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000137542 | 2026-09-17 16:00 | 32.0872 | 395 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000137542 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000137542 | AUD-2026-06-2000013060ACN-2026-06-4000137542 | 21 | 21 | 27 | 80 | 2 | -4 | 48 | 57
HARINIVAS S | 2026-10-01 | JOSVIN SUNNY | 2026-10-01 | POINT IS OPENED IN Q2 FY26 AUDIT | GM-O&D INSPECTION AT KOZHIKODE-JUNE 2026 | 2026-06-11 18:30 | AUD-2026-06-2000013060 | 2026-06-10 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138601 | Closed | JOSVIN SUNNY | 2026-10-01 | MDSA 2025-26 :Total 28 points, 3 complied. MDSA 2024-25 :Total 70 points, 64 complied. SSA 2025, total 61 points, 54 complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1892 | KOZHIKODE DEPOT | All the points to be complied in time bound manner | SOD | Marketing | CZR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013060ACN-2026-06-4000138601 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013060ACN-2026-06-4000138601 | 2026-09-17 16:00 | 32.0872 | 395 | >20 | AUD-2026-06-2000013060 - ACN-2026-06-4000138601 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013060ACN-2026-06-4000138601 | AUD-2026-06-2000013060ACN-2026-06-4000138601 | 21 | 21 | 27 | 80 | 2 | -4 | 44 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | 1. Location has signed agreement with HOCL for sharing of foam tender with terminal in case of any emergency. Agreement dt 19.03.2026 is valid for 2 years- COMPLIED 2. Location has disposed off Misc.MS Scrap-10 MT vide RFD no.1006588 and 1006581 kept near pump house - COMPLIED 3. KSEB has approved deduction of SD amount of subsequent monthly bills from September 2026 - COMPLIED 4. Locationhas carried out cost benefit analysis for reduction of Contract demand. The analysis indicates that there is no significant cost advantage in reducing contract demand from 300KVA TO 265KVA. Also the same will incur additional cost for replacement of CT. Hence location has dropped the proposal of contract demand deduction from 300KVA to 265KVA- COMPLIED 5. Dip elimination data collection completed. File note was sent back by HWO for modification. The same has been resubmitted with due changes. File note has been sent for approval. - COMPLIED | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125835 | Closed | Sreelal P P | 2026-10-01 | 1. Signing of Agreement with HOCL for sharing of foam tender for compliance of site appraisal recommendation to be given prime importance. 2. One more lot of scrap is under auction with a due date of 16.03.2026. 3. Followup with KSEB for refund of 25lakhs underSecurity Deposit. 4. Location is working towards reduction of contract demand to 265KVA from 300KVA. 5. Dip elimination data collection completed. File note will be submitted by 31.03.2026 | 1.3 | Pending issues reviewed | 1845 | IRUMPANAM TERMINAL | All pending jobs to be completed | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125835 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125835 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125835 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125835 | AUD-2026-03-2000011133ACN-2026-03-4000125835 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Status of Audits OISD - 43/43 Complied SSA - 46/47 Complied MDSA 2025 March - 50/50 Complied Comprehensive Audit - 22/26 Complied Pending audit points were highlighted in subsequent GM audits. Hence point being closed to prevent repetetion of points | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125842 | Closed | Sreelal P P | 2026-10-01 | Status of Audits OISD - 39/43 Complied SSA - 37/47 Complied MDSA 2025 March - 44/50 Complied Comprehensive Audit - 16/26 Complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1845 | IRUMPANAM TERMINAL | Audit compliance to be done in time bound manner | SOD | Marketing | CZR | 2026-05-31 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S4 | F2 | 2026-05-31 | AUD-2026-03-2000011133ACN-2026-03-4000125842 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125842 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125842 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125842 | AUD-2026-03-2000011133ACN-2026-03-4000125842 | 21 | 21 | 26 | 80 | 1 | -4 | 39 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Boundary wall strengthening work carried out vide PO placed on M/s Hitech Engineers | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000141176 | Closed | Sreelal P P | 2026-10-01 | The location had floated tender for repair of boundary wall along LPG parking area. However tender has failed due to higher quote from bidder. New tender to be floated | 1.3 | Pending issues reviewed | 1845 | IRUMPANAM TERMINAL | Take timely action for compound wall repairs as per consultant report | SOD | Marketing | CZR | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S4 | F2 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141176 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141176 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141176 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141176 | AUD-2026-06-2000013833ACN-2026-06-4000141176 | 21 | 21 | 27 | 80 | 1 | -4 | 52 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Status of Audits OISD - 43/43 Complied SSA - 46/47 Complied MDSA 2025 March - 50/50 Complied Comprehensive Audit - 22/26 Complied OISD Surprise Audit - 5/11 Complied Senior Management Inspection March 26 - 11/12 Complied Pending audit points reviewed in subsequent GM audit. Point being closed to prevent repetetion of similar audit points | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000141188 | Closed | Sreelal P P | 2026-10-01 | Status of Audits OISD - 39/43 Complied SSA - 42/47 Complied MDSA 2025 March - 46/50 Complied Comprehensive Audit - 19/26 Complied OISD Surprise Audit - 3/11 Complied Senior Management Inspection March 26 - 8/12 Complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1845 | IRUMPANAM TERMINAL | Audit compliance to be done in time bound manner | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 9 | ASSET INTEGRITY | S3 | F3 | 2026-09-30 | AUD-2026-06-2000013833ACN-2026-06-4000141188 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141188 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141188 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141188 | AUD-2026-06-2000013833ACN-2026-06-4000141188 | 21 | 21 | 27 | 80 | 1 | -4 | 57 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | 1. Spare skimmer procured from M/s Emperor Enterprises 2. ETP logbook is maintained and flowmeters readings are recorded | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000141189 | Closed | Sreelal P P | 2026-10-01 | Full round taken with entire maintenance team. Operated dyke valve No:5 and HVLR 3. Visited ETP area. | 4.1 | Full Field round completed. | 1845 | IRUMPANAM TERMINAL | 1.Spare skimmer belt to be procured and kept available for operational readiness. 2. Operate ETP functionality at regular intervals and maintain log book for release of water. | SOD | Marketing | CZR | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141189 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141189 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141189 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141189 | AUD-2026-06-2000013833ACN-2026-06-4000141189 | 21 | 21 | 27 | 80 | 1 | -4 | 48 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Paint touch up work carried out on hydrant line near TK6 | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141194 | Closed | Sreelal P P | 2026-10-01 | Paint touch-up work for the hydrant line near TK-06 to be carried out. | 6.1 |  | 1845 | IRUMPANAM TERMINAL | Paint touch-up work for the hydrant line near TK-06 to be carried out. | SOD | Marketing | CZR | 2026-07-31 | POOR EQUIPMENT MAINTENANCE | 4 | EMERGENCY | S2 | F2 | 2026-07-31 | AUD-2026-06-2000013833ACN-2026-06-4000141194 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141194 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141194 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013833ACN-2026-06-4000141194 | AUD-2026-06-2000013833ACN-2026-06-4000141194 | 21 | 21 | 27 | 80 | 1 | -4 | 48 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Mesh/screens provided for the windows of the PCC Room to prevent entry of insects and dust. | GM-O&D INSPECTION AT IRUMPNAMA TERMINAL | 2026-06-19 17:00 | AUD-2026-06-2000013833 | 2026-06-19 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000141195 | Closed | Sreelal P P | 2026-10-01 | Mesh/screens to be provided for the windows of the PCC Room to prevent entry of insects and dust. | 6.2 |  | 1845 | IRUMPANAM TERMINAL | Mesh/screens to be provided for the windows of the PCC Room to prevent entry of insects and dust. | SOD | Marketing | CZR | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-08-31 | AUD-2026-06-2000013833ACN-2026-06-4000141195 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013833ACN-2026-06-4000141195 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-06-2000013833 - ACN-2026-06-4000141195 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013833ACN-2026-06-4000141195 | AUD-2026-06-2000013833ACN-2026-06-4000141195 | 21 | 21 | 27 | 80 | 1 | -4 | 52 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | New E2 Officer and two E0 officers have reported at location in September. Adequate manpower available at location. | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154524 | Closed | Sreelal P P | 2026-10-01 | Interacted with Officers. Concerns regarding reduction in Employees due to superannuation was discussed. Location needs E0 employees in place of retiring NM employees. Available three (one clerical + two field staff) will superannuate by May 2027. One operations officer E2 grade is assigned to location, reported at location on 7.9.2026. . | 1.1 | Interaction with all officers (1–1.5 hrs) | 1845 | IRUMPANAM TERMINAL | Matter is to be persued further with Zone/HQO for placement of E0 Employees | SOD | Marketing | CZR | 2026-10-31 | COST-CUTTING COMPROMISING SAFETY | 4 | EMERGENCY | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154524 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154524 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154524 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017404ACN-2026-09-4000154524 | AUD-2026-09-2000017404ACN-2026-09-4000154524 | 21 | 21 | 27 | 80 | 1 | -4 | 61 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Location has completed pipeline coating repair works. | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154525 | Closed | Sreelal P P | 2026-10-01 | Pipeline coating repairs are in progress. | 1.3 | Pending issues reviewed | 1845 | IRUMPANAM TERMINAL | Location to timely complete repair works as per survey report | SOD | Marketing | CZR | 2026-12-31 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S4 | F2 | 2026-12-31 | AUD-2026-09-2000017404ACN-2026-09-4000154525 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154525 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154525 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154525 | AUD-2026-09-2000017404ACN-2026-09-4000154525 | 21 | 21 | 27 | 80 | 1 | -4 | 70 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Location has initiated action as per the recommendations. | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154527 | Closed | TILKAN RAVINDRA KUMAR | 2026-10-02 | Clear guidelines communicated to concerned officers | 1.6 | Expectations clearly communicated to officers | 1845 | IRUMPANAM TERMINAL | XX | SOD | Marketing | CZR | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154527 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154527 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154527 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154527 | AUD-2026-09-2000017404ACN-2026-09-4000154527 | 21 | 21 | 27 | 80 | 1 | -4 | 61 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | SOP for Bottom loading operations are displayed at Gantry 1,Gantry 2 and Gantry 3 | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154529 | Closed | Sreelal P P | 2026-10-01 | Discussed with LIC and DSO | 1.8 | Improvement plans discussed | 1845 | IRUMPANAM TERMINAL | SOP for Bottom loading operations at Gantry 1 and Gantry 2 are to be displayed. Location to review display of SOPs in field appropriately for all critical operations / equipments | SOD | Marketing | CZR | 2026-10-31 | POOR COMMUNICATION | 6 | PROCESS SAFETY | S2 | F3 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154529 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154529 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154529 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154529 | AUD-2026-09-2000017404ACN-2026-09-4000154529 | 21 | 21 | 27 | 80 | 1 | -4 | 61 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Trafffic management strictly implemented by security near approach road. Strict wheelchoke compliance ensured by patrolling security. | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154530 | Closed | Sreelal P P | 2026-10-01 | Alertness of security verified and found to be satisfactory | 2.4 | Security alertness checked (night-halt / surprise checks) | 1845 | IRUMPANAM TERMINAL | Location to ensure traffic management along approach road | SOD | Marketing | CZR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017404ACN-2026-09-4000154530 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154530 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154530 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017404ACN-2026-09-4000154530 | AUD-2026-09-2000017404ACN-2026-09-4000154530 | 21 | 21 | 27 | 80 | 1 | -4 | 57 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Location has Tested the network including the functionality of Solenoid Valves | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154531 | Closed | Sreelal P P | 2026-10-01 | Foam Inventory is adequate as per OISD STD 244 and 117. AFFF Requirement - 8.08 AFFF Available - 9.85KL ARAFFF Requirement - 8.88KL ARAFFF Available - 19.5KL | 2.9 | Foam inventory verified | 1845 | IRUMPANAM TERMINAL | Auto-filling functionality of the foam system to be checked, tested, and confirmed | SOD | Marketing | CZR | 2026-10-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 6 | ASSET INTEGRITY | S3 | F2 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154531 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154531 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154531 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154531 | AUD-2026-09-2000017404ACN-2026-09-4000154531 | 21 | 21 | 27 | 80 | 1 | -4 | 61 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Stock accounting being done with atmost care and importance. Location has laid new unloading line for solvent from Bay 16 owing to the issue with the old line | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154533 | Closed | Sreelal P P | 2026-10-01 | Location is in line with the SOD HQO circulars and performing Auto reconciliations. Auto reconciliation being done | 3.8 | Auto vs Manual reconciliation checked | 1845 | IRUMPANAM TERMINAL | 1. Loctaion to carry out stock accounting with due importance. Stock loss is to be reviewed critically, on a daily basis and all possible setps are to be taken timely in case of loss in any product. | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-09-30 | AUD-2026-09-2000017404ACN-2026-09-4000154533 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154533 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154533 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154533 | AUD-2026-09-2000017404ACN-2026-09-4000154533 | 21 | 21 | 27 | 80 | 1 | -4 | 57 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Boundary wall repair carried vide PO placed on Hitech Engineers | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154535 | Closed | Sreelal P P | 2026-10-01 | Boundary wall repairs are in progress towards LPG TT parking side. | 3.16 | Earth pits / boundary / vegetation control checked | 1845 | IRUMPANAM TERMINAL | Location to complete Boundary wall repair as per inspection report | SOD | Marketing | CZR | 2026-10-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-10-31 | AUD-2026-09-2000017404ACN-2026-09-4000154535 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154535 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154535 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017404ACN-2026-09-4000154535 | AUD-2026-09-2000017404ACN-2026-09-4000154535 | 21 | 21 | 27 | 80 | 1 | -4 | 61 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Tender flloated for procurement of valves. Project will be completed within timeline | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154538 | Closed | Sreelal P P | 2026-10-01 | Reviewed project status of Valve procurement | 4.3 | 2 projects to be completed for which tendering is under progress | 1845 | IRUMPANAM TERMINAL | Take action for timely completion of approved NPCB Projects viz. Overfill protection for UG Tanks, HOVs for Hydrant line etc. Tendering and PO placement is to be ensured for all approved NPCB projects | SOD | Marketing | CZR | 2026-12-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-12-30 | AUD-2026-09-2000017404ACN-2026-09-4000154538 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154538 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154538 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017404ACN-2026-09-4000154538 | AUD-2026-09-2000017404ACN-2026-09-4000154538 | 21 | 21 | 27 | 80 | 1 | -4 | 70 | 57
TILKAN RAVINDRA KUMAR | 2026-10-02 | Sreelal P P | 2026-10-01 | Location has uploaded the details of surplus assets in assetmanagement portal | GM O&D AUDIT Q2 26-27 AT IUMPANAM TERMI | 2026-09-02 16:30 | AUD-2026-09-2000017404 | 2026-09-02 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000154539 | Closed | Sreelal P P | 2026-10-01 | Top loading arms removed from Gantry are placed at one place. | 4.5 | scrap disposal progress reviwed/scrap free environment checked. | 1845 | IRUMPANAM TERMINAL | Take action for timely disposal of the material | SOD | Marketing | CZR | 2026-12-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-12-30 | AUD-2026-09-2000017404ACN-2026-09-4000154539 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017404ACN-2026-09-4000154539 | 2026-09-02 16:30 | 47.0663 | 396 | >20 | AUD-2026-09-2000017404 - ACN-2026-09-4000154539 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017404ACN-2026-09-4000154539 | AUD-2026-09-2000017404ACN-2026-09-4000154539 | 21 | 21 | 27 | 80 | 1 | -4 | 70 | 57
|  | KAMLESH SAHU | 2026-10-02 | Calibration tower has commissioned and under operation | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153278 | Completed | KAMLESH SAHU | 2026-10-02 | New calibration Tower was not commissioned | 1.4 | Earlier action points status checked | 1528 | RAIPUR IRD-II | Advised to commissioned the calibration tower and shift the activity to this Depot | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153278 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153278 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153278 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153278 |  | AUD-2026-09-2000017611ACN-2026-09-4000153278 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | As discussed, Location has issued needful instructions to concern officers and workman and same is monitering on daily basic. As a result, gantry performance has graduarlly improved | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153280 | Completed | KAMLESH SAHU | 2026-10-02 | Improvement plan with smooth transition of important portfolio of officers was discussed with LIC in view of transfer of officers | 1.8 | Improvement plans discussed | 1528 | RAIPUR IRD-II | TT gantry perfromance improvement was discussed as per SBU targets given | SOD | Marketing | ECZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153280 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153280 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153280 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153280 |  | AUD-2026-09-2000017611ACN-2026-09-4000153280 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Training to security has imparted on 23 Aug 2026 and refresher and Practical training demostrate on workman,security and field officer on 24 Sept 26 | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153281 | Completed | KAMLESH SAHU | 2026-10-02 | In the evening after the closer of the operation , HLVR was operated by New Officer . Security on the duty were not confident . | 2.2 | Double contingency scenario simulated; observations recorded | 1528 | RAIPUR IRD-II | Security needs the hands on training to operate all the fire fighting equipments . | SOD | Marketing | ECZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | EMERGENCY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153281 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153281 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153281 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153281 |  | AUD-2026-09-2000017611ACN-2026-09-4000153281 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Location has registered 100 % employee in CLMS Portal. Although newly joined staff will continue to register | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153283 | Completed | KAMLESH SAHU | 2026-10-02 | Security alertness checked at various post | 2.4 | Security alertness checked (night-halt / surprise checks) | 1528 | RAIPUR IRD-II | CLMS needs the effective implimentation for all the contract labour | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153283 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153283 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153283 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153283 |  | AUD-2026-09-2000017611ACN-2026-09-4000153283 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Location is ensure the dip checking of 100% Tank truck till file note for dip ellimination executed | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153285 | Completed | KAMLESH SAHU | 2026-10-02 | Post loading Dip Checked 2 TTs ( CG12BE0406 & CG07CU0599 ) at Raipur IRD II & 2 TTs ( MH05EL7230 & MH05EL7231 ) at Raipur IRD I. Dip found Ok for all TT except TT no CG07CU0599, in which 2.0 cm ( C1 +4mm, C2 +6mm, C3 +1cm ). TT was released after removing excessproduct as per SOP | 3.2 | Post-loading dip checks verified | 1528 | RAIPUR IRD-II | Location to ensure stabilisation of TT gantry & Dip elimination FN by Jan 27. Till the stabilisation Dip checking record to be maintained for all the TT | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153285 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153285 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153285 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153285 |  | AUD-2026-09-2000017611ACN-2026-09-4000153285 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Location has completed all pending route correction and continue to correct wherever anomolies will observe | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153286 | Completed | KAMLESH SAHU | 2026-10-02 | Checked and Deviation Found. | 3.3 | VTS deviations reviewed | 1528 | RAIPUR IRD-II | route correction in some cases | SOD | Marketing | ECZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153286 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153286 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153286 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153286 |  | AUD-2026-09-2000017611ACN-2026-09-4000153286 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Location has seggregate the usable material and scarp items | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153288 | Completed | KAMLESH SAHU | 2026-10-02 | Several project material lying idle like valves , fittings , strainer , etc which was shifted from other locations by project team | 3.9 | Abnormal variations / unused assets reviewed | 1528 | RAIPUR IRD-II | Location advised to seggregate the material in usable and scrap items and take action | SOD | Marketing | ECZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153288 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153288 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153288 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153288 |  | AUD-2026-09-2000017611ACN-2026-09-4000153288 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | KAMLESH SAHU | 2026-10-02 | Wate cooler provided | RAIPUR-2 -Q2-SENIOR MGMT INSPECTION | 2026-08-28 18:00 | AUD-2026-09-2000017611 | 2026-08-26 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153297 | Completed | KAMLESH SAHU | 2026-10-02 | No water cooler provided for TT crew | 6.3 | Driver amenity room | 1528 | RAIPUR IRD-II | to be provided . Budget request to be given | SOD | Marketing | ECZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017611ACN-2026-09-4000153297 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017611ACN-2026-09-4000153297 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-09-2000017611 - ACN-2026-09-4000153297 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017611ACN-2026-09-4000153297 |  | AUD-2026-09-2000017611ACN-2026-09-4000153297 | 21 |  | 27 | 80 | 3 | 3 | 57
|  | ANKIT KUMAR | 2026-10-02 | ALl improvement plans are being implemented including budget proposal submitted | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142964 | Completed | ANKIT KUMAR | 2026-10-02 | a. TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlier VC's with all Location TAS officer. b. Shift officers - Making TW Gantry leakage free. c. Maintenace officer - Seeking budget for tank and pipeline maintenance and repair jobs d. Transportation - Maintaining Annex-1 of VTS circular and ensuring that all TT's are covered for VTS and EM locking check on daily monthly basis with record e. TT Gantry officer - Improvement in LPM. f. Ch. Mgr. Opns.- Cycle time of the location was 64' during Apr'26 and during May'26 it is hovering around 60'. Cycle time of the location to be improved to 52' as per the AOP target. | 1.8 | Improvement plans discussed | 1216 | BAHADURGARH TERMINAL | a. The TAS Officer should focus on improving TT exit time and LPM at the location. b. Expedite Physical verification of pipeline quantity and record same. c. Initiate the process for seeking the required budget for tank and pipeline maintenance and repair works. d. Annexure-1 of the VTS circular to be maintained and ensure that all TTs are covered under VTS. Monthly checks for VTS functionality and EM locking should be carried out and proper records maintained. e. The TT Gantry Officer should take necessary steps to improve the LPM at the gantry to enhance operational efficiency. f. Ch. Mgr. Opns. to undertake wholistic review of factors impacting cycle time and bring it in line with the AOP target. | SOD | Marketing | NZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142964 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142964 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142964 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142964 |  | AUD-2026-06-2000013589ACN-2026-07-4000142964 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | ESD made functional and being checked quarterly | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142973 | Completed | ANKIT KUMAR | 2026-10-02 | 1. ESD - Tot 23 No of ESD available at the location out of which 06 nos are soft ESD. As per OISD 244 clause no. 9.3(C)-(iii) ESD System shall be checked during each fire drill conducted with full shut down and records shall be maintained. However, location is mentioning observations related to ESD performance (including timings & delays in operation) in the fire-drill report. 2. Functionality of ESDs were checked during the fire drill done on 21.05.2026. ESD-09 at bay no. 9 of TLF Gantry# 2, ESD-03 at TLF Gantry#1 & ESD-07 at Product Pump House as well as soft ESD from System were operated during the drills. However, thru none of these actuations, Fire Emergency Siren could not get activated. | 2.11.04 | HVLR/RSFPS/HCD/ESD functionality checked | 1216 | BAHADURGARH TERMINAL | 1. Location to ensure recording of ESD performance in the fire drill report picking up timings recorded in the TAS system to maintain congruity of records. 2. Location to maintain ESDs in prime working condition at all the time so that the intended operations are performed on actuation of any of them. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142973 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142973 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142973 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142973 |  | AUD-2026-06-2000013589ACN-2026-07-4000142973 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Hazardous Endorsement are being insured in DL physcial copy or online copy | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142974 | Completed | ANKIT KUMAR | 2026-10-02 | It has been observed that No Trained Security personnel is having HAZ endorsement to move TT in Gantry. However, DCT/TPT are havingHAZ endorsement to move TT from gantry 50-100 m in case of emergency. Further, on checking records of driver maintained at location it was found that few TT drivers of Haryana were not having HAZ Endorsed Licence although Training certificates for carrying Dangerous & Hazardous Goods is available in records. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1216 | BAHADURGARH TERMINAL | Endorsement of Hazardous goods carrying authorisation on driving license of each TT driver to be taken up with authorities. | SOD | Marketing | NZ | 2026-07-31 |  | 1 |  | S1 | F1 | 2026-07-31 | AUD-2026-06-2000013589ACN-2026-07-4000142974 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142974 | 2026-09-05 | 44.7538 | 333 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142974 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142974 |  | AUD-2026-06-2000013589ACN-2026-07-4000142974 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Six monthly Check camp for TT Crew and Contract Workmen organised in June'26 | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142975 | Completed | ANKIT KUMAR | 2026-10-02 | Color blindness, night blindness & eye sight check was performed for all the TT crew and contract worker by the location during thehealth check-up camp organized by the location in Sep'25. Next health check-up camp is planned by the location in June'26. | 2.16 | Eyesight / colour-blindness awareness checked | 1216 | BAHADURGARH TERMINAL | Location to obtain details of findings during the health check-up from the agency engaged for it in excel format. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142975 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142975 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142975 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142975 |  | AUD-2026-06-2000013589ACN-2026-07-4000142975 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Lux level report format changed both OISD 244 and PNGRB refrence recorded | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142966 | Completed | ANKIT KUMAR | 2026-10-02 | Reviewed Lux level recordings available at the location on 16/03/26, 15/04/26 & 17/05/26. Following are the observations: 1. The format doesn't have provision for recording date & time of observations. 2. There is no mention in the report about inference drawn & action required there upon, if any. 3. The name and designation of the person recording the readings as well the controlling officer is missing. On reviewing all the recorded readings, it is observed that the lux levels recorded are adequate as against the requirement mentioned for the location in OISD 244. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1216 | BAHADURGARH TERMINAL | Format for recording the lux levels to be suitably modified. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142966 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142966 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142966 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142966 |  | AUD-2026-06-2000013589ACN-2026-07-4000142966 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | All open VA alerts are being closed in Novex on daily basis | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000142970 | Completed | ANKIT KUMAR | 2026-10-02 | 1. All the 82 CCTVs which are VA enabled are integrated with the VA system. Out of these 82 cameras, 2 are not accessible from the VA server as per the reply from M/s. Avathon who is managing the VA portal. This status has been verified on 20th May'26 @ 17:40 hrs. 2. Further, 550 open VA alerts are reflecting in the NOVEX portal all pertaining to 8th & 9th Apr'26. Location has written mail to M/s. Avathon for dropping of these alerts (as per the location, all these alerts are false alerts). | 2.7 | VA alerts checked / analysed | 1216 | BAHADURGARH TERMINAL | 1. Location to get all the 82 cameras which are hooked to the VA system on board for video analytics 2. Location to take up with digital team HQO for dropping of false alerts. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142970 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142970 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142970 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142970 |  | AUD-2026-06-2000013589ACN-2026-07-4000142970 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Hzaradous Endorsement are being ensured in DL physcial copy or online copy | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142976 | Completed | ANKIT KUMAR | 2026-10-02 | Part B check was done on HR61D7192, of M/s New Diamond logistic on 20/05/2026. Following are the observations 1. Exhaust of the engine was found near the fuel tank of the vehicle without double protection. 2. Drain pipe to be extended to the bottom of the tank 3. Toe Guard from the TT top was found not extended upto bottom of the TT. 4. HAZ Endorsed licence was available with the TT driver valid 27.10.2027 Discipline: During checking of ID cards of TT crew at the TLF Gantry, it was found that few of the helpers were doing duty on another TT on temporary permission. During interaction, it came out that this is a regular practice. | 3.1 | TT fittings & discipline checked | 1216 | BAHADURGARH TERMINAL | 1. Double protection on exhaust of vehicle to be ensured wherever it is near to its fuel tank. 2. Drain pipes from TT top to be ensured extended to the bottom of the TT. Crew Discipline: Dedicated trained crew (driver and helper) to be ensured for each TT during loading inside the location premises as well as enroute to the retail outlets. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142976 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142976 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142976 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142976 |  | AUD-2026-06-2000013589ACN-2026-07-4000142976 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Daily Auto Reco is being carried out for improving TFMS% | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142980 | Completed | ANKIT KUMAR | 2026-10-02 | Avg. TFMS-SAP reconciliation % for the month of April 26 is 96%. | 3.1 | TFMS/SAP reconciliation checked | 1216 | BAHADURGARH TERMINAL | Location to further improve the % of TFMS-SAP reconciliation. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142980 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142980 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142980 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142980 |  | AUD-2026-06-2000013589ACN-2026-07-4000142980 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Novex alarms being closed on daily basis | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142981 | Completed | ANKIT KUMAR | 2026-10-02 | Verified last 3 months TAS alerts in NOVEX portal on 21.05.2026 @ 16:39 hrs. and one critical alert pertaining to safety PLC communication error dtd 15.5.26 which was attended on same day but alert needs to be closed by location. | 3.12 | Critical alarms checked & corrective actions reviewed | 1216 | BAHADURGARH TERMINAL | Location to close all the open alerts in NOVEX and confirm back to zone. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142981 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142981 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142981 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142981 |  | AUD-2026-06-2000013589ACN-2026-07-4000142981 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Grass cutting and vegetation degrowth spray are being carried out extensively | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142982 | Completed | ANKIT KUMAR | 2026-10-02 | Housekeeping of some areas are requiring major upkeep which were discussed during field round with location team. Areas requiring immediate attention are OWS, Tank Farm Area, Pipeline Manifolds for overgrown grass, repainting of pipelines wherever corosion is found. | 3.15.01 | Housekeeping & PPE usage checked | 1216 | BAHADURGARH TERMINAL | Housekeeping to be properly maintained. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142982 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142982 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142982 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142982 |  | AUD-2026-06-2000013589ACN-2026-07-4000142982 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Grass cutting and vegetation degrowth spray are being carried out extensively | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142985 | Completed | ANKIT KUMAR | 2026-10-02 | Vegetation Control - At many places Encroaching/Overgrown vegetation observed along the boundary wall. | 3.16.03 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | Vegetation control measures to be taken by the location | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142985 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142985 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142985 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142985 |  | AUD-2026-06-2000013589ACN-2026-07-4000142985 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | No pending points | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142988 | Completed | ANKIT KUMAR | 2026-10-02 | SSA - 03-10 Sep 2025 - Total observations are 34 in no. and as on date all 34 points are complied. | 3.18.04 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-06-2000013589ACN-2026-07-4000142988 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142988 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142988 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142988 |  | AUD-2026-06-2000013589ACN-2026-07-4000142988 | 21 |  | 27 | 80 | 9 | 9 | 83
|  | ANKIT KUMAR | 2026-10-02 | Manual reconciliation are being carried out in cases as per SOP and reasons being recorded | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142978 | Completed | ANKIT KUMAR | 2026-10-02 | Out of total 2479 tank reconciliations done during the period 23rd Feb'26 to 20th May'26, only 169 instances of manual dip entries are there in SAP. Reconciliation based on auto dip was done for 93.18% of tanks during the period. Out of the 169 reconciliations done based on manual dips, 59 instances were for month end reconciliations when manual dip entries were mandated by HQO. 110 instancesare pertaining to reconciliations done on manual dips on days other than month ends. Location's control room officers are entering the reasons for manual dip reconciliation at daily day end closing in the google spreadsheet provided by zonal operations as well asHQO Opns. | 3.8 | Auto vs Manual reconciliation checked | 1216 | BAHADURGARH TERMINAL | Location to reduce the instance of manual Reconciliation and continue to update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142978 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142978 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142978 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142978 |  | AUD-2026-06-2000013589ACN-2026-07-4000142978 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | Reasons are abnormal gain and loss are being revieewd on daily basis | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000142979 | Completed | ANKIT KUMAR | 2026-10-02 | There are only 8 instances of abnormal variations during the period 23rd Feb'26 to 20th May'26. Reasons for abnormal gain/ loss arefound entered in SAP. | 3.9 | Abnormal variations / unused assets reviewed | 1216 | BAHADURGARH TERMINAL | Location to take necessary precautions in future to avoid instances of abnormal variation (gain/ loss). | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000013589ACN-2026-07-4000142979 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142979 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142979 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142979 |  | AUD-2026-06-2000013589ACN-2026-07-4000142979 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Hydrant Painting line is being carried out | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142989 | Completed | ANKIT KUMAR | 2026-10-02 | Painting of Hydrant Line required at several places in TWG / TFA / and around peripheral sections | 4.1.01 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Hydrant line painting work to be carried out | SOD | Marketing | NZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-06-2000013589ACN-2026-07-4000142989 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142989 | 2026-09-05 | 44.7538 | 425 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142989 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142989 |  | AUD-2026-06-2000013589ACN-2026-07-4000142989 | 21 |  | 27 | 80 | 9 | 9 | 61
|  | ANKIT KUMAR | 2026-10-02 | Sand buckets filled and painting done | SR MGMT INSPECTION BAHADURGARH Q12627 | 2026-06-25 17:30 | AUD-2026-06-2000013589 | 2026-06-25 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000142990 | Completed | ANKIT KUMAR | 2026-10-02 | Sand bucket found to be partially filled with sand near MCC2. Also, painting is required for sand buckets. | 4.1.02 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Ensure sand buckets to be filled adequately and painting to be done | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000013589ACN-2026-07-4000142990 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013589ACN-2026-07-4000142990 | 2026-09-05 | 44.7538 | 332 | >20 | AUD-2026-06-2000013589 - ACN-2026-07-4000142990 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013589ACN-2026-07-4000142990 |  | AUD-2026-06-2000013589ACN-2026-07-4000142990 | 21 |  | 27 | 80 | 9 | 9 | 48
|  | ANKIT KUMAR | 2026-10-02 | All improvement plans are being implemented | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000149677 | Completed | ANKIT KUMAR | 2026-10-02 | a. The TAS Officer should focus on improving TT exit time and LPM at the location. b. Expedite Physical verification of pipeline quantity and record same. b. The TT Gantry Officer should take necessary steps to improve the LPM at the gantry to enhance operational efficiency. f.Location to undertake wholistic review of factors impacting cycle time and bring it in line with the AOP target. | 1.8 | Improvement plans discussed | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149677 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149677 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149677 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149677 |  | AUD-2026-09-2000016768ACN-2026-09-4000149677 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Hazardous Endorsement is being ensured by DL physcial copy or online copy | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149684 | Completed | ANKIT KUMAR | 2026-10-02 | Few DCT/TPT are having HAZ endorsement to move TT from gantry 50-100 m in case of emergency. Further, on checking records of driver maintained at location it was found that few TT drivers of Haryana were not having HAZ Endorsed Licence although Training certificates for carrying Dangerous & Hazardous Goods is available in records. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1216 | BAHADURGARH TERMINAL | Endorsement of Hazardous goods carrying authorisation to be ensured on driving license of each TT driver. | SOD | Marketing | NZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149684 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149684 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149684 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149684 |  | AUD-2026-09-2000016768ACN-2026-09-4000149684 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Six monthly medical camp organised for TT Crew and Contract Workers in June'26 | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000149685 | Completed | ANKIT KUMAR | 2026-10-02 | Color blindness, night blindness & eye sight check was performed for all the TT crew and contract worker by the location during thehealth check-up camp organized by the location in June 26. Specs has been provided to Crew | 2.16 | Eyesight / colour-blindness awareness checked | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-08-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-08-30 | AUD-2026-09-2000016768ACN-2026-09-4000149685 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149685 | 2026-09-05 | 44.7538 | 363 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149685 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149685 |  | AUD-2026-09-2000016768ACN-2026-09-4000149685 | 21 |  | 27 | 80 | 9 | 9 | 52
|  | ANKIT KUMAR | 2026-10-02 | TT fitting are being checked on regular basis | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149686 | Completed | ANKIT KUMAR | 2026-10-02 | TT fittings of 3 Nos TTs were checked | 3.1 | TT fittings & discipline checked | 1216 | BAHADURGARH TERMINAL | 1. Double protection on exhaust of vehicle to be ensured wherever it is near to its fuel tank. 2. Drain pipes from TT top to be ensured extended to the bottom of the TT. 3. In few TTs Gap found between Valve chamber cover. to Be rectified. In ATF TT no HR55 AV0723 Vaove wheel nut found not weled to wheel. To b checked on all TTs and recified Crew Discipline: Dedicated trained crew (driver and helper) to be ensured for each TT during loading inside the location premises as well as enroute to the retail outlets. | SOD | Marketing | NZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149686 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149686 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149686 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149686 |  | AUD-2026-09-2000016768ACN-2026-09-4000149686 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Manual Reco is carried out as per SOP to improve TFMS % | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149689 | Completed | ANKIT KUMAR | 2026-10-02 | Avg. TFMS-SAP reconciliation % for the month of July 26 is 93,7%. | 3.1 | TFMS/SAP reconciliation checked | 1216 | BAHADURGARH TERMINAL | Location to improve the same | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149689 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149689 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149689 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149689 |  | AUD-2026-09-2000016768ACN-2026-09-4000149689 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Grass Cutting activity and vegetation anti growth spray are being done extensively to improve housekeeping | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149690 | Completed | ANKIT KUMAR | 2026-10-02 | Housekeeping of some areas are requiring major upkeep which were discussed during field round with location team. Areas requiring immediate attention are OWS, Tank Farm Area, Pipeline Manifolds for overgrown grass, repainting of pipelines wherever corosion is found. | 3.15 | Housekeeping & PPE usage checked | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-09-30 | HARSH WORKING CONDITIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149690 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149690 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149690 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149690 |  | AUD-2026-09-2000016768ACN-2026-09-4000149690 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Grass Cutting activity and vegetation anti growth spray are being done extensively to improve housekeeping | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149692 | Completed | ANKIT KUMAR | 2026-10-02 | Vegetation Control - At many places Encroaching/Overgrown vegetation observed along the boundary wall. | 3.16 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | XX | SOD | Marketing | NZ | 2026-09-30 | HARSH WORKING CONDITIONS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149692 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149692 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149692 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149692 |  | AUD-2026-09-2000016768ACN-2026-09-4000149692 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Stock loss is being monitored on daily basis | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000149688 | Completed | ANKIT KUMAR | 2026-10-02 | High stock losses in MS, ATF and Etanol and MTO | 3.9 | Abnormal variations / unused assets reviewed | 1216 | BAHADURGARH TERMINAL | Location to closely monitor the same on daily basis and take immediiate corrective action. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149688 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149688 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149688 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149688 |  | AUD-2026-09-2000016768ACN-2026-09-4000149688 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Painting Job is being carried out | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149694 | Completed | ANKIT KUMAR | 2026-10-02 | Painting of Hydrant Line required at several places in TWG / TFA / and around peripheral sections | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Hydrant line painting work to be carried out | SOD | Marketing | NZ | 2026-10-31 | HARSH WORKING CONDITIONS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-10-31 | AUD-2026-09-2000016768ACN-2026-09-4000149694 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149694 | 2026-09-05 | 44.7538 | 425 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149694 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016768ACN-2026-09-4000149694 |  | AUD-2026-09-2000016768ACN-2026-09-4000149694 | 21 |  | 27 | 80 | 9 | 9 | 61
|  | ANKIT KUMAR | 2026-10-02 | Leakages are being attended as and when required basis | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149696 | Completed | ANKIT KUMAR | 2026-10-02 | Tk 1,2and 3 all HSD tanks and minor leakage/sweating is observed from the shell where wind girder welding joint | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | location to attend the same thru cold weld and seek budget for long term repair | SOD | Marketing | NZ | 2027-03-30 | HARSH WORKING CONDITIONS | 5 | ASSET INTEGRITY | S1 | F5 | 2027-03-30 | AUD-2026-09-2000016768ACN-2026-09-4000149696 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149696 | 2026-09-05 | 44.7538 | 575 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149696 | 532 | 8294 | 21 | 8294 | -161 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149696 |  | AUD-2026-09-2000016768ACN-2026-09-4000149696 | 21 |  | 27 | 80 | 9 | 9 | 83
|  | ANKIT KUMAR | 2026-10-02 | Thermography and Insulation testing done | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149698 | Completed | ANKIT KUMAR | 2026-10-02 | Thermography due date in MCC -1 mentioned as 16.3.25 Mat Insulation date due since 29.5.26 to be updated. 500 KVA DG set door broken, Lube oil low. | 4.2 | Maintenance activities reviewed | 1216 | BAHADURGARH TERMINAL | Corrective action to be taken | SOD | Marketing | NZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149698 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149698 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149698 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149698 |  | AUD-2026-09-2000016768ACN-2026-09-4000149698 | 21 |  | 27 | 80 | 9 | 9 | 57
|  | ANKIT KUMAR | 2026-10-02 | Time Extension taken for Fire Engine Project | SMA_BAHADURGARH TERMINAL_Q2 | 2026-08-20 18:00 | AUD-2026-09-2000016768 | 2026-08-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000149699 | Completed | ANKIT KUMAR | 2026-10-02 | There are 6 Projects, one is closed, two time extension is being processed, 3 projects will be completed within schedule time | 4.3 | Project progress reviewed | 1216 | BAHADURGARH TERMINAL | Time extension of two projects to be expedited | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000016768ACN-2026-09-4000149699 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016768ACN-2026-09-4000149699 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-09-2000016768 - ACN-2026-09-4000149699 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000016768ACN-2026-09-4000149699 |  | AUD-2026-09-2000016768ACN-2026-09-4000149699 | 21 |  | 27 | 80 | 9 | 9 | 57
NIMDEO AMIT VINAYAK | 2026-10-03 | ANKIT KUMAR | 2026-08-21 | Necessary ractification made in the same day. Now its functioning well | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125562 | Closed | AGARWAL VIPUL | 2026-03-18 | MEFG - There are 16 Nos of MEFG installed at the Location. MEFG located inside the Dyke wall of TK-13 was operated by Shri. Dinesh Meena. The officer was found to be acquainted with the operation of the MEFG, however water nozzle at 6 O'clock position was was found to be partially choke. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1216 | BAHADURGARH TERMINAL | Proper preventive maintenance of all MEFG's shall be ensured to maintain their operational readiness at all times. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011128ACN-2026-03-4000125562 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125562 | 2026-09-05 | 44.7538 | 397 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125562 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125562 | AUD-2026-03-2000011128ACN-2026-03-4000125562 | 21 | 21 | 26 | 80 | 9 | 9 | 28 | 57
NIMDEO AMIT VINAYAK | 2026-10-03 | ANKIT KUMAR | 2026-08-21 | 15 Approved MOCs have been closed .Remaining will be done | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125573 | Closed | AGARWAL VIPUL | 2026-03-18 | During FY 2025-26, Total 33 Nos of MoC's were raised and 19 MoC's were approved. A total of 14 MOCs are still in submitted stage. | 3.17 | MOC status reviewed | 1216 | BAHADURGARH TERMINAL | MOC to be approved and closer of the same in time bound manner | SOD | Marketing | NZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125573 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125573 | 2026-09-05 | 44.7538 | 397 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125573 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125573 | AUD-2026-03-2000011128ACN-2026-03-4000125573 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 57
NIMDEO AMIT VINAYAK | 2026-10-03 | ANKIT KUMAR | 2026-08-21 | Foam pourer optimum performance enured post retification | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125595 | Closed | NIMDEO AMIT VINAYAK | 2026-10-03 | The foam pourer of TK-10 was operated and it was observed that out of five discharge assemblies, two were operating satisfactorily while three showed reduced output. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The concerned assemblies should be inspected and rectified to ensure proper foam discharge. | SOD | Marketing | NZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125595 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125595 | 2026-09-05 | 44.7538 | 397 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125595 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011128ACN-2026-03-4000125595 | AUD-2026-03-2000011128ACN-2026-03-4000125595 | 21 | 21 | 26 | 80 | 9 | 9 | 31 | 57
|  | SINGH BHOPENDRA | 2026-10-03 | All OISD points closed | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124808 | Completed | SINGH BHOPENDRA | 2026-10-03 | OISD : Total point 24, Pending point: 0, Closure submitted. MDSA: Total point 48, Pending point: 4, EDC: 30.06.2026 SSA: Total point 13, Pending point: 3, EDC: 31.03.2026 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1157 | BAREILLY DEPOT | Location to ensure compliance of open audit observation scheduled for closure in current FY | SOD | Marketing | NUZ | 2026-03-31 | POOR COMMUNICATION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124808 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124808 | 2026-07-16 | 95.7538 | 211 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124808 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011014ACN-2026-03-4000124808 |  | AUD-2026-03-2000011014ACN-2026-03-4000124808 | 21 |  | 26 | 80 | 3 | 3 | 31
|  | SINGH BHOPENDRA | 2026-10-03 | Drain Cleaning work completed | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124818 | Completed | SINGH BHOPENDRA | 2026-10-03 | Oil observed in siding drain | 6.8 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 |  | 1 |  | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124818 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124818 | 2026-07-16 | 95.7538 | 195 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124818 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011014ACN-2026-03-4000124818 |  | AUD-2026-03-2000011014ACN-2026-03-4000124818 | 21 |  | 26 | 80 | 3 | 3 | 28
|  | SINGH BHOPENDRA | 2026-10-03 | Datamine updated | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124803 | Completed | SINGH BHOPENDRA | 2026-10-03 | Surplus unused product pumps are available at location. Updated in data mine. Same is required to be updated in surplus asset portal. | 3.9 | Abnormal variations / unused assets reviewed | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 |  | 1 |  | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124803 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124803 | 2026-07-16 | 95.7538 | 195 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124803 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011014ACN-2026-03-4000124803 |  | AUD-2026-03-2000011014ACN-2026-03-4000124803 | 21 |  | 26 | 80 | 3 | 3 | 28
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155086 | Open |  |  | 1. HLSA recommendations w.r.t. Officers pick and drop is pending. 2. Compliance to PCSA is pending. | 1.3 | Pending issues reviewed | 1313 | BAITALPUR DEPOT | Location to comply with the audit observation as per time line | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-10-2000017616ACN-2026-10-4000155086 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155086 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155086 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155086 |  | AUD-2026-10-2000017616ACN-2026-10-4000155086 | 21 |  | 27 | 80 | 1 | 1 | 70
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155087 | Open |  |  | Leval-II Mock Drill was conducted at Baitalpur on 31-08-2026 with scenerio of Lakage and Fire in HSD -02 pump in TLF pump house. Observations: 1. Foam Monitor was operated prior to insertion of Foam pickup tube 2. Hose handling was observed to be improper | 2.1 | Fire drill conducted in last 6 months (surprise) | 1313 | BAITALPUR DEPOT | Location to take corrective action. | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155087 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155087 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155087 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155087 |  | AUD-2026-10-2000017616ACN-2026-10-4000155087 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155088 | Open |  |  | Lux level checked during the Night Inspection on 24.09.2026 and found to be adequate as per standard. However, 5 nos of street lights were found non functional within the premises. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017616ACN-2026-10-4000155088 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155088 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155088 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155088 |  | AUD-2026-10-2000017616ACN-2026-10-4000155088 | 21 |  | 27 | 80 | 1 | 1 | 65
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155089 | Open |  |  | Yes, ERDMP of Baitalpur reviewed and is updated. Next revision due in 11/09/2028. Scenerios related to L-I, L-II and L-III were also reviewed and observed that all scenerios are relevant to the location. Further monthly Mock drill reports has been reviewed and location is covring all the scenerios in line with ERDMP. During review it was observed that HIRA/QRA is not available at he locationwith the change in facility | 2.5 | Emergency response preparedness reviewed | 1313 | BAITALPUR DEPOT | HAZOP, QRA study to be conducted with the change in facility | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-10-2000017616ACN-2026-10-4000155089 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155089 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155089 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155089 |  | AUD-2026-10-2000017616ACN-2026-10-4000155089 | 21 |  | 27 | 80 | 1 | 1 | 70
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155090 | Open |  |  | Tot. 52 no of CCTV's are available at the location out of which only 46 CCTV's are working. Remaining 6 no of CCTV which are not working needs repair. Random check was carried out to ensure backup recording of 92 days and found available | 2.6 | CCTV functioning checked | 1313 | BAITALPUR DEPOT | Location to take corrective action and get 6 nos of CCTV camera repaired which are also associated with VA system | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155090 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155090 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155090 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155090 |  | AUD-2026-10-2000017616ACN-2026-10-4000155090 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155091 | Open |  |  | Boundary Wall - The boundary wall requires civil repair along the external periphery where ever required. At several locations, theplaster has deteriorated and is found to be dislodged. The concertina coil installed along the periphery is intact, except at two locations, i.e., near TK-07 and the scrap yard, where repair is required. | 3.16 | Earth pits / boundary / vegetation control checked | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017616ACN-2026-10-4000155091 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155091 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155091 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155091 |  | AUD-2026-10-2000017616ACN-2026-10-4000155091 | 21 |  | 27 | 80 | 1 | 1 | 65
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155092 | Open |  |  | OISD - The last OISD audit was conducted during 19–21 Sep’23. All 49 observations complied. T4S - The last T4S audit was conductedduring 06–08 April’26. A total of 23 observations were raised. 11 observations complied. MDSA/Comprehensive Audit - The last Comprehensive audit was conducted during 23-26 Sep'25. A total of 50 observations were raised, 47 observations complied, 3 in completed state SSA - Last SSA was conducted during Sep'25. A total of 28 observations were raised, 27 complied and 1 in completed state HLSA- A total of 11 observations were raised, 10 complied and 1 in pending state | 3.18 | OISD/MDSA/SSA/T4S/HLSA compliance reviewed | 1313 | BAITALPUR DEPOT | Expedite compliance of all the pending audit observations through close monitoring | SOD | Marketing | NCR | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-10-2000017616ACN-2026-10-4000155092 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155092 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155092 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155092 |  | AUD-2026-10-2000017616ACN-2026-10-4000155092 | 21 |  | 27 | 80 | 1 | 1 | 70
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155093 | Open |  |  | Fire Alarm panel showing continuous alarm at Hi level. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Logic for High alarm is to be reviewed and modified as per standard practice | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155093 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155093 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155093 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155093 |  | AUD-2026-10-2000017616ACN-2026-10-4000155093 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155094 | Open |  |  | Various SOPs are about to get expire as per 3 yrs philosophy of the location | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Corrective action to be taken for SOP revision. | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155094 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155094 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155094 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155094 |  | AUD-2026-10-2000017616ACN-2026-10-4000155094 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155095 | Open |  |  | Ammendment in Factory Licence is pending. Application has been submitted already. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Corrective action to be taken for grant of ammended factory Licence | SOD | Marketing | NCR | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017616ACN-2026-10-4000155095 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155095 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155095 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155095 |  | AUD-2026-10-2000017616ACN-2026-10-4000155095 | 21 |  | 27 | 80 | 1 | 1 | 65
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155096 | Open |  |  | Drain lines near sample room area found choked | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155096 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155096 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155096 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155096 |  | AUD-2026-10-2000017616ACN-2026-10-4000155096 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155097 | Open |  |  | Housekeeping in MCC room is not up to the mark. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155097 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155097 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155097 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155097 |  | AUD-2026-10-2000017616ACN-2026-10-4000155097 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155098 | Open |  |  | in MCC room, entry point of power cable found to be unsealed | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155098 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155098 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155098 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155098 |  | AUD-2026-10-2000017616ACN-2026-10-4000155098 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155099 | Open |  |  | Near Sample room, body shower found to be un-operational due to broken pipe connection | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155099 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155099 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155099 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155099 |  | AUD-2026-10-2000017616ACN-2026-10-4000155099 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155750 | Open |  |  | During random checking, at Bay no 7 & 8 only single harness was found. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1313 | BAITALPUR DEPOT | Location to take corrective action | SOD | Marketing | NCR | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017616ACN-2026-10-4000155750 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155750 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155750 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155750 |  | AUD-2026-10-2000017616ACN-2026-10-4000155750 | 21 |  | 27 | 80 | 1 | 1 | 61
[5 empty] | ZONAL INSPECTION BAITALPUR Q2 | 2026-09-26 17:30 | AUD-2026-10-2000017616 | 2026-09-24 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155751 | Open |  |  | LPR for CCTV procurement and VHF procurement is in progress | 4.3 | Project progress reviewed | 1313 | BAITALPUR DEPOT | Expedite the tendering process for CCTV and VHF procurement to ensure timely finalization and installation. | SOD | Marketing | NCR | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017616ACN-2026-10-4000155751 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017616ACN-2026-10-4000155751 | 2026-09-26 17:30 | 23.0247 | 455 | >20 | AUD-2026-10-2000017616 - ACN-2026-10-4000155751 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017616ACN-2026-10-4000155751 |  | AUD-2026-10-2000017616ACN-2026-10-4000155751 | 21 |  | 27 | 80 | 1 | 1 | 65
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.10 ENGAGEMENT & COMMUNICATION | ACN-2026-10-4000155477 | Open |  |  | a) A structured monitoring system to be ensured to track TT exit time and LPM on a daily basis, with periodic review by location. b) A monthly compliance checklist shall be institutionalized for VTS coverage and EM locking verification of all TTs. c) A preventive maintenance and inspection schedule shall to be followed for all critical field equipment, with records maintained and periodically audited to ensure operational readiness. d) Budget requisitions shall be initiated in a timely manner, with systematic follow-up to ensure prompt approval and disbursement of funds. | 1.1000000000000001 |  | 1341 | HISAR TERMINAL | a) A structured monitoring system to be ensured to track TT exit time and LPM on a daily basis, with periodic review by location. b) A monthly compliance checklist shall be institutionalized for VTS coverage and EM locking verification of all TTs. c) A preventive maintenance and inspection schedule shall to be followed for all critical field equipment, with records maintained and periodically audited to ensure operational readiness. d) Budget requisitions shall be initiated in a timely manner, with systematic follow-up to ensure prompt approval and disbursement of funds. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155477 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155477 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155477 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155477 |  | AUD-2026-10-2000017909ACN-2026-10-4000155477 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155478 | Open |  |  | On-site Mock fire drill was conducted on 17th Sep'26 forming a double contingency scenario, one at Tank farm area near TK4 and other at near TT Gantry Bay No 8. District Fire Tender and Medical aid did not arrive at site. Mutual aid members from RhBhPL arrived atthe site. Areas of Improvement: 1. There was much delay in Rescue operations, which need to be Quick and Effective. 2. Pressure in SCABA cylinder was only 60 Bar, way too low to be used in any situation 3. Coordination between the teams needs to be strengthened. 4. Reaction time needs to be reduced by each team, like movement of Emergency Trolley. | 2.2000000000000002 | Double contingency scenario simulated; observations recorded | 1341 | HISAR TERMINAL | Corrective actions to be taken. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155478 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155478 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155478 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155478 |  | AUD-2026-10-2000017909ACN-2026-10-4000155478 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155479 | Open |  |  | Location is carrying out lux level monitoring on monthly basis. From the records available, lux levels were checked on 10.04.2026, 12.05.2026, 15.06.2026, 14.07.2026, 13.08.2026 & 11.09.2026 during H1: 2026-27. In all these reports, lux levels are recorded lower than the required level in Control Room & the TT parking area with remarks LED light not working + Cable fault. Corrective action taken is not recorded in the report. Further, comprehensive checking of lux level was done during the comprehensive audit of the location during Sep'26 and its findings were as below: (a) Lux Levels are inadequate in Fire Pump House at 65 only, Admin building at 250 only, Control room at 250 aganist 400. 8 aganist 10 in TT Parking area. Apart from these night inspection was carried out during this visit on 28.09.2026 and some street lights near the emergency gate were found non-operational. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1341 | HISAR TERMINAL | a) Lux levels as per the norms to be maintained in all the operating areas. b) Records maintained should be entered with the follow-up action taken with date for closure of findings below the minimum lux level norms. | SOD | Marketing | NZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017909ACN-2026-10-4000155479 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155479 | 2026-09-30 17:00 | 19.0455 | 455 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155479 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155479 |  | AUD-2026-10-2000017909ACN-2026-10-4000155479 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155480 | Open |  |  | Surprise visit was done at terminal around 2300 hours on 28/09/2026 and found all security guards in alert position. Security shiftwas headed by Head guard Sh. Sukendar along with Guards Jitendra Punia, Satyawan & Hoshiyar Singh. During the inspection, HVLR#1 was operated by the guard Satyawan. The equipment could not discharge water/ foam when operated from the remote panel. However, after relieving the hydrant pressure from the adjioning WCFM, the equipment started discharging. Apparently, the pneumatic pressure was not adequate to overcome the hydrant pressure to open the butterfly valve. Location officers perform Night Surprise inspection and records pertaining to same was found at the main gate register. However, the night inspection records are not being filled deligently with some informations like names of the guards manning the terminal not being recorded. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1341 | HISAR TERMINAL | Location to look into the root cause of non-operating of the HVLR from the remote panel and take corrective action to avoid repetition of such instances. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155480 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155480 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155480 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155480 |  | AUD-2026-10-2000017909ACN-2026-10-4000155480 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155481 | Open |  |  | Total 60 CCTVs are installed covering entry/ exit gate, periphery of installation and all critical operating areas (viz. Tank farm,TT gantry, product pump house, exchange pit, fire water pump house etc.). Monitoring done on continuous basis with record keeping. 10 Camera are not working as on date (29/09/2026). Also 92 days CCTV recording is available. Random recording checked for 29.06.2026and found available. | 2.6 | CCTV functioning checked | 1341 | HISAR TERMINAL | Faulty cameras to be made functional. | SOD | Marketing | NZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017909ACN-2026-10-4000155481 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155481 | 2026-09-30 17:00 | 19.0455 | 455 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155481 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155481 |  | AUD-2026-10-2000017909ACN-2026-10-4000155481 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155482 | Open |  |  | During the Visit, Access control at main gate as well as entry to the licensed area was checked and found to be not-functional. | 2.8 | Access control systems checked | 1341 | HISAR TERMINAL | Corrective action needs to be taken. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155482 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155482 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155482 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155482 |  | AUD-2026-10-2000017909ACN-2026-10-4000155482 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155483 | Open |  |  | HCD - Total 6 nos. of open path type HCD and 10 nos. of point type HCD provided at various places of potential leak sources. Total 16 Nos. of HCD available at the location. Open path HCD of Product Pump House was checked with filters of 20% of LEL and 60% of LEL. However, the 20% filter could only achieve 19.8% of LEL simulation thus not generating field as well as Control Room Alarms (audioas well as visual). 60% filter could achieve only 54% of LEL simulation with alarms generated in field as well as control room. Open path HCD provided in the maniford area outside the MS dyke is yet to be commissioned | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1341 | HISAR TERMINAL | Location to ensure availability of proper filters for simulation of open path HCDs. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155483 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155483 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155483 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155483 |  | AUD-2026-10-2000017909ACN-2026-10-4000155483 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155484 | Open |  |  | Total 18 Nos of ESD provided at the follwoing locations:- 1. Control Room 2. TM Room 3. Planning Room 4. TLF Gantry Bay06 5. TLF Gantry Bay02 6. TLF Gantry Bay10 7. TLF Gantry Bay16 8. TLF PH Near BD Pump 9. TLF PH Near ADD Skid 10. VRU Area 11. HSD Tank 01 12. HSD Tank 03 13. MS Tank 04 14. MS Tank 05 15. ETH Tank 07 16. ETP Area 17. Near MCC Room 18. Visitor Room Multidirection board for easy identification of ESD03 provided at TT in gate is not available Functionality of ESD was checked during On-site Mock drill conducted on 17/09/2026 in the presence of the Comprehensive Safety Audit team and was found okay. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1341 | HISAR TERMINAL | Multidirection sign board for easy identification of ESD03 at TT in gate to be provided. | SOD | Marketing | NZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-10-2000017909ACN-2026-10-4000155484 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155484 | 2026-09-30 17:00 | 19.0455 | 455 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155484 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155484 |  | AUD-2026-10-2000017909ACN-2026-10-4000155484 | 21 |  | 27 | 80 | 0 | 0 | 65
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155485 | Open |  |  | Part B Check was done on TT no HR 57A 1762. Total 7 Nos NCs issued | 3.1 | TT fittings & discipline checked | 1341 | HISAR TERMINAL | NCs to be complied | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155485 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155485 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155485 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155485 |  | AUD-2026-10-2000017909ACN-2026-10-4000155485 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155486 | Open |  |  | Post loading dip checks were performed on four TTs viz.. HR56C9751, HR39C7980, HR39E1582 & HR57B1450, during the visit and variation in only 1 chamber was found of -1.0mm (within tolerable limit). Dip rod measurements for all the TTs were also carried out and physical variation were found to be within tolerable limits. However, in case of TT# HR56C9751, the calibration certificate was found to have mention of its 3 chambers having capacity of 4000L each whereas as per the PESO drawing the chambers are physically having capacity of 4000L, 5000L & 5000L. Apparently, the calibration certificate issued by the W&M official is wrong. | 3.2 | Post-loading dip checks verified | 1341 | HISAR TERMINAL | Location to exercise strict monitoring of the W&M certificate of each TT after calibration to avoid wrong issuance by the W&M official. The particular certificate to be got corrected. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155486 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155486 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155486 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155486 |  | AUD-2026-10-2000017909ACN-2026-10-4000155486 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155487 | Open |  |  | Check for 5% VTS deviation is being done by the location and has been reviewed during visit | 3.3 | VTS deviations reviewed | 1341 | HISAR TERMINAL | Proper record for 5 % daily check and 100% monthly check to be made | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155487 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155487 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155487 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155487 |  | AUD-2026-10-2000017909ACN-2026-10-4000155487 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155488 | Open |  |  | Check for 5% EM locks is being done by the location and has been reviewed during visit | 3.5 | EM Lock SOP compliance verified | 1341 | HISAR TERMINAL | Proper record for 100% monthly check to be made | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155488 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155488 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155488 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155488 |  | AUD-2026-10-2000017909ACN-2026-10-4000155488 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155489 | Open |  |  | 1. There are a total of 230 instances of local loading during the period 1st Jul'26 to 29th Sep'26 all with PROVER writted under Truck No. column except in case of one instance on 8th Aug'26. Location is maintaining day-wise local loading report duly signed by TAS Officer. However, signature of LIC is missing on this particular report although MFM Vs. BCU Vs. Invoice quantity report are beingsigned by the LIC on daily basis. 2. Bay Re-Assignment was also verified for the period 1st Jul'26 to 29th Sep'26. During this period, locations carried out 18 cases of Bay Re-Assignments. Last bay reassigment during the period was carried out on 12.09.2026- Print-out of the same duly signed by the TAS officer is available in the day end bunch provided to the LIC on daily basis. However, reason for bay re-assignment is not being captured in the report. | 3.14 | Local loading checks (if applicable) | 1341 | HISAR TERMINAL | 1. Local loading records should be signed by the LIC as well. 2. Bay Re-assignment reasons should be captured at the day end and got signed by the LIC as well. | SOD | Marketing | NZ | 2026-10-30 |  | 1 |  | S1 | F1 | 2026-10-30 | AUD-2026-10-2000017909ACN-2026-10-4000155489 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155489 | 2026-09-30 17:00 | 19.0455 | 424 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155489 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155489 |  | AUD-2026-10-2000017909ACN-2026-10-4000155489 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155490 | Open |  |  | Housekeeping - Housekeeping of the location is found to be generally satisfactory with some areas requiring improvement which were discussed during field round with location team (details given below). 1. Warehouse: (a) cobwebs were found at many places inside the warehouse. (b) Records were found kept scattered on the floor without proper stacking & identification. (c) Spare material kept inside the warehouse were found not to be identified with nomenclature and there is no bin system maintained in the warehouse. 2. Grass was found grown below the product pipeline alongside the tank farms with grass touching the pipelines at some places. Grass was also found touching the firehydrant ring main behind the scrap yard. | 3.15 | Housekeeping & PPE usage checked | 1341 | HISAR TERMINAL | 1. Warehouse: (a) to be kept cobweb free. (b) records to be stored properly in designated trunks with disposal of old records as per the corporation's record disposal policy. (c) Spares should be stored as per bin system inside the warehouse with identified inventory levels. MIVs should be used for issue of material from the warehouse and surplus material should declared so for utilization elsewhere. 2. All pipelines should be kept vegetation free. Additionally, location to originate proposal for providing PCC/ RCC underthe pipelines to keep them vegetation free for proper inspection during routine rounds and to avoid corosion of the pipelines. | SOD | Marketing | NZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-10-2000017909ACN-2026-10-4000155490 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155490 | 2026-09-30 17:00 | 19.0455 | 485 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155490 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155490 |  | AUD-2026-10-2000017909ACN-2026-10-4000155490 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155491 | Open |  |  | The crocodile clip installed at Bay No. 08 & used for earthing of TTs placed for loading was found to be having gap when not latched on the TT body making it ineffective for clamping of small thickness cleats provided on some TTs. This may result in improper bonding/ earthing contact with the TT during gantry operations. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1341 | HISAR TERMINAL | Replace the defective crocodile clip at Bay No. 08 immediately to ensure proper bonding/earthing during TT gantry operations. Also,check for similar kind of issues at other bays and take corrective actions as required. | SOD | Marketing | NZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017909ACN-2026-10-4000155491 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155491 | 2026-09-30 17:00 | 19.0455 | 425 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155491 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155491 |  | AUD-2026-10-2000017909ACN-2026-10-4000155491 | 21 |  | 27 | 80 | 0 | 0 | 61
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155492 | Open |  |  | Scrap area was visited during the visit and following observations were made: 1. Some miscellaneous scrap were kept outside the scrap area. 2. Plastic drums were found kept in awaiting disposal. 3. Used oil was found stored in 13 barrels of 200L each awaiting disposal. 4. New DUs of retail were found kept with worn out protective plastic covers. 5. Unused project time surplus pipes were found kept directly on soil. 6. Lot of grass vegetation was observed inside the scrap yard. 7. Approach to the WCFM#41 which is provided for protecting the scrap area was found unclear of vegetation. Platform for the WCFM was also found not provided. 8. The WCFM#41 was operated and was found operating well. However, nuts and bolts associated with its flanges were found highly rusted. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1341 | HISAR TERMINAL | 1. All the miscellaneous scrap accummulated inside the location premises to be shifted to the designated scrap area and disposed-off in a time bound manner. 2. To be disposed-off within 3 months from now. 3. To be disposed-off within 3 months from now. 4. Matter to be taken up with retail to provide proper protection to the company's assets lying insde the scrap yard and ensure that properprotection with plastic covers are provided on the DUs to mitigate the weathering effects of nature. 5. Proper base to avoid deterioration of the pipes to be provided. 6. Scrap area to be kept vegetation free. 7. Proper approach to be provided to the WCFM#41 and all others which do not have proper approach. 8. Nut bolts associated with all the flanges should be properly maintain with petroleum gelly/ grease to avoid corrosion. | SOD | Marketing | NZ | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-10-2000017909ACN-2026-10-4000155492 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155492 | 2026-09-30 17:00 | 19.0455 | 486 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155492 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155492 |  | AUD-2026-10-2000017909ACN-2026-10-4000155492 | 21 |  | 27 | 80 | 0 | 0 | 70
[5 empty] | SMA_HISAR TERMINAL_Q2 | 2026-09-30 17:00 | AUD-2026-10-2000017909 | 2026-09-29 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-10-4000155493 | Open |  |  | Functioning of hooters available in the control room were checked and following are the findings: 1) For H, HH & HHH for TK03 was checked and found to be working with visual indication along with audio. 2. Dyke Valve # 03 was opened physically and hooter was found working with visual indication as well. 3. Open Path HCD in Pump House was verified with 60% of LEL filter. An indication of 54% LEL appeared in the TAS screen with local hooter operating in the pump house. However, hooter in the control room did not functionduring the testing including visual indication. | 5.2 | Functioning of all Hooters in control room | 1341 | HISAR TERMINAL | HCD alarm (Hooter & visual Indicator) in the control room to be rectified. | SOD | Marketing | NZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017909ACN-2026-10-4000155493 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017909ACN-2026-10-4000155493 | 2026-09-30 17:00 | 19.0455 | 425 | >20 | AUD-2026-10-2000017909 - ACN-2026-10-4000155493 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-10-2000017909ACN-2026-10-4000155493 |  | AUD-2026-10-2000017909ACN-2026-10-4000155493 | 21 |  | 27 | 80 | 0 | 0 | 61
NIDAMARTHI NAGA KIRAN | 2026-10-04 | S SWETHA BAI | 2026-09-07 | Trend data for UG tank levels has been attached. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147900 | Closed | S SWETHA BAI | 2026-09-07 | Sick TT TAS screenshot to be attached in Sick TTs Report. | 6.4 |  | 1919 | SECUNDERABAD TERMINAL | Sick TT TAS screenshot to be attached in Sick TTs Report. | SOD | Marketing | SCR | 2026-10-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147900 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147900 | 2026-08-06 19:00 | 73.9622 | 398 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147900 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016364ACN-2026-08-4000147900 | AUD-2026-08-2000016364ACN-2026-08-4000147900 | 21 | 21 | 27 | 80 | 1 | -12 | 61 | 57
|  | SATYENDRA CHOURASIA | 2026-10-04 | FE2 CWP reading rectified after replacement of sensor. | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129559 | Completed | SATYENDRA CHOURASIA | 2026-10-04 | Full Field round completed(gantry/tank farm/Product pump house/Fire Pump House/control room/Emergency exit gate/security/admin). For FE2, CWP reading is showing as 25 where as the limit is 2 to 3 kg | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1919 | SECUNDERABAD TERMINAL | FE2 CWP reading to be checked and rectified | SOD | Marketing | SCR | 2026-05-20 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129559 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129559 | 2026-08-06 19:00 | 73.9622 | 261 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129559 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012102ACN-2026-05-4000129559 |  | AUD-2026-05-2000012102ACN-2026-05-4000129559 | 21 |  | 27 | 80 | 1 | -12 | 38
|  | SATYENDRA CHOURASIA | 2026-10-04 | Reading issue rectified after replacement of sensor. Leakage from gland arrested. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147042 | Completed | SATYENDRA CHOURASIA | 2026-10-04 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin). For FE-3, the LOP value displayed on the display board was found mentioned as < 2 kg/cm² instead of the required > 2 kg/cm². For FE-2, the CWP reading on the display board was showing 0 kg, whereas the specified operating range is 2–3 kg. FE - 4 delivery valve gland leakage observed. Smoke detector checked in cable cellar of MCC room , functioning found OK. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1919 | SECUNDERABAD TERMINAL | Location to take corrective action | SOD | Marketing | SCR | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147042 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147042 | 2026-08-06 19:00 | 73.9622 | 425 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147042 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147042 |  | AUD-2026-08-2000016364ACN-2026-08-4000147042 | 21 |  | 27 | 80 | 1 | -12 | 61
|  | DAS DARSHAN | 2026-10-05 | The rake unloading points have been prominently marked to make it identifiable in the field. Hence complied | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143500 | Completed | DAS DARSHAN | 2026-10-05 | The rake unloading points are not prominently identifiable in the field. Adequate markings/signages not provided. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Provide and maintain adequate markings/signages for all rake unloading points to ensure clear identification and facilitate safe and efficient operations. | SOD | Marketing | NCR | 2026-07-20 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-07-20 | AUD-2026-06-2000013451ACN-2026-07-4000143500 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143500 | 2026-09-03 | 46.7538 | 322 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143500 | 532 | 8294 | 21 | 8294 | 91 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143500 |  | AUD-2026-06-2000013451ACN-2026-07-4000143500 | 21 |  | 27 | 80 | 0 | 0 | 46
|  | ASHIRBADA MISHRA | 2026-10-05 | Otained approval for MOC No. 3200000979 for the storage of MS RON 91 in the Bowser. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154829 | Completed | ASHIRBADA MISHRA | 2026-10-05 | MOC records are available. All MOCs are closed on time except those which works are going on | 3.17 | MOC status reviewed | 1856 | COIMBATORE DEPOT | MOC for power100 to be submitted for storing product in Trucks. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017811ACN-2026-09-4000154829 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154829 | 2026-08-28 17:00 | 52.0455 | 394 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154829 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154829 |  | AUD-2026-09-2000017811ACN-2026-09-4000154829 | 21 |  | 27 | 80 | 0 | 1 | 57
|  | DAS DARSHAN | 2026-10-05 | 1. The LPR for deployment of an Emergency Vehicle at the IRD is initiated and we have sent budget proposal to zone. Once the budgetis approved, the emergency vehicle will be positioned at Lucknow IRD 2. All HLSA recommendations are complied with | ZONAL INSPECTION LUCKNOW IRD Q1 | 2026-05-22 18:00 | AUD-2026-06-2000013451 | 2026-05-21 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143482 | Completed | DAS DARSHAN | 2026-10-05 |  | 1.3 | Pending issues reviewed | 1292 | LUCKNOW DEPOT | 1. The LPR for deployment of an Emergency Vehicle at the IRD shall be initiated immediately to ensure timely emergency response andcompliance with safety requirements. 2. The location shall ensure compliance with HLSA recommendations Appropriate measures and alternative surveillance arrangements, should be implemented to address gaps. | SOD | Marketing | NCR | 2026-07-15 | THIRD PARTY ERRORS | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-15 | AUD-2026-06-2000013451ACN-2026-07-4000143482 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013451ACN-2026-07-4000143482 | 2026-09-03 | 46.7538 | 317 | >20 | AUD-2026-06-2000013451 - ACN-2026-07-4000143482 | 532 | 8294 | 21 | 8294 | 96 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000013451ACN-2026-07-4000143482 |  | AUD-2026-06-2000013451ACN-2026-07-4000143482 | 21 |  | 27 | 80 | 0 | 0 | 46
|  | ASHIRBADA MISHRA | 2026-10-05 | TK-3 was successfully recommissioned on 18.09.2026 following completion of cleaning, comprehensive inspection, repairs, sand blasting, and internal and external painting works. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154830 | Completed | ASHIRBADA MISHRA | 2026-10-05 | All OISD points are complied. Pending MDSA/SSA points related to tank inpection is reviewed and works are in progress | 3.18 | OISD/MDSA/SSA compliance reviewed | 1856 | COIMBATORE DEPOT | To follow up and put back the Tank TK03 into operation at the earliest. | SOD | Marketing | SZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017811ACN-2026-09-4000154830 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154830 | 2026-08-28 17:00 | 52.0455 | 394 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154830 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154830 |  | AUD-2026-09-2000017811ACN-2026-09-4000154830 | 21 |  | 27 | 80 | 0 | 1 | 57
|  | DAS DARSHAN | 2026-10-05 | The location have complied all the points of OISD/MDSA/SSA except the point pertaining to installion of lights of MDSA and SSA audit. The lights have been installed in the pumphouse, tamkfarm and gantry area. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122662 | Completed | DAS DARSHAN | 2026-10-05 | Summary attached as annexure 1. Location is advised to close the compliance of priority basis scheduled in current FY. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1292 | LUCKNOW DEPOT | Corrective action to be taken. | SOD | Marketing | NCR | 2026-03-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011009ACN-2026-03-4000122662 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122662 | 2026-09-03 | 46.7538 | 211 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122662 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011009ACN-2026-03-4000122662 |  | AUD-2026-03-2000011009ACN-2026-03-4000122662 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | ASHIRBADA MISHRA | 2026-10-05 | All 27 numbers of 75 kg and 25 kg fire extinguisher sheds at the location were cleaned and painted. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154834 | Completed | ASHIRBADA MISHRA | 2026-10-05 | paint of 75 KG fire extinguisher cover near tank no 6 is peeled out and not identificable. | 6.3 | Additional Observations | 1856 | COIMBATORE DEPOT | Painting to be carried out and proper identification to be done. | SOD | Marketing | SZ | 2026-11-30 |  | 1 |  | S1 | F1 | 2026-11-30 | AUD-2026-09-2000017811ACN-2026-09-4000154834 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154834 | 2026-08-28 17:00 | 52.0455 | 455 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154834 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154834 |  | AUD-2026-09-2000017811ACN-2026-09-4000154834 | 21 |  | 27 | 80 | 0 | 1 | 65
|  | ASHIRBADA MISHRA | 2026-10-05 | A new wind sock installed on the top of TK3 and wind sock visibility from all location checked and verified. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154832 | Completed | ASHIRBADA MISHRA | 2026-10-05 | No wind sock visibility from HVLR remote panel No 4. | 6.1 | Additional Observations | 1856 | COIMBATORE DEPOT | Wind socks to be provided and should be visible from all areas. | SOD | Marketing | SZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154832 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154832 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154832 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154832 |  | AUD-2026-09-2000017811ACN-2026-09-4000154832 | 21 |  | 27 | 80 | 0 | 1 | 61
|  | ASHIRBADA MISHRA | 2026-10-05 | Breath analyzer register maintained and all the breath analyzer test details is being recorded on daily basis. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154822 | Completed | ASHIRBADA MISHRA | 2026-10-05 | Security alertness at night checked in CCTV and found in order. Various equipments like HHMD and Breath Analyser were checked. Records were checked for the same and found being maintained in register at security gate. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1856 | COIMBATORE DEPOT | Breath Analyzer records to be maintained with traceability of truck number, concerned driver/contract workmen etc. | SOD | Marketing | SZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154822 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154822 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154822 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154822 |  | AUD-2026-09-2000017811ACN-2026-09-4000154822 | 21 |  | 27 | 80 | 0 | 1 | 61
|  | ASHIRBADA MISHRA | 2026-10-05 | All ethanol-related circulars and instructions are being strictly complied with. QC sampling, testing, and monitoring are carried out as per the prescribed guidelines and instructions. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154828 | Completed | ASHIRBADA MISHRA | 2026-10-05 | 1 Ethanol TT(KA01AN8649) verified- TT dip found okay and UG Tank dips verified before and after uloading in UG tanks and found okay | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1856 | COIMBATORE DEPOT | Location to strictly follow the recent ethanol related circular and to strictly follow the test schedules. | SOD | Marketing | SZ | 2026-10-31 |  | 2 |  | S1 | F2 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154828 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154828 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154828 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154828 |  | AUD-2026-09-2000017811ACN-2026-09-4000154828 | 21 |  | 27 | 80 | 0 | 1 | 61
|  | ASHIRBADA MISHRA | 2026-10-05 | Loading locations are being immediately intimated in case of any stock loss observed following receipt of a rake. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154821 | Completed | ASHIRBADA MISHRA | 2026-10-05 | Location has been following circulars and maintaining records in CCTV monitoring, VTS monitoring, TT checks, Ethanol blending, TW stock loss Etc. Location is on the Top in terms of overall performance score in SZ and TAS parameters amongst All India locations. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1856 | COIMBATORE DEPOT | Location is advised to monitor Stock loss in Tank wagon unloading and to analyze reasons for loss in coordination with Loading location. | SOD | Marketing | SZ | 2026-12-31 |  | 2 |  | S1 | F2 | 2026-12-31 | AUD-2026-09-2000017811ACN-2026-09-4000154821 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154821 | 2026-08-28 17:00 | 52.0455 | 486 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154821 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154821 |  | AUD-2026-09-2000017811ACN-2026-09-4000154821 | 21 |  | 27 | 80 | 0 | 1 | 70
KOCHARA ASWINI KUMAR | 2026-10-05 | VIVEK KUMAR SAROJ | 2026-10-03 |  | LOCATION VISIT-BATHINDA_18.06.26 | 2026-06-18 | AUD-2026-07-2000015568 | 2026-06-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000142620 | Closed |  |  | Additional TTs to be inducted. Differential payment to be given to transporters. | 1.3 | Pending issues reviewed | 1164 | BHATINDA TERMINAL | Location to coordinate with Zonal Transportation for expediting the jobs. | SOD | Marketing | NFZ | 2026-07-31 | LACK OF TRAINING OR COMPETENCY | 12 | PROCESS SAFETY | S3 | F4 | 2026-07-31 | AUD-2026-07-2000015568ACN-2026-07-4000142620 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015568ACN-2026-07-4000142620 | 2026-09-28 19:00 | 20.9622 | 399 | >20 | AUD-2026-07-2000015568 - ACN-2026-07-4000142620 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015568ACN-2026-07-4000142620 | AUD-2026-07-2000015568ACN-2026-07-4000142620 | 21 | 21 | 27 | 80 | 1 | -2 | 48 | 57
DINESH KUMAR | 2026-10-05 |  |  | Corrective action taken as per recommediations | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000129953 | Closed | DINESH KUMAR | 2026-10-05 | Location has to prepare detailed ERDMP for POL road trucks for detailed roadside emergency procedures | 2.15 | TT crew roadside emergency procedures checked | 1254 | JALANDHAR DEPOT | Location has to prepare detailed ERDMP for POL road trucks for detailed roadside emergency procedures | SOD | Marketing | NFZ | 2026-05-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-05-30 | AUD-2026-05-2000011851ACN-2026-05-4000129953 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129953 | 2026-08-21 | 59.7538 | 399 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129953 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000011851ACN-2026-05-4000129953 | AUD-2026-05-2000011851ACN-2026-05-4000129953 | 21 | 21 | 27 | 80 | 0 | -21 | 39 | 57
KATAKAM SRINIVAS | 2026-10-05 | BAGADE AMAR ARUN | 2026-10-05 | ESD Buttons replaced from Glass type to Push Type. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146515 | Closed | BAGADE AMAR ARUN | 2026-10-05 | Location has 4 HVLR, 3 point type HCD, 5 open path HCD, 12+1 ESDs all are functioning properly | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1485 | AKOLA DEPOT | Replace ESD buttons from break glass type to push type | SOD | Marketing | WZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146515 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146515 | 2026-08-24 | 56.7538 | 399 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146515 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146515 | AUD-2026-06-2000013155ACN-2026-07-4000146515 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
KATAKAM SRINIVAS | 2026-10-05 | BAGADE AMAR ARUN | 2026-10-05 | Authorized person details updated and displayed at MCC Room | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146522 | Closed | BAGADE AMAR ARUN | 2026-10-05 | Details of authorized personnel displayed outside the MCC room are outdated. | 6.5 | MCC room display boards | 1485 | AKOLA DEPOT | Update and display the latest authorized personnel details | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146522 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146522 | 2026-08-24 | 56.7538 | 399 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146522 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146522 | AUD-2026-06-2000013155ACN-2026-07-4000146522 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
KATAKAM SRINIVAS | 2026-10-05 | BAGADE AMAR ARUN | 2026-10-05 | Dry grass near UG tank is cut and removed. | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154978 | Closed | BAGADE AMAR ARUN | 2026-10-05 | Workers were having PPE and Houskeeping is found ok. However, there was some dry grass observed near UG tanks. | 3.15 | Housekeeping & PPE usage checked | 1485 | AKOLA DEPOT | Location to take necessary action. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-09-2000017374ACN-2026-09-4000154978 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154978 | 2026-08-24 | 56.7538 | 399 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154978 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017374ACN-2026-09-4000154978 | AUD-2026-09-2000017374ACN-2026-09-4000154978 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
DINESH KUMAR | 2026-10-05 |  |  | TT induction started shall be completed | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151904 | Closed | DINESH KUMAR | 2026-10-05 | Time period of additional TTs taken earlier is going to expire | 6.1 | Transportation | 1254 | JALANDHAR DEPOT | Additional TTs induction to be done by Location in time. | SOD | Marketing | NFZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-09-2000017550ACN-2026-09-4000151904 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151904 | 2026-08-21 | 59.7538 | 399 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151904 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017550ACN-2026-09-4000151904 | AUD-2026-09-2000017550ACN-2026-09-4000151904 | 21 | 21 | 27 | 80 | 0 | -21 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | Delhi Terminal has mailed other location for requirement of 4 Co owned TTs of capacity 23 KL(5x4+3) | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150033 | Closed | KUMAR LIKESH | 2026-10-05 | 1. Delhi Terminal has four company-owned, 23 KL tank trucks. These TTs are presently underutilized due to non-availability of matching indents. The TTs have been offered to other locations; however, no response has been received. As per norms, these TTs can be operated for a maximum period of 10 years. They have already completed 8 years of service and, in any case, will be required to be declared obsolete after completion of their service life. 2. Bijwasan Terminal Land of approx 15 acre is under control of Delhi Terminal. Delhi Terminal has provided very limited security i.e One guard in each sift to avoid any encroachment and manning of main Gate. However different SBU's are storing like Retail, Aviation and INC are storing their various materials in this premises. These SBU's has already been conveyed to review safety, security, ward and watch of their material.HQO has informed that this land has been offered to HPGRE. | 1.3 | Delhi Terminal has mailed other location for requirement of 4 Co owned TTs of capacity 23 KL(5x4+3) | 1221 | DELHI TERMINAL | 1. Transfer of Company owned TT's to another Location. | SOD | Marketing | NZ | 2027-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017114ACN-2026-09-4000150033 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150033 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150033 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150033 | AUD-2026-09-2000017114ACN-2026-09-4000150033 | 21 | 21 | 27 | 80 | 3 | 3 | 83 | 57
|  | KUMAR LIKESH | 2026-10-05 | Point 1,2 & 4 is complied. Painting to be planned as per the allotment of additional budget | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150040 | Completed | KUMAR LIKESH | 2026-10-05 | - Earth Pits - Total 247 Earth pits are there at the location. Earth Pit No 78 & 79 were checked for earth resistance and following observations were made w.r.t. displayed/ observed readings during the visit. EP 78 (TTL Gantry): Individual Reading (Displayed on Board/ Physically Observed- 1.37 Ω / 0.47 Ω Grid Reading (Displayed on Board/ Physically Observed- 0.47 Ω / 0.03 Ω EP 79 (TTL Gantry): Individual Reading (Displayed on Board/ Physically Observed- 1.37 Ω / 0.46 Ω Grid Reading (Displayed on Board/ Physically Observed- 0.42 Ω / 0.05 Ω However, date of verification of earth pit resistance was not found changed as per the actual date of testing & records available. Flexible wires originating directly from earth pits were observed during the previous visit- this point is still open for 100% compliance. - Boundary- Condition of Boundary wall is found satisfactory, However painting is required, also at some places and Concertina coil needs replacement along with Provision of broken glass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. Previous visit's inspection point still open. -Vegetation Control - No Encroaching/ Overgrown vegetation was observed across the boundary wall. | 3.16 | Earth pits / boundary / vegetation control checked | 1221 | DELHI TERMINAL | - Earthing connections should be originated from nearest earthing strips available at the electrical equipment rather than taking earthing connections directly from the earthpit. - Earth pit date of testing should be displayed as per the actual date of testingon all earth pits. - Painting of Boundary wall is to be planned and damaged Concertina coil to be replaced with new one - Broken Glass pieces to be placed for detereance | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150040 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150040 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150040 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150040 |  | AUD-2026-09-2000017114ACN-2026-09-4000150040 | 21 |  | 27 | 80 | 3 | 3 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | Idenitication of scenarios as per ERDMP completed. All scenarios shall be covered in current year. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150034 | Closed | KUMAR LIKESH | 2026-10-05 | Fire drills conducted in last 6 months were reviewed and found that location has been conducting one fire-drill per month as per requirement. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1221 | DELHI TERMINAL | Location to ensure covering of all ERDMP identified scenarios under mock drill in one year. | SOD | Marketing | NZ | 2027-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017114ACN-2026-09-4000150034 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150034 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150034 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150034 | AUD-2026-09-2000017114ACN-2026-09-4000150034 | 21 | 21 | 27 | 80 | 3 | 3 | 83 | 57
|  | KUMAR LIKESH | 2026-10-05 | Power100 Proposal has been sent to HQO. Proposal under initiative has been approved with Proposal ID SOD260995. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150046 | Completed | KUMAR LIKESH | 2026-10-05 | Additive dosing skid to be provided for Power 100 additives dosing | 6.1 |  | 1221 | DELHI TERMINAL | Additive dosing skid to be provided for Power 100 additives dosing | SOD | Marketing | NZ | 2026-12-30 |  | 1 |  | S1 | F1 | 2026-12-30 | AUD-2026-09-2000017114ACN-2026-09-4000150046 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150046 | 2026-08-27 | 53.7538 | 485 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150046 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150046 |  | AUD-2026-09-2000017114ACN-2026-09-4000150046 | 21 |  | 27 | 80 | 3 | 3 | 70
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | TPA done by SK Electrical Works & LUX LEVELS found as per OISD Requirements. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150035 | Closed | GARG PANKAJ | 2026-10-05 | Lux levels at various locations inside the terminal premises was taken during the night inspection on 29th Jul'26. Following observations w.r.t. Lux Levels Vs. Actual requirement as per OISD were made: - Near TT in Gate: 33 Vs. 20 - Road Behind Admin Building: 01 Vs. 10 - Bay No. 12: 132 Vs. 60 - Bay No. 19: 43 Vs. 60 - Bay No. 22: 28 Vs. 60 - UG Tank Farm: All lights were kept off for repairs (03 Vs. 20) - ROSOV of TK07: 20 Vs. 60 - Product Pump House: 298 Vs. 100. Two lights were flickering. Last Lux Level was verified by the location internally on 08.07.2026 and lux levels were found meeting the minimum requirement as per OISD in all areas. | 2.2999999999999998 | Lux levels checked (gantry/roads/admin) during night-halt | 1221 | DELHI TERMINAL | Lux levels to be maintained as per the requirement. | SOD | Marketing | NZ | 2026-12-31 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017114ACN-2026-09-4000150035 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150035 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150035 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150035 | AUD-2026-09-2000017114ACN-2026-09-4000150035 | 21 | 21 | 27 | 80 | 3 | 3 | 70 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | Level chart displayed near both foam tanks. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150036 | Closed | KUMAR LIKESH | 2026-10-05 | As per the foam calculation shared by the location, the foam requirement for the location is 11 KL. The foam available physically is 14.08KL as per the HSE officer as of 30th July'26 opening. Location has 2 mother tanks for foam pourer. The details of these two Foam mother tanks along with their inventory observed on 26.05.2026 is as given below: - Foam Tank# 1: Capacity 9000L (0 - 165cm diameter with level tube as graduated scale along side available). Observed Foam level: 53.5 cm. - Foam Tank# 2: Capacity 8000L (0 - 57cm diameter with level tube as graduated scale along side available). Observed Foam level: 18 cm. As per the record presented bythe location, Foam availability at the location was confirmed by the location as 12KL which is more than the minimum storage requirement as per OISD 244. | 2.9 | Foam inventory verified & PO for 3KL Additional Foam raised. | 1221 | DELHI TERMINAL | PENDING RECOMMENDATION OF PREVIOUS VISIT: Location to display the level wise stock in litres on the Foam Tanks for immediate assessment during site visit. | SOD | Marketing | NZ | 2026-09-30 | INSTRUMENTATION OR ALARM FAILURES | 1 | EMERGENCY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150036 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150036 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150036 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150036 | AUD-2026-09-2000017114ACN-2026-09-4000150036 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | i) Assessment of LPM requirement for each HVLR completed. Ii) completed . iii) Complied. Iv) Complied | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150037 | Closed | GARG PANKAJ | 2026-10-05 | HVLR- Total 05 No of HVLR are available at the location. HVLR No. 01 – Checked for its movement in all directions and found satisfactory. However, the equipment did not operate in Jet mode and only Fog mode could be activated. The equipment could not be stopped from its panel & had to be closed physically. None of the indicators were found working on its operating panel. It was operated byMr. Likesh Kumar and his knowledge about the functionality was found satisfactory. HVLR No. 04: Leakage was found from the HVLR#4 with its feed gate valve in closed condition. This was also the observation made during the last quarter's inspection. HVLR No. 02 – Operated by Mr. Likesh and his knowledge about the functionality of its panel was found satisfactory. The HVLR was not movingin down direction and its fog mode did not function to the desired degree with restricted fog generation. Location is carrying out monthly testing of HVLRs with the last testing done on 13.04.2026. RSFPS- NA, At Delhi terminal has 7nos. of AG Class A Tanks- all are having Fixed Roof with 5 equipement with IFR. HCD- Open Path HCD No. 01 – Located in the manifold area of Product Pump House was tested with 20%. Local hooter & alarm in TAS room were observed- TAS log was also verified. Similarly, Open Patch HCD neardyke drain valve# 4 was verified with 20% filter as was found working satisfactorily with local as well as TAS + Security Cabin annunciations. However, annunciation during the first testing was accepted and reset from the marketing room without communication to field/ concerned officer before doing so. Location is maintaining month test report of HCD with last testing done on 08.05.2026. ESD- Location is carrying out monthly testing of ESDs. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1221 | DELHI TERMINAL | HVLR: (i) Location to carry out assessment of LPM requirement of all the HVLRs to ensure that they hit the targetted location on the facilities they are supposed to protect. (ii) Location to carry out servicing of inlet gate valves connected all HVLRs to avoid leakages when in closed conditions. (iii) Functioning of HVLRs to be maintained in prime working condition all the time. Alarm Acceptance: Training to be given to security personnel on communication required to be made to field immediately on hearing any alarm annunciation and reseting of such alarms to be done only after advise from field. | SOD | Marketing | NZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150037 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150037 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150037 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150037 | AUD-2026-09-2000017114ACN-2026-09-4000150037 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | Fire hose testing completed and records maintained. All faulty hoses replaced. DCP replenishment details are maintained. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150038 | Closed | KUMAR LIKESH | 2026-10-05 | PREVIOUS VISIT'S OBSERVATIONS: - During the visit, one portable foam type fire extinguishers of 50L capacity was operated near TLFGantry 1 by a contract labor in the presence of TAS Officer and HSE officer. While the foam generation was evident, leakages were found from the nitrogen hose pipe connecting the external propellant cylinder to the foam cylinder. Further, the technique of closingthe valve of the nitrogen cylinder was known only to the contract labour operating it. CURRENT VISIT'S OBSERVATIONS: - Two HVLR's & one MEFG were operated by the TAS & M&I Officer and his knowledge level was found satisfactory. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1221 | DELHI TERMINAL | PENDING POINTS OF PREVIOUS VISIT: - Periodic testing of pressure hoses should be carried out to ensure nil failures during emergencies. - Replenishment of foam as well as nitrogen to be ensured in the used foam fire extinguisher. - Training to be imparted to all officer on how to use these fire extinguishers. | SOD | Marketing | NZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150038 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150038 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150038 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150038 | AUD-2026-09-2000017114ACN-2026-09-4000150038 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | "1.All single earthing point have been identified and work is under progress to convert all of them to double earthing. 2.Emergency trolley is maintained with its equipment stored in designated place. Equipment name displayed in hindi/english. 3. DFMD repair completed. " | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150043 | Closed | GARG PANKAJ | 2026-10-05 | PREVIOUS VISIT'S OBSERVATIONS: 1. Looping of earthing connections was observed at many places including Foam Storage shed, HVLRs, .... Similarly, at some places, multiple earthing connections to equipment were found originating from a single point of the nearby earthing strip. 2. Emergency Trolley placed in front of TT Gantry under the shed was checked. Stretcher was found not kept at the designated place. 3. DFMD installed at the main gate doesn't show indication on one side and its multizone functionality didn't seemaccurate. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1221 | DELHI TERMINAL | PREVIOUS VISIT'S PENDING RECOMMENDATIONS: 1. Independent earthing should be ensured for all electrical equipment and all 3 phase electrical equipment to be provided with double independent earthing connections. 2. Emergency trolley should be maintained with itsequipment stored in the designated place. Display of the equipment should be made in hindi as well. 3. DFMD to be attended to for intended functionality. | SOD | Marketing | NZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150043 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150043 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150043 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150043 | AUD-2026-09-2000017114ACN-2026-09-4000150043 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
|  | KUMAR LIKESH | 2026-10-05 | Scrap Valuation done by Surveyor valuing scrap approx 1.3 Lakh. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150044 | Completed | KUMAR LIKESH | 2026-10-05 | PREVIOUS VISIT'S OBSERVATIONS: Only few misc scrap valuing less that Rs 10000/- available. Location will dispose the same after accumulation of sizable quantity to justify surveyor fees. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1221 | DELHI TERMINAL | PREVIOUS VISITS RECOMMENDATIONS: Location of ensure disposal of the scrap within reasonable time to avoid accumulation. | SOD | Marketing | NZ | 2026-12-30 |  | 4 |  | S2 | F2 | 2026-12-30 | AUD-2026-09-2000017114ACN-2026-09-4000150044 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150044 | 2026-08-27 | 53.7538 | 485 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150044 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017114ACN-2026-09-4000150044 |  | AUD-2026-09-2000017114ACN-2026-09-4000150044 | 21 |  | 27 | 80 | 3 | 3 | 70
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | Tank sprinkler line repair completed. | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATION | ACN-2026-09-4000150047 | Closed | KUMAR LIKESH | 2026-10-05 | Leakages in Tank sprinkler lines to be rectified | 6.1 |  | 1221 | DELHI TERMINAL | Leakages in Tank sprinkler lines to be rectified | SOD | Marketing | NZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150047 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150047 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150047 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150047 | AUD-2026-09-2000017114ACN-2026-09-4000150047 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR LIKESH | 2026-10-05 | "1.Complied 2. Complied 3.complied 4. Complied 5. Complied 6. Complied 7.Will be completed by 30.10.2026 8. Complied 9. Complied 10.Complied 11. Complied 12 Complied 13.Complied. 14. Complied" | SENIOR MANAGEMENT AUDIT_DELHI TML_Q2 | 2026-07-30 17:00 | AUD-2026-09-2000017114 | 2026-07-28 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150048 | Closed | GARG PANKAJ | 2026-10-05 | 1. Ethanol pump # 3 was reported as not in operation. Only single earthing was found given to its motor. Further, its panel in MCC room was found electrically energized with SFU in on condition. LOTO is not practiced in the MCC room for all the equipment not in use. 2. Oil leakage was observed from the oil chamber's oil seal of MS Pump no. 1. 3. List of authorized personnel was not found displayed in front of the MCC Room. 4. An un-regulated entry/ exit was found from licensed area (Hazardous Area) to the MCC room thruthe expanded mesh fencing available to seggregate the two areas. 5. Single line diagram in the MCC room is mention of MTO 1 & MTO 2 in the VFD Panel whereas the physical feeders have been labled as Ethanol 1 & Ethanol 2 in the VFD panel. 6. Emergency exit of the MCC room was found locked from the outside restricting personnel inside the MCC room using it in case of any emergency. 7. Phase wise PF indication was found to be fluctuating grossly between the range 0.64 to 0.85 whereas the PF in the HT meter room was found to be 0.98. 8. Out of total 4 exhaust fans provided in the MCC room, three were found removed for repairs. 9. Housekeeping inside the DG room was found to be not upto the mark with lot of electrical items scattered on its floor near the 500KVA DG set. 10. Following records of MCC + DG room were inspected and suggestions for improvement were discussed with Sh. Likesh Kumar (TAS & M&I Officer) & Sh. Kuldeep Kumar (HSE Officer): (a) Monthly Checklist for Battery Bank, (b) Daily Checklist for Centrifugal Pump & Motor, (c) Solar Generation Record, (d) DG Log Books, (e) Monthly Checklist for Motors, (f) Diesel Generator Register (Actually for Diesel IssueRegister), (g) Weekly functioning of Fans & Lights of TAS room, and (h) Daily Transformer Checklist. 11. Some of the Foam Drums provided for Fixed Foam Monitors were found in uncapped conditions. 12. Dyke Drain Valve#4 was operated on 29.07.2026 @ 18:06 hrs.. It was observed that no local or TAS room alarm was annunciated when the water started passing. 13. MEFG in TK04 dyke was operated and its performance was found to be satisfactory. 14. In the Additive Pump House, Power-95 additive tank was found to be in open condition in the flange provided for a electrical devise. | 6.2 |  | 1221 | DELHI TERMINAL | 1. (a) Double independent earthing to be ensured for all the 3-phase pump motors. (b) All pumps & motors which are not in use should be marked/ tagged as not in use in the field. (c) Electrical de-enrgisation of all such Not in use pumps should be ensured thru LOTO in the MCC room. 2. Oil leakage from MS Pump no. 1 should be arrested. 3. List of authorized personnel should be displayed in front of the MCC Room. 4. No unregulated entry/ exit to/ from the licensed area (Hazardous Area) should be provided and all such locations should be permanently closed. 5. Single line diagram in the MCC room should be suitably modified and approved by the LIC. 6. Emergency exit of the MCC room should be maintained for the intended purpose. 7. Phase wise PF indication in the MCC room should be rectified and monitored on daily basis to access actual electrical consumption performance. 8. Exhaust fans provided in the MCC room to be made functional. 9. Housekeeping inside the DG room to be improved. 10. Records being maintained in the MCC room shouldbe suitably modified as discussed. 11. Foam Drums provided for Fixed Foam Monitors should be ensured in capped condition when not in use to avoid water ingress. 12. Dyke Drain Valve sensors to be suitably adjusted for timely alarms. 14. Corrective action to betaken. | SOD | Marketing | NZ | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-09-2000017114ACN-2026-09-4000150048 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017114ACN-2026-09-4000150048 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-09-2000017114 - ACN-2026-09-4000150048 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017114ACN-2026-09-4000150048 | AUD-2026-09-2000017114ACN-2026-09-4000150048 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Complied to all HQO/Zonal circulars and improvement plans | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122496 | Closed | KUMAR KULDEEP | 2026-08-08 | Interaction was carried out at Delhi Terminal in presence of LIC and all location officers on expectations from location and each officer. | 1.2 | Complied to all HQO/Zonal circulars and improvement plans | 1221 | DELHI TERMINAL | Compliance to recent HQO/Zonal circulars, improvement plans to be ensured | SOD | Marketing | NZ | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011120ACN-2026-03-4000122496 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000122496 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000122496 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000122496 | AUD-2026-03-2000011120ACN-2026-03-4000122496 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Fire Organization Chart updated. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122498 | Closed | GARG PANKAJ | 2026-10-05 | Security Guard alertness and emergency response has been check in form of Night inspection on 20th Jan'26 for Delhi Terminal and found ok. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1221 | DELHI TERMINAL | Fire Organization Chart required updation/ Correction. | SOD | Marketing | NZ | 2026-02-28 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | EMERGENCY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000122498 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000122498 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000122498 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000122498 | AUD-2026-03-2000011120ACN-2026-03-4000122498 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | The rectification of the NASH device has been successfully completed. Further, the CCTV system has been thoroughly checked, and it is confirmed that continuous recording for a period of 92 days is available and maintained. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122499 | Closed | KUMAR KULDEEP | 2026-08-08 | Tot No of CCTV - 54 No, and all are working Presently some issues are arising with NASH device, for which location has taken up the issue with M/s Score for its resolution. An additional 284 TB NASH device is available at Delhi Tml for backup support. Issue of NASH Device to be rectified in consultation with vendor and ensure 92 days CCTV footage recording to be maintained | 2.6 | CCTV functioning checked | 1221 | DELHI TERMINAL | NASH device to be rectified and 92 days CCTV footage recording ot be ensured | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 2 | EMERGENCY | S2 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000122499 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000122499 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000122499 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000122499 | AUD-2026-03-2000011120ACN-2026-03-4000122499 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Complied | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123550 | Closed | GARG PANKAJ | 2026-10-05 | Thorough checking TT No DL01 GE 4143 was done along with LIC and concerned officer to sensitize the need for proper inspection of TTs in line with the extant circular. Fire extinguisher was operated by the TT Driver and was found satisfactory. Annex -07 | 3.1 | TT fittings & discipline checked | 1221 | DELHI TERMINAL | Compliance of the observation made w.r.t. TT inspected to be ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123550 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123550 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123550 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123550 | AUD-2026-03-2000011120ACN-2026-03-4000123550 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | 33 locks sent for repair/checks with Sterna. Balance identified locks shall be sent after receipt of previous lot. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123551 | Closed | KUMAR KULDEEP | 2026-08-08 | EM lock checked using Intelligent Key was done for six no of TTs and online report as per requirement was submitted after checking.Plastic dust cover were found broken in few locks location & location has been advise to replace them and confirm to zone by 31st Jan’2026. | 3.5 | EM Lock SOP compliance verified | 1221 | DELHI TERMINAL | Broken Plastic Dust covers need to be replaced with new one | SOD | Marketing | NZ | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123551 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123551 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123551 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123551 | AUD-2026-03-2000011120ACN-2026-03-4000123551 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Instances of maunal reconciliation reduced. Google sheet being updated on regular basis. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123552 | Closed | KUMAR KULDEEP | 2026-08-08 | Out of total 2092 tank reconciliations done during the period 1st Oct'25 to 19th Jan'26, only 22 instances belonging to 31st Dec'25were done in manual mode which was done as per the HQO guidelines for quarter end. Rest all cases recorded in SAP are done in auto mode. No abnormality was found. | 3.8 | Auto vs Manual reconciliation checked | 1221 | DELHI TERMINAL | Location to reduce the instance of manual Reconciliation and update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NZ | 2026-02-28 | THIRD PARTY ERRORS | 1 | EMERGENCY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123552 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123552 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123552 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123552 | AUD-2026-03-2000011120ACN-2026-03-4000123552 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Surplus items updated in the portal. 02 Nos. of Jockey pumps alongwith its panel has been shifted to Cochin terminal. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123553 | Closed | KUMAR KULDEEP | 2026-08-08 |  | 3.9 | Abnormal variations / unused assets reviewed | 1221 | DELHI TERMINAL | Location to revert back with action taken. | SOD | Marketing | NZ | 2026-02-28 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123553 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123553 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123553 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123553 | AUD-2026-03-2000011120ACN-2026-03-4000123553 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | It has already coordinated with the pipelines group to address the issue of false Tank Leakage Alarms. It has been agreed, executedand implemented that, upon completion of Product Level Tests (PLTs), the tanks shall be placed under dormant mode after allowing a minimum product settling time of forty‑five minutes. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123554 | Closed | KUMAR KULDEEP | 2026-08-08 | Verified last 3 months TAS alerts in NOVEX portal and only 3 critical open alerts of Tank Leakage Alarms were found which are related to tanks handed over to pipelines groups for product receipt. Location has been advised to take up with pipelines officials to put the tanks under dormant mode after completion of PLTs after giving minimum 45’ product settling time to avoid such false “Tank Leakage Alarms”. | 3.12 | Critical alarms checked & corrective actions reviewed | 1221 | DELHI TERMINAL | Location has been advised to take up with pipelines officials to put the tanks under dormant mode after completion of PLTs after giving minimum 45’ product settling time to avoid such false “Tank Leakage Alarms”. | SOD | Marketing | NZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123554 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123554 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123554 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123554 | AUD-2026-03-2000011120ACN-2026-03-4000123554 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | 1) Repairing of damaged concertina coil completed. 2) Location is in process of preparing proposal for obtaining additional MEB for painting of boundary wall, replacement of concertina coil and placement of broken glass pieces. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123555 | Closed | KUMAR KULDEEP | 2026-08-08 |  | 3.16 | Earth pits / boundary / vegetation control checked | 1221 | DELHI TERMINAL | 1. Painting of Boundary wall is to be planned and damaged Concertina coil to be replaced with new one 2. Broken Glass piecesto be placed for detereance | SOD | Marketing | NZ | 2026-07-31 | INSUFFICIENT SUPERVISION | 1 | EMERGENCY | S1 | F1 | 2026-07-31 | AUD-2026-03-2000011120ACN-2026-03-4000123555 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123555 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123555 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123555 | AUD-2026-03-2000011120ACN-2026-03-4000123555 | 21 | 21 | 26 | 80 | 3 | 3 | 48 | 57
|  | KUMAR KULDEEP | 2026-10-05 | Visitor entry, Visitor exit, Hazardeous area exit and enrollment CBAC reader repair completed by CAMC vendor M/s. Godrej. | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141153 | Completed | KUMAR KULDEEP | 2026-10-05 | During the visit, Access control was checked and found that CBAC Systen was functional alongwith Biometric operational at Maingate,Entry to Licence area and Control room. However, out of the four readers available at the main gate, one reader is not functional. Further, enrollment of new personnel (contract labor) is not allowed by the system. | 2.8 | Access control systems checked | 1221 | DELHI TERMINAL | Faults in the CBAC system to be rectified immediately and confirmed back to zone. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141153 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141153 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141153 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141153 |  | AUD-2026-06-2000014036ACN-2026-06-4000141153 | 21 |  | 27 | 80 | 3 | 3 | 48
|  | KUMAR KULDEEP | 2026-10-05 | Level wise stock in litres chart displayed near on the Foam Tanks for immediate assessment during site visit. | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141154 | Completed | KUMAR KULDEEP | 2026-10-05 | As per the foam calculation shared by the location, the foam requirement for the location is 11 KL. Location has 2 mother tanks forfoam pourer. The details of these two Foam mother tanks along with their inventory observed on 26.05.2026 is as given below: - Foam Tank# 1: Capacity 9000L (0 - 165cm diameter with level tube as graduated scale along side available). Observed Foam level: 53.5 cm. - Foam Tank# 2: Capacity 8000L (0 - 57cm diameter with level tube as graduated scale along side available). Observed Foam level: 18 cm. As per the record presented by the location, Foam availability at the location was confirmed by the location as 12KL whichis more than the minimum storage requirement as per OISD 244. | 2.9 | Foam inventory verified | 1221 | DELHI TERMINAL | Location to display the level wise stock in litres on the Foam Tanks for immediate assessment during site visit. | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141154 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141154 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141154 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141154 |  | AUD-2026-06-2000014036ACN-2026-06-4000141154 | 21 |  | 27 | 80 | 3 | 3 | 48
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | The fire alarm panel installation work has now been successfully completed, and the subject MoC stands closed | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123556 | Closed | KUMAR KULDEEP | 2026-08-08 |  | 3.17 | MOC status reviewed | 1221 | DELHI TERMINAL | MOC to be closed within time bound manner | SOD | Marketing | NZ | 2026-03-31 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011120ACN-2026-03-4000123556 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123556 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123556 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123556 | AUD-2026-03-2000011120ACN-2026-03-4000123556 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Comprehensive/MDSA Actionable Point: 1. All recommendations of QRA has been complied. 2. Inspection by Dy Controller of Explosives, Faridabad has been completed. Certain gaps were observed, and corrective works advised are currently in progress. 3. The rectification of the Secondary Radar Gauge installed at Tank TK‑05 has been duly completed in accordance with the stipulated Purchase Orderdelivery date. 4. Compliance to OISD Guideline for Tank Emergency drain Blind shall be completed during next scheduled cleaning oftanks. 5. The work of reducing the height of the Hydrant Valve has been completed. Self Safety Audit Actionable Point: 1. All recommendations of QRA has been complied. 2. The rectification of the Secondary Radar Gauge installed at Tank TK‑05 has been duly completed in accordance with the stipulated Purchase Order delivery date. 3. Compliance to OISD Guideline for Tank Emergency drain Blind shall be completed during next scheduled cleaning of tanks. PNGRB T4S Actionable point 1. PNGRB T4S PO placed on M/s. BOSAI SAFETY PRIVATE LIMITED. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123557 | Closed | KUMAR KULDEEP | 2026-08-08 |  | 3.18 | OISD/MDSA/SSA compliance reviewed | 1221 | DELHI TERMINAL | XX | SOD | Marketing | NZ | 2026-12-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-03-2000011120ACN-2026-03-4000123557 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123557 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123557 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123557 | AUD-2026-03-2000011120ACN-2026-03-4000123557 | 21 | 21 | 26 | 80 | 3 | 3 | 70 | 57
|  | KUMAR KULDEEP | 2026-10-05 | Location has completed idenitication of scenarios as per ERDMP. Location has planned to cover all scenarios in current year. | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141150 | Completed | KUMAR KULDEEP | 2026-10-05 | Fire drills conducted in last 6 months were reviewed and found that location has been conducting one fire-drill per month as per requirement. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1221 | DELHI TERMINAL | Location to ensure proper description of the emergency scenario being considered for every fire drill and records to be maintained accordingly. Location to ensure covering of all ERDMP identified scenarios under mock drill in one year. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-06-2000014036ACN-2026-06-4000141150 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141150 | 2026-08-27 | 53.7538 | 394 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141150 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141150 |  | AUD-2026-06-2000014036ACN-2026-06-4000141150 | 21 |  | 27 | 80 | 3 | 3 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Safety Behavioural Training has been successfully organized and completed in coordination with the Sarathi Mitra Driver Capacity Building Program and the Joy of Safety – A CSR Initiative by Suzuki Motorcycle India Pvt. Ltd. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.19 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123558 | Closed | KUMAR KULDEEP | 2026-08-08 | Interaction with TT crew of TT No: DL01 GE 4498, DL01 GC 7573, UP81 FT 6989 and DL01 GE 4143 was done along with location officers for reinforcing safety behavior. | 3.19 | Interaction with TT crew/workmen to reinforce safety behaviour | 1221 | DELHI TERMINAL | Safety Behavioural training to be organized | SOD | Marketing | NZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011120ACN-2026-03-4000123558 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123558 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123558 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123558 | AUD-2026-03-2000011120ACN-2026-03-4000123558 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | 1. The oil cups of all pumps (2 no Ethanol/1 no MS and 1 no HSD Pump) has been replaced. Additionally, a mild leakage observed from the mechanical seal of one MS pump has also been rectified. 2. Painting of the support angles of TK‑09 has been completed. 3. Maintenance of earth pit chambers has been completed. 4. All non operational lights on TT gantry are replaced and now all lights of TT gantry are operational now. 5. Leakage has been arrested from Bay no. 13 swivel joint. 6. The Emergency Trolley tools and tackles have been arranged and secured in their designated compartments. 7. The rectification of the Secondary Radar Gauge installed at Tank TK‑05 has been duly completed in accordance with the stipulated Purchase Order delivery date. The corrective action was executedwithin the scheduled timeline, and the equipment was fully rectified. 8. The Emergency Trolley tools and tackles have been arranged and secured in their designated compartments. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123559 | Closed | KUMAR KULDEEP | 2026-08-08 | 1. 5 No of Loading pumps in product pump house (2 no Ethanol/ 1 no MS pump and 1 No HSD pump) needs replacement of Oil cups and 1 No MS pump mild leakage observed from Mechanical seal 2. Rusting on support angles observed in TK-09. 3. Earth Pits Chamber required maintenance. (Civil work) 4. Few lights are non operational in TT Gantry. 5. In Bay 13, leakage from swivel joint is observed 6. Emergency Trolley placed in front of TT Gantry under the shed was checked. All material was placed. Location has been advised to place right material at designated place. 7. In Tank no 5, secondary radar gauge although showing the levels is not generating alarms. Spare parts advised by OEM M/s Emerson were ordered in Sep’25 with delivery period of 10-12 weeks. M/s Emerson has advised due to imported nature of components, delivery is getting delayed.Zone along with location will follow up rigorously for expediting the job. 8. Emergency Trolley placed in front of TT Gantry under the shed was checked. All material was placed. Location has been advised to place right material at designated place. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1221 | DELHI TERMINAL | 1. Maintenance of all the pumps has to be completed in time bound manner. 2. Support Angles to be painted. 3. Maintenance of Eartpit chamber where ever required. 4. ALL TT Gantry lights to be checked and maintained. 5. Leakage arested 6. Placement of allTools and Tacked ast designated place to be ensure 7. Secondary Radar Gauge to be rectified as pere PO delivery date 8. Emergency Trolley Tools and Tackles to be places in Designated compartment | SOD | Marketing | NZ | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011120ACN-2026-03-4000123559 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123559 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123559 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123559 | AUD-2026-03-2000011120ACN-2026-03-4000123559 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Scrap disposal activity has been completed. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123560 | Closed | KUMAR KULDEEP | 2026-08-08 | Out of total estimated scrap realization value of Rs.8.82 Lakhs, already realized Scrap value of Rs.8.9 Lakhs thru successful auctioning of 5 out of total 7 lots. Disposal of balance 2 lots is in progress. EDC of disposal of balance 2 lots is 28th Feb’26 and the location will be declared Scrap Free by 15th Mar’26 along with closure of AMDA as well. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1221 | DELHI TERMINAL | Balance 2 No. of Lots have been auctioned and Rs. 2..0 Lakhs are expexted & Scrap disposed by 15th March . | SOD | Marketing | NZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-15 | AUD-2026-03-2000011120ACN-2026-03-4000123560 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123560 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123560 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123560 | AUD-2026-03-2000011120ACN-2026-03-4000123560 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 57
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | The earlier issue pertaining to the smoke detector hooters has been rectified, and the necessary repair work has been completed. Post‑repair verification confirms that the smoke detector hooters are now fully functional and operational. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-03-4000123561 | Closed | KUMAR KULDEEP | 2026-08-08 | All Hooters in working condition except Smoke Deterctors Hooters | 5.2 | Functioning of all Hooters in control room | 1221 | DELHI TERMINAL | Smoke Detectors Hooters to be activated | SOD | Marketing | NZ | 2026-02-28 | INSTRUMENTATION OR ALARM FAILURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123561 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123561 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123561 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123561 | AUD-2026-03-2000011120ACN-2026-03-4000123561 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
|  | KUMAR KULDEEP | 2026-10-05 | Leaking nitrogen hose pipe replacement completed. Also training was imparted to contract workmen deployed on TT gantry on operationof Fire Extinguisher. | SR MGMT INSPECTION DELHI TML | 2026-05-27 17:00 | AUD-2026-06-2000014036 | 2026-05-25 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000141156 | Completed | KUMAR KULDEEP | 2026-10-05 | - During the visit, one portable foam type fire extinguishers of 50L capacity was operated near TLF Gantry 1 by a contract labor inthe presence of TAS Officer and HSE officer. While the foam generation was evident, leakages were found from the nitrogen hose pipeconnecting the external propellant cylinder to the foam cylinder. Further, the technique of closing the valve of the nitrogen cylinder was known only to the contract labour operating it. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1221 | DELHI TERMINAL | #NAME? | SOD | Marketing | NZ | 2026-07-30 |  | 1 |  | S1 | F1 | 2026-07-30 | AUD-2026-06-2000014036ACN-2026-06-4000141156 | DL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000014036ACN-2026-06-4000141156 | 2026-08-27 | 53.7538 | 332 | >20 | AUD-2026-06-2000014036 - ACN-2026-06-4000141156 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000014036ACN-2026-06-4000141156 |  | AUD-2026-06-2000014036ACN-2026-06-4000141156 | 21 |  | 27 | 80 | 3 | 3 | 48
GARG PANKAJ | 2026-10-05 | KUMAR KULDEEP | 2026-08-08 | Solar performance being monitred on daily basis, close followup being made with the vendor for pending rectifications. Hydrant pipeline has been painted and grass cutting activity has been completed. | SENIOR MGMT INSPECTION 1221 DELHI TML | 2026-01-21 17:00 | AUD-2026-03-2000011120 | 2026-01-19 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123562 | Closed | KUMAR KULDEEP | 2026-08-08 | Solar Plant Performance is down . Some scections of the Pipelines & Hydrant Pipelines getting rusted , Grass Cutting required in Solar Plant Area . | 6.1 |  | 1221 | DELHI TERMINAL | Solar Plant Performance to be monitored and improved . Some scections of the Pipelines & Hydrant Pipelines getting rusted , to be painted . Grass Cutting to be expedited . | SOD | Marketing | NZ | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 1 | ENVIRONMENTAL | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011120ACN-2026-03-4000123562 | DL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011120ACN-2026-03-4000123562 | 2026-08-27 | 53.7538 | 399 | >20 | AUD-2026-03-2000011120 - ACN-2026-03-4000123562 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011120ACN-2026-03-4000123562 | AUD-2026-03-2000011120ACN-2026-03-4000123562 | 21 | 21 | 26 | 80 | 3 | 3 | 26 | 57
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Damaged dust cover lock's identified & sent for replacement. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153074 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Yes complied. Checked TT MH41AU3177 & MH41AU8724. EM Lock dust cover found damage. | 3.5 | EM Lock SOP compliance verified | 1397 | HPCL MANMAD IRD | EM locks with damaged dust covers shall be replaced by Sterna at the earliest. | SOD | Marketing | WZ | 2026-09-16 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-16 | AUD-2026-09-2000017452ACN-2026-09-4000153074 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153074 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153074 | 532 | 8294 | 21 | 8294 | 33 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153074 | AUD-2026-09-2000017452ACN-2026-09-4000153074 | 21 | 21 | 27 | 80 | 7 | 7 | 55 | 58
SINGH AMAR BAHADUR | 2026-10-06 | DINESH KUMAR | 2026-10-06 | Grass cutting completed | LOCATION VISIT-JALANDHAR_19-21.08.26 | 2026-08-21 | AUD-2026-09-2000017550 | 2026-08-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151902 | Closed | DINESH KUMAR | 2026-10-06 | Grass/vegetation has increased due to rainy season. | 3.16 | Earth pits / boundary / vegetation control checked | 1254 | JALANDHAR DEPOT | Grasscutting to be done in all the operating areas. | SOD | Marketing | NFZ | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-15 | AUD-2026-09-2000017550ACN-2026-09-4000151902 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017550ACN-2026-09-4000151902 | 2026-08-21 | 59.7538 | 400 | >20 | AUD-2026-09-2000017550 - ACN-2026-09-4000151902 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017550ACN-2026-09-4000151902 | AUD-2026-09-2000017550ACN-2026-09-4000151902 | 21 | 21 | 27 | 80 | 0 | -21 | 55 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | The expiry of TAS credentials for each officer maintained on a half-yearly basis now. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153075 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | TAS Credentials of some officers found expired. | 6.1 | General | 1397 | HPCL MANMAD IRD | The expiry of TAS credentials for each officer should be maintained on a half-yearly basis. | SOD | Marketing | WZ | 2026-09-16 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-16 | AUD-2026-09-2000017452ACN-2026-09-4000153075 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153075 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153075 | 532 | 8294 | 21 | 8294 | 33 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153075 | AUD-2026-09-2000017452ACN-2026-09-4000153075 | 21 | 21 | 27 | 80 | 7 | 7 | 55 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Transformer silica gel replaced | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153076 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Transformer Silica gel found pink. | 6.2 | General | 1397 | HPCL MANMAD IRD | Transformer silica gel to be replaced immediately. | SOD | Marketing | WZ | 2026-09-16 | INSUFFICIENT SUPERVISION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-09-16 | AUD-2026-09-2000017452ACN-2026-09-4000153076 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153076 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153076 | 532 | 8294 | 21 | 8294 | 33 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017452ACN-2026-09-4000153076 | AUD-2026-09-2000017452ACN-2026-09-4000153076 | 21 | 21 | 27 | 80 | 7 | 7 | 55 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | "Water Checked & Found Nil” stamping being done on every TT. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153077 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | The “Water Checked & Found Nil” stamp was not found on the invoice. | 6.3 | General | 1397 | HPCL MANMAD IRD | “Water Checked & Found Nil” stamping to be done on each invoice. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153077 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153077 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153077 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017452ACN-2026-09-4000153077 | AUD-2026-09-2000017452ACN-2026-09-4000153077 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Old safety policy board replaced. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection |  | ACN-2026-09-4000153078 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Old safety policy found near Ingate. | 6.4 | General | 1397 | HPCL MANMAD IRD | Old safety policy board to be replaced. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153078 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153078 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153078 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153078 | AUD-2026-09-2000017452ACN-2026-09-4000153078 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Structures painted as advised. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153079 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | The portion of the gantry structure that was previously buried in soil and is now exposed due to soil removal shall be repainted. | 6.5 | General | 1397 | HPCL MANMAD IRD | Structure to be painted as advised. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153079 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153079 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153079 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153079 | AUD-2026-09-2000017452ACN-2026-09-4000153079 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Valve closed properly. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153080 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Valves on the hydrant line were found leaking. | 6.6 | General | 1397 | HPCL MANMAD IRD | Valves to be closed properly, incase leakage still not stopped same is to be replaced. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153080 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153080 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153080 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153080 | AUD-2026-09-2000017452ACN-2026-09-4000153080 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Valve replaced. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153081 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | The valve of the replenishment pipe of the eyewash tank near the VRU was found broken | 6.7 | General | 1397 | HPCL MANMAD IRD | Valve to be replaced at the earliest. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153081 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153081 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153081 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153081 | AUD-2026-09-2000017452ACN-2026-09-4000153081 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
MEHETRE KIRAN K | 2026-10-06 | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Done as advised. | MNAMAD LOCATION VIST DATED08.09.2026 | 2026-09-08 | AUD-2026-09-2000017452 | 2026-09-08 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153082 | Closed | PRITAM ANIL SURYAWANSHI | 2026-10-06 | Oil marks observed below flange of HSD line infront of TK1 | 6.8 | General | 1397 | HPCL MANMAD IRD | Nut bolts shall be tightened, and the underside of the flange shall be cleaned thoroughly. The oil marks below the flange shall also be cleaned, and the area shall be monitored to check whether any fresh oil marks reappear. | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-30 | AUD-2026-09-2000017452ACN-2026-09-4000153082 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017452ACN-2026-09-4000153082 | 2026-09-08 | 41.7538 | 400 | >20 | AUD-2026-09-2000017452 - ACN-2026-09-4000153082 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017452ACN-2026-09-4000153082 | AUD-2026-09-2000017452ACN-2026-09-4000153082 | 21 | 21 | 27 | 80 | 7 | 7 | 57 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | It is related to Direct sale SBU. Issue has been taken up but response is awaited. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150328 | Closed | RAHUL RAJ | 2026-10-06 | UG storage tank lying near pond area to be disposed. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150328 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150328 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150328 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150328 | AUD-2026-08-2000016904ACN-2026-09-4000150328 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | 1. All the faulty panel has replaced with spare panel & Weather is also ok. Now, Solar units are being generated as per design 2. Fire Engine has been repaired but still getting issues as life cycle Is completed. Replacement of fire engine is approved under NPCB 2026-27. LPR has been sent to HQO for tendering | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000150327 | Closed | RAHUL RAJ | 2026-10-06 | 1. Solar generation for month Jul'26 was reviewed and found under performing. As per location, performance is low due to rainy weather. 2. Smoke is observed from exhaust pipe joint with engine for FE 3 and 2. 3. Checked crtical alarm from Fire engine 2 and found working. 4. Fire engines are tripping on overspeed alarm. | 4.2 | Maintenance activities reviewed | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150327 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150327 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150327 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150327 | AUD-2026-08-2000016904ACN-2026-09-4000150327 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Observation scheduled for closure as of Aug'26 has been closed | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150325 | Closed | RAHUL RAJ | 2026-10-06 | Location to close observation scheduled for closure as of Aug'26 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-05 | AUD-2026-08-2000016904ACN-2026-09-4000150325 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150325 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150325 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150325 | AUD-2026-08-2000016904ACN-2026-09-4000150325 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Contract workmen has been advised to follow the safety rules without any deviation. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150324 | Closed | RAHUL RAJ | 2026-10-06 | Housekeeping is satisfactory. Contract workmen found not using PPE at calibration tower on date 06.08.2026 | 3.15 | Housekeeping & PPE usage checked | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-05 | AUD-2026-08-2000016904ACN-2026-09-4000150324 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150324 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150324 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150324 | AUD-2026-08-2000016904ACN-2026-09-4000150324 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Surplus details are updated on Portal. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150323 | Closed | RAHUL RAJ | 2026-10-05 | 1. Comments are being recorded for abnormal variation. 2. Updation of suplus assets in pending. 12 inch DBBV, strainers, UG vertical pumps and MFM are found in godown hoever same were not updated in the portal. | 3.9 | Abnormal variations / unused assets reviewed | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-05 | AUD-2026-08-2000016904ACN-2026-09-4000150323 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150323 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150323 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150323 | AUD-2026-08-2000016904ACN-2026-09-4000150323 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Emptiness of Ethanol is being done by two officers. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150322 | Closed | RAHUL RAJ | 2026-10-05 | Dip checked for TT GJ39T7915 Chamber 1: (-10 mm), Chamber 2: (-10 mm), chamber 3: (-10 mm), chamber 4: (-5 mm), chamber 5: (-6 mm),Chamber 6: (-10 mm). Upon review of CCTV, Emptiness of ethanol TT is not being checked by two officers at location. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-05 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-05 | AUD-2026-08-2000016904ACN-2026-09-4000150322 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150322 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150322 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150322 | AUD-2026-08-2000016904ACN-2026-09-4000150322 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Time clock and CCTV stamp of CCTV has been corrected during the AMC visit dt 08.09.2026 | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150319 | Closed | RAHUL RAJ | 2026-10-05 | 46 cameras out of 51 are currently working. Time clock and CCTV stamp of CCTV is not correct. | 2.6 | CCTV functioning checked | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150319 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150319 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150319 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150319 | AUD-2026-08-2000016904ACN-2026-09-4000150319 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Training has been conducted on electrical fire response on 01.10.2026. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150317 | Closed | RAHUL RAJ | 2026-10-05 | Location has been conducting the mock fire drills on monthly basis covering various scenarios recommended in ERDMP. Report reviewed for mock drill month Jul'26. Location of Emergency1: MCC room electrical panel, Location of Emergency2: Nil. Observation recorded in mock drill Refersher training on electrical fire response. Compliance pending. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-15 | AUD-2026-08-2000016904ACN-2026-09-4000150317 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150317 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150317 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150317 | AUD-2026-08-2000016904ACN-2026-09-4000150317 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Surprise night inspection being carried out forthnightly as per circular and reports are available | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150315 | Closed | RAHUL RAJ | 2026-10-05 | Surprise night inspection are not being done by location regularly. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016904ACN-2026-09-4000150315 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150315 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150315 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150315 | AUD-2026-08-2000016904ACN-2026-09-4000150315 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-05 | Security Guards has been sensitized the criticality. Now being done regularly | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150318 | Closed | RAHUL RAJ | 2026-10-05 | During review of CCTV footage of date 17.07.2026, security checks for electrician were not carried out. However same was done on date 18.07.2026 | 2.4 | Security alertness checked (night-halt / surprise checks) | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-15 | AUD-2026-08-2000016904ACN-2026-09-4000150318 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150318 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150318 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016904ACN-2026-09-4000150318 | AUD-2026-08-2000016904ACN-2026-09-4000150318 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | TREM Card is updated and distributed to TT Crew | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131776 | Closed | RAHUL RAJ | 2026-10-06 | TT crew of CG07BM2570, GJ19Y8923, DD01P9976, GJ15AV8919 & GJ26T5166 were enquired about road side emergency. TT crew is aware of same. However upon verification of HPCL emergency contact number printed over TREM card were found out of service. | 2.15 | TT crew roadside emergency procedures checked | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131776 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131776 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131776 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131776 | AUD-2026-05-2000012564ACN-2026-05-4000131776 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Re-Calibration done on 13.08.2026 | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131778 | Closed | RAHUL RAJ | 2026-10-06 | Post loading dip checking done, Variation observed in TT number CG07BM2570 loaded at bay no 7. Variation observed in chamber 1: 0 mm, chamber 2: 0 mm, chamber 3: +7 mm, chamber 4: +7 mm & chamber 5: +10 mm. | 3.2 | Post-loading dip checks verified | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131778 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131778 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131778 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131778 | AUD-2026-05-2000012564ACN-2026-05-4000131778 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Ethanol Blending is being checked regularly and found within limited | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131780 | Closed | RAHUL RAJ | 2026-10-06 | Ethanol blending checked for TT number CG07BM2570, loaded at bay no 7. Ethanol blending found 15%. Location officer shall randomly carry out ethanol blending check at gantry and record shall be maintained. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131780 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131780 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131780 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131780 | AUD-2026-05-2000012564ACN-2026-05-4000131780 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Surplus item details are updated on Portal | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131783 | Closed | RAHUL RAJ | 2026-10-06 | Comments are being recorded for abnormal variation. Location to update surplus/idle assets in surplus portal. | 3.9 | Abnormal variations / unused assets reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131783 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131783 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131783 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131783 | AUD-2026-05-2000012564ACN-2026-05-4000131783 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | MOC has been taken | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131785 | Closed | RAHUL RAJ | 2026-10-06 | Location has not taken MOC for removal for flood light tower | 3.17 | MOC status reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131785 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131785 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131785 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131785 | AUD-2026-05-2000012564ACN-2026-05-4000131785 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | All the points are closed as per schedule. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131786 | Closed | RAHUL RAJ | 2026-10-06 | As per SAP, audit compliance is 54% for all audits (PM - MDSA Audit, PM - OISD- External Safety Audit, PM - SAFE100 Self Safety Audit, PM - Senior Management Inspection, PM - SOD TANK AG CR, PM - SOD TANK AG EFR, PM - SOD TANK AG IFR, PM - SOD TANK UG). Locationhas closed only 75% audit observation which are scheduled for closure in May'26. Supporting document for audit observation closed in SAP are not attached by location | 3.18 | OISD/MDSA/SSA compliance reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012564ACN-2026-05-4000131786 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131786 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131786 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131786 | AUD-2026-05-2000012564ACN-2026-05-4000131786 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Samples are being disposed of in the presence of officer and records of it are being maintained duly signed by officer. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131791 | Closed | RAHUL RAJ | 2026-10-06 | TLF Sample prior and post of date 05.04.2026 and 06.03.2026 were disposed of physically however above mentioned date sample were found kept in sample room, same were not disposed. No remarks was updated for same. | 6.2 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131791 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131791 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131791 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131791 | AUD-2026-05-2000012564ACN-2026-05-4000131791 | 21 | 21 | 27 | 80 | 2 | 2 | 40 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | TK-14 external inspection is carried out and report is submitted to Zone | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000131798 | Closed | RAHUL RAJ | 2026-10-06 | Location to carry out external inspection of Tank no 14. | 6.9 |  | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012564ACN-2026-05-4000131798 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131798 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131798 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012564ACN-2026-05-4000131798 | AUD-2026-05-2000012564ACN-2026-05-4000131798 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 58
GIRI ANJANI KUMAR | 2026-10-06 | RAHUL RAJ | 2026-10-06 | Corrective Action has been Taken | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122722 | Closed | RAHUL RAJ | 2026-10-06 | • Solar generation for a period Apr’25 to Jan’26 was reviewed and observed that frequent inverter tripping was happened due to which generation on those days were affected. Location has been advised to ensure close monitoring of solar generation specially of 50 KWp unit for generation as per design basis. • Operation of Fire Engines were checked and found functional as per requirement. Fire Engine No-03 (standby) is under maintenance. Location has been advised to follow up with AMC service provider for restoration of FE No-03 within timelines. | 4.2 | Maintenance activities reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122722 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122722 | 2026-08-06 | 74.7538 | 400 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122722 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122722 | AUD-2026-03-2000011215ACN-2026-03-4000122722 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | point is getting repeated in Q1 26-27 SMA | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000121655 | Closed | MEENA NITESH KUMAR | 2026-09-08 | Allotment of Budget for Revamping of TKMS01, TKMS02 and TK17. These tanks are not in use due to maintenance issues. | 1.3 | Pending issues reviewed | 1334 | HPCL REWARI IRD | Budget of Rs 2.75 crores sought from HQO. However no budget has been allocated yet. | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011158ACN-2026-03-4000121655 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121655 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121655 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121655 | AUD-2026-03-2000011158ACN-2026-03-4000121655 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Necessary Action is being taken and same is getting repeated in Q1 26-27 SMA | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121364 | Closed | MEENA NITESH KUMAR | 2026-09-08 | Allotment of Budget for Revamping of TKMS01, TKMS02 and TK17. These tanks are not in use due to maintenance issues. | 1.3 | Pending issues reviewed | 1334 | HPCL REWARI IRD | Budget of Rs 2.75 crores sought from HQO. However no budget has been allocated yet. | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-02-2000011004ACN-2026-02-4000121364 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121364 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121364 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121364 | AUD-2026-02-2000011004ACN-2026-02-4000121364 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 | Necessary budget has been received for TK01 TK02 TK17 dated 01.10.2026 | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153342 | Closed | SINGH YUGAL KISHOR | 2026-10-03 | 1. Repair of of TKMS01, TKMS02 and TK17. These tanks are not in use due to maintenance issues. 2. Location has sent proposal thru Zone for 6 Nos addtional bays , One addtional MS Tank of 2000 Kl and two HSD Tank of 3000 KL and 3900 KL as cost of 41 Crores . Followup to be maintained | 1.3 | Pending issues reviewed | 1334 | HPCL REWARI IRD | Location to proposal for budget for Rs.2.75 Crores under NPCB: 2026-27 (contingency). has been rejected by HQO. Location has been adised to take services of consultant for optimisation of repair cost | SOD | Marketing | NZ | 2026-12-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-12-30 | AUD-2026-09-2000017364ACN-2026-09-4000153342 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153342 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153342 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017364ACN-2026-09-4000153342 | AUD-2026-09-2000017364ACN-2026-09-4000153342 | 21 | 21 | 27 | 80 | 1 | 1 | 70 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 | Necessary Action is being taken | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121365 | Closed | SHEKHAR RAJ | 2026-02-25 | Location is operating with 1+5 against the approved manpower of 1+7, additional manpower is required for Rewari IRD | 1.5 | HQO / Zonal support required identified | 1334 | HPCL REWARI IRD | Matter taken up with HQO by Zonal O&D Head | SOD | Marketing | NZ | 2026-06-30 | HARSH WORKING CONDITIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-02-2000011004ACN-2026-02-4000121365 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121365 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121365 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121365 | AUD-2026-02-2000011004ACN-2026-02-4000121365 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Circulars has been given the all offciers and acknowlegement taken | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000121657 | Closed | MEENA NITESH KUMAR | 2026-09-08 | Interaction was carried out at Rewari Terminal in presence of LIC and all location officers on expectations from location and each officer, compliance to recent HQO/Zonal circulars, improvement plans. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1334 | HPCL REWARI IRD | All circular compliance shall be reviewed by LIC and confirmation to be provided | SOD | Marketing | NZ | 2026-03-30 | OUTDATED OR COMPLEX SOPS | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-30 | AUD-2026-03-2000011158ACN-2026-03-4000121657 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121657 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121657 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011158ACN-2026-03-4000121657 | AUD-2026-03-2000011158ACN-2026-03-4000121657 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Point repeated in Q1 26-27 SMA | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121372 | Closed | MEENA NITESH KUMAR | 2026-09-08 | HVLR - Total 06 Nos of HVLR is available at the Location. HVLR No. 05 – Checked for its movement in all directions and found satisfactory. HVLR No: 02 has been operated by Sh Rohit Katiyar. The thruput of HVLR is 1000 GPM. The officer is found to be well acquainted with the operations of the HVLR. RSFPS - Only one tank, TK-26, is equipped with an RSFPS and its operation was checked from the field. The RSFPS operated successfully, and foam was dispersed evenly along the entire rim seal of the tank. However, it is brought to notice that testing of the RSFPS cannot be carried out from the control room due to an issue with the PC on which the required software is installed. HCD - Total 16 Nos of HCD available at the location. Out of which 07 nos are Open path and 09 Nos are Point type HCD. All HCD's are operatinal Open Path Type HCD No: 01 located at Pump House operated; and tested for 20% , 40% LEL using test film. Point type HCD No: 03 Located at Pump House operated; and found to be operated at 39% LEL. ESD - Tot 14 No of ESD available at the location. The Functionality of ESD has been checked during Mock drill conducted on 11th Feb'26 and found satisfactory. ESD NO: 02 activated placed in Control room. The Functionality of ESD has been checked during Off SHift Mock drill conducted on 12th Feb'26 and found satisfactory. ESD NO: 06 activated placed in front of Product pump House | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1334 | HPCL REWARI IRD | The feature of testing of RSFPS from Control room to be made operational. | SOD | Marketing | NZ | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000011004ACN-2026-02-4000121372 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121372 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121372 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121372 | AUD-2026-02-2000011004ACN-2026-02-4000121372 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Point is repeating in Q1 26-27 | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121373 | Closed | MEENA NITESH KUMAR | 2026-09-08 | It has been observed that No Trained Security personnel is having HAZ endorsement to move TT in Gantry. However, DCT/TPT are havingHAZ endorsement to move TT from gantry 50-100 m in case of emergency. Details of TT Drivers (enclosed): 1. Shri. Rakesh Kumar - DL No: UP62 20090015529 Valid till 12/07/2030 , HAZ Endorsement valid till 20-04-2028 2. Shri. Lilu Ram - DL No: RJ10 20050019521 valid till 07-08-2028 , HAZ Endorsement valid till 07-08-2028 However, on checking records of driver maintained at location it was found that few TT drivers of haryana were not having HAZ Endorsed Licence although Training certificates for carrying Hazardous goods is available in records. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1334 | HPCL REWARI IRD | Location to ensure 100% HAZ endorsement on drivers licence | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-02-2000011004ACN-2026-02-4000121373 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121373 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121373 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121373 | AUD-2026-02-2000011004ACN-2026-02-4000121373 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | EM Lock SOP compliance verified | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121669 | Closed | MEENA NITESH KUMAR | 2026-09-08 | EM lock checked using Intelligent Key was done for six no of TTs by Zonal head Intelligent key and as well as LIC' intelligent key and online report as per requirement was submitted after checking. Plastic dust cover were found broken in few locks & location has been advise to replace them and confirm to zone by 28th Feb 2026. One Lock no HE 7447 of TT number HR61E9619 found supected. New lock issued and suspected lock will be sent for OEM inspection . Location will update the state on portal. | 3.5 | EM Lock SOP compliance verified | 1334 | HPCL REWARI IRD | Broken Plastic dust covers of locks to be replaced | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121669 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121669 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121669 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121669 | AUD-2026-03-2000011158ACN-2026-03-4000121669 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Necessary Action is taken | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121377 | Closed | MEENA NITESH KUMAR | 2026-09-08 | EM lock checked using Intelligent Key was done for six no of TTs by Zonal head Intelligent key and as well as LIC' intelligent key and online report as per requirement was submitted after checking. Plastic dust cover were found broken in few locks & location has been advise to replace them and confirm to zone by 28th Feb 2026. One Lock no HE 7447 of TT number HR61E9619 found supected. New lock issued and suspected lock will be sent for OEM inspection . Location will update the state on portal. | 3.5 | EM Lock SOP compliance verified | 1334 | HPCL REWARI IRD | Broken Plastic dust covers of locks to be replaced | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011004ACN-2026-02-4000121377 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121377 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121377 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121377 | AUD-2026-02-2000011004ACN-2026-02-4000121377 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Necessary Action is taken | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121378 | Closed | MEENA NITESH KUMAR | 2026-09-08 | Out of total 2235 tank reconciliations done during the period 1st Oct'25 to 10th Feb'26, only 90 instances were done in manual mode. Reconciliation based on auto dip was done for 95.97% of tanks during the period. Out of the 90 reconciliations done based on manual dips, 32 instances were for 31st Oct'26, 30th Nov'25, 31st Dec'25 & 31st Jan'26 when manual dip entries were mandated by HQO. | 3.8 | Auto vs Manual reconciliation checked | 1334 | HPCL REWARI IRD | Location to reduce the instance of manual Reconciliation and update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121378 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121378 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121378 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121378 | AUD-2026-02-2000011004ACN-2026-02-4000121378 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Auto vs Manual reconciliation checked | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121670 | Closed | MEENA NITESH KUMAR | 2026-09-08 | Out of total 2235 tank reconciliations done during the period 1st Oct'25 to 10th Feb'26, only 90 instances were done in manual mode. Reconciliation based on auto dip was done for 95.97% of tanks during the period. Out of the 90 reconciliations done based on manual dips, 32 instances were for 31st Oct'26, 30th Nov'25, 31st Dec'25 & 31st Jan'26 when manual dip entries were mandated by HQO. | 3.8 | Auto vs Manual reconciliation checked | 1334 | HPCL REWARI IRD | Location to reduce the instance of manual Reconciliation and update google sheet provided by Zone for all the earlier instances of manual reconciliation with reasons. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121670 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121670 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121670 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121670 | AUD-2026-03-2000011158ACN-2026-03-4000121670 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Jocky pump maintenance is done and working now | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000121680 | Closed | MEENA NITESH KUMAR | 2026-09-08 | All maintenance records were examined and found all activities were completed in defined time line. Further, Jockey Pump maintenance under progress. | 4.2 |  | 1334 | HPCL REWARI IRD | Maintaine of Jockey pump to be done in time bound manner | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121680 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121680 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121680 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121680 | AUD-2026-03-2000011158ACN-2026-03-4000121680 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | maintenance is done and Pump is working now | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121388 | Closed | MEENA NITESH KUMAR | 2026-09-08 | All maintenance records were examined and found all activities were completed in defined time line. Further, Jockey Pump maintenance under progress. | 4.2 | Maintenance activities reviewed | 1334 | HPCL REWARI IRD | Maintaine of Jockey pump to be done in time bound manner | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121388 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121388 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121388 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121388 | AUD-2026-02-2000011004ACN-2026-02-4000121388 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 58
MANDAL PRATAPKUMAR | 2026-10-07 | NILABH | 2026-10-07 | SOP for Sluice Gate Operation displayed. | ZONAL INSPECTION Q2-2026-27 KANPUR | 2026-08-26 17:00 | AUD-2026-08-2000017157 | 2026-08-24 00:35 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000150278 | Closed | NILABH | 2026-10-07 | SOP for Sluice Gate Operation not displayed. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1305 | KANPUR TERMINAL | SOP to be displayed. | SOD | Marketing | NCR | 2026-09-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-15 | AUD-2026-08-2000017157ACN-2026-08-4000150278 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017157ACN-2026-08-4000150278 | 2026-08-26 17:00 | 54.0455 | 401 | >20 | AUD-2026-08-2000017157 - ACN-2026-08-4000150278 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017157ACN-2026-08-4000150278 | AUD-2026-08-2000017157ACN-2026-08-4000150278 | 21 | 21 | 27 | 80 | 4 | 4 | 55 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 | Necessary Action is being taken | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000121391 | Closed | SHEKHAR RAJ | 2026-02-25 | A total of 148 instances of bay reallocation are appearing during the period 1st Jan'26 to 10th Feb'26. Out of these, 43 instances are on account of driver not reported. Apparently, biometric verification of all the TT drivers is not enabled for all the TT drivers which is resulting in multiple card swiping by one driver for many TTs and when the turn of the TT comes, actual TT is not available for loading. Location has been advised to enable Bio-metric verification at R1 for all the drivers to avoid bay re-allocation on this account. EDC 15th Mar’26. Two MS Tanks (TK-1 and Tk-2 of Capacity 590 KL Each) and one Slop Tank (TK-17-500 KL) are under Outage for Major Repair. Direction is sought from HQO on whether these tanks are to be repaired or New Tank is to be Built. Proposals for both the Options have been submitted | 6.1 | High priority areas requiring immediate action. | 1334 | HPCL REWARI IRD | a) Biometric registration to be ensured | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011004ACN-2026-02-4000121391 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121391 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121391 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121391 | AUD-2026-02-2000011004ACN-2026-02-4000121391 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Point is repeating in q1 sma | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000121683 | Closed | MEENA NITESH KUMAR | 2026-09-08 | A total of 148 instances of bay reallocation are appearing during the period 1st Jan'26 to 10th Feb'26. Out of these, 43 instances are on account of driver not reported. Apparently, biometric verification of all the TT drivers is not enabled for all the TT drivers which is resulting in multiple card swiping by one driver for many TTs and when the turn of the TT comes, actual TT is not available for loading. Location has been advised to enable Bio-metric verification at R1 for all the drivers to avoid bay re-allocation on this account. EDC 15th Mar’26. Two MS Tanks (TK-1 and Tk-2 of Capacity 590 KL Each) and one Slop Tank (TK-17-500 KL) are under Outage for Major Repair. Direction is sought from HQO on whether these tanks are to be repaired or New Tank is to be Built. Proposals for both the Options have been submitted | 6.1 | High priority areas requiring immediate action. | 1334 | HPCL REWARI IRD | a) Biometric registration to be ensured | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121683 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121683 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121683 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121683 | AUD-2026-03-2000011158ACN-2026-03-4000121683 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 |  | Q1 2627 SR MGMT AUDIT REWARI TRMINAL | 2026-06-11 15:00 | AUD-2026-06-2000013601 | 2026-06-09 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000139983 | Closed |  |  | Allotment of Budget for Revamping of TKMS01, TKMS02 and TK17. These tanks are not in use due to maintenance issues. | 1.3 | Pending issues reviewed | 1334 | HPCL REWARI IRD | Location to originate proposal for seeking budget for Rs.2.75 Crores under NPCB: 2026-27 (contingency). | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013601ACN-2026-06-4000139983 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013601ACN-2026-06-4000139983 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-06-2000013601 - ACN-2026-06-4000139983 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013601ACN-2026-06-4000139983 | AUD-2026-06-2000013601ACN-2026-06-4000139983 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 |  | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000121656 | Closed |  |  | Location is operating with 1+5 against the approved manpower of 1+7, additional manpower is required for Rewari IRD | 1.5 | HQO / Zonal support required identified | 1334 | HPCL REWARI IRD | Matter taken up with HQO by Zonal O&D Head | SOD | Marketing | NZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-06-30 | AUD-2026-03-2000011158ACN-2026-03-4000121656 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121656 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121656 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011158ACN-2026-03-4000121656 | AUD-2026-03-2000011158ACN-2026-03-4000121656 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
TYAGI ATUL | 2026-10-07 | SINGH YUGAL KISHOR | 2026-10-03 |  | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000153344 | Closed |  |  | TAS officer to focus on improvement of TT exit time and LPM for the location- Last inspection's pending point. | 1.8 | Improvement plans discussed | 1334 | HPCL REWARI IRD | XX | SOD | Marketing | NZ | 2026-12-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-12-15 | AUD-2026-09-2000017364ACN-2026-09-4000153344 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153344 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153344 | 532 | 8294 | 21 | 8294 | -56 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017364ACN-2026-09-4000153344 | AUD-2026-09-2000017364ACN-2026-09-4000153344 | 21 | 21 | 27 | 80 | 1 | 1 | 68 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 |  | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121664 | Closed |  |  | HVLR - Total 06 Nos of HVLR is available at the Location. HVLR No. 05 – Checked for its movement in all directions and found satisfactory. HVLR No: 02 has been operated by Sh Rohit Katiyar. The thruput of HVLR is 1000 GPM. The officer is found to be well acquainted with the operations of the HVLR. RSFPS - Only one tank, TK-26, is equipped with an RSFPS and its operation was checked from the field. The RSFPS operated successfully, and foam was dispersed evenly along the entire rim seal of the tank. However, it is brought to notice that testing of the RSFPS cannot be carried out from the control room due to an issue with the PC on which the required software is installed. HCD - Total 16 Nos of HCD available at the location. Out of which 07 nos are Open path and 09 Nos are Point type HCD. All HCD's are operatinal Open Path Type HCD No: 01 located at Pump House operated; and tested for 20% , 40% LEL using test film. Point type HCD No: 03 Located at Pump House operated; and found to be operated at 39% LEL. ESD - Tot 14 No of ESD available at the location. The Functionality of ESD has been checked during Mock drill conducted on 11th Feb'26 and found satisfactory. ESD NO: 02 activated placed in Control room. The Functionality of ESD has been checked during Off SHift Mock drill conducted on 12th Feb'26 and found satisfactory. ESD NO: 06 activated placed in front of Product pump House | 2.11 | Point is getting repeated q1 SMA 25-26 | 1334 | HPCL REWARI IRD | The feature of testing of RSFPS from Control room to be made operational. | SOD | Marketing | NZ | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-03-2000011158ACN-2026-03-4000121664 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121664 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121664 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121664 | AUD-2026-03-2000011158ACN-2026-03-4000121664 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 58
TYAGI ATUL | 2026-10-07 | MEENA NITESH KUMAR | 2026-09-08 | Point is getting repeated in Q1 SMA 26-27 | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121665 | Closed | MEENA NITESH KUMAR | 2026-09-08 | It has been observed that No Trained Security personnel is having HAZ endorsement to move TT in Gantry. However, DCT/TPT are havingHAZ endorsement to move TT from gantry 50-100 m in case of emergency. Details of TT Drivers (enclosed): 1. Shri. Rakesh Kumar - DL No: UP62 20090015529 Valid till 12/07/2030 , HAZ Endorsement valid till 20-04-2028 2. Shri. Lilu Ram - DL No: RJ10 20050019521 valid till 07-08-2028 , HAZ Endorsement valid till 07-08-2028 However, on checking records of driver maintained at location it was found that few TT drivers of haryana were not having HAZ Endorsed Licence although Training certificates for carrying Hazardous goods is available in records. | 2.13 | Point is getting repeated in Q1 SMA 26-27 | 1334 | HPCL REWARI IRD | Location to ensure 100% HAZ endorsement on drivers licence | SOD | Marketing | NZ | 2026-06-30 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011158ACN-2026-03-4000121665 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121665 | 2026-09-10 17:00 | 39.0455 | 401 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121665 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121665 | AUD-2026-03-2000011158ACN-2026-03-4000121665 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 58
|  | AGARWAL RAVI KUMAR | 2026-10-09 | 1. Solar generation is generating as per design 2. All the fire Engine is working fine 3. Checklist has been corrected 4. Same shall be revised and corrected from next quarter 5. Calibration of Pressure Gauges is completed. Stickers printing under process. 6. HSD bottom loading arm of bay no 4 is arrested 7. Hooter for dyke valve for dyke no 2 is replaced. Now, working fine 8. Issue has been rectified 9 . Touch up paint has been done | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131788 | Completed | AGARWAL RAVI KUMAR | 2026-10-09 | 1. Solar generation for month may'26 was reviewed and found under performing. As per location, alignment of solar panel is correct as per third party report. Location to correct alignment of panel or priority. 2. Fire Engine No-03 (standby) is under maintenance.Location has been advised to follow up with AMC service provider for restoration of FE No-03 within timelines. 3. Reviewed work permits 180000105713 (Fabrication civil & mechanical). filling of checklist is found not as per site condition. 4. As per field, strainer cleaning is due 16.03.2026. Location confirmed strainer cleaning has been completed in apr'26 however change of date in pending. From the records, it is observed that location is putting cleaning date same for all strainer in spite of strainer being cleaned of different dates. Which is not reflecting actual strainer cleaning date. 5. Due date calibration for pressure gauge is not updatedin TLF pump house. 6. Leakage observed in HSD bottom loading arm of bay no 4. 7. Hooter for dyke valve for dyke no 2 is under repair. 8. Dyke valve of dyke no 2 was found in open condition however same not giving any audio/visual alarm in the field. Same was found bypassed by using piece of wood. 9. Location is carrying out hydrant line painting. For section in tank farm area, Top of hydrant line was painted however bottom part of line which is not visible normally and gets rusted first was not painted by the vendor. | 4.2 | Maintenance activities reviewed | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 |  | 1 |  | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131788 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131788 | 2026-08-06 | 74.7538 | 291 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131788 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131788 |  | AUD-2026-05-2000012564ACN-2026-05-4000131788 | 21 |  | 27 | 80 | 2 | 2 | 42
SABLE RONAK MOHANKUMAR | 2026-10-09 | SINGH PREETI | 2026-10-09 | RFD No. 1008547 initiated and approved and Sent to CPO for TAS Scrap. Surplus material identified, segregated and kept at designated place in store room and list also prepared. PM Activities being done regularly as per schedule and records being maintained. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000140177 | Closed | SINGH PREETI | 2026-10-09 | Location to ensure disposal of scrap material and shifting of surplus material to required location. Location shall carry out preventive maintenace activity properly in the field. | 1.8 | Improvement plans discussed | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-08-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-30 | AUD-2026-06-2000013929ACN-2026-06-4000140177 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140177 | 2026-08-22 22:00 | 57.8372 | 403 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140177 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140177 | AUD-2026-06-2000013929ACN-2026-06-4000140177 | 21 | 21 | 27 | 80 | 1 | 1 | 52 | 58
SABLE RONAK MOHANKUMAR | 2026-10-09 | SINGH PREETI | 2026-10-09 | Occupancy sensors installed for lighting, ACs for energy savings. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140814 | Closed | SINGH PREETI | 2026-10-09 | Occupancy sensors to be installed for lighting, ACs for energy savings. | 6.17 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140814 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140814 | 2026-08-22 22:00 | 57.8372 | 403 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140814 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140814 | AUD-2026-06-2000013929ACN-2026-06-4000140814 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 58
SABLE RONAK MOHANKUMAR | 2026-10-09 | SINGH PREETI | 2026-10-09 | Delay in opening water MOV valve of HVLR 4&2 issue rectified now. Corrosion removed, greasing done and valves operating smoothly now. Checked after maintainance and MOVs are now operating ok, without delay. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150755 | Closed | SINGH PREETI | 2026-10-09 | HVLR 4& 2 checked. Delay is observed in opening water MOV valve. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150755 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150755 | 2026-08-22 22:00 | 57.8372 | 403 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150755 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150755 | AUD-2026-08-2000016905ACN-2026-09-4000150755 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 58
|  | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Dip Elimination file note No 136395 Initiated On :17-Sep-2026 | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000143371 | Completed | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Improvement plans regarding TT dip elimination discussed | 1.8 | Improvement plans discussed | 3708 | VISAKH NBOT | TT Dip elimination file note to be initiated after necessary data collection | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143371 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143371 | 2026-09-18 17:30 | 31.0247 | 302 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143371 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015047ACN-2026-07-4000143371 |  | AUD-2026-07-2000015047ACN-2026-07-4000143371 | 21 |  | 27 | 80 | 2 | 1 | 44
|  | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Dip Elimination file note No 136395 Initiated On :17-Sep-2026 | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125097 | Completed | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Dip elimination file note to be processed | 6.2 |  | 3708 | VISAKH NBOT | Dip elimination file note to be processed | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011315ACN-2026-03-4000125097 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125097 | 2026-09-18 17:30 | 31.0247 | 241 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125097 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011315ACN-2026-03-4000125097 |  | AUD-2026-03-2000011315ACN-2026-03-4000125097 | 21 |  | 26 | 80 | 2 | 1 | 35
AILAVARAPU VENKATA KRISHNA MURTY | 2026-10-10 | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Live Fire training done on 11-09-26.28-09-26, 09-10-26 for all security Guard at HPCL Visakh Refinery. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143393 | Closed | DIWAKAR KAMLESH KUMAR | 2026-10-10 | Live Fire training not conducted to Security Guards | 6.2 |  | 3708 | VISAKH NBOT | Live Fire training to be conducted to Security Guards | SOD | Marketing | SCR | 2026-10-31 | INSUFFICIENT SUPERVISION | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-07-2000015047ACN-2026-07-4000143393 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143393 | 2026-09-18 17:30 | 31.0247 | 404 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143393 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143393 | AUD-2026-07-2000015047ACN-2026-07-4000143393 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | Training Programme organized | ZONAL VISIT REPORT 10.01.2026 VASHI TERM | 2026-01-10 | AUD-2026-03-2000011165 | 2026-01-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123407 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1588 | VASHI WHITE OIL TERMINAL | training programmand refresher course to be organized | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011165ACN-2026-03-4000123407 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011165ACN-2026-03-4000123407 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-03-2000011165 - ACN-2026-03-4000123407 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011165ACN-2026-03-4000123407 | AUD-2026-03-2000011165ACN-2026-03-4000123407 | 21 | 21 | 26 | 80 | 15 | 11 | 35 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | training programmand refresher course organized | VASI LOCATION VISIT 04.05.2026 | 2026-05-04 | AUD-2026-07-2000016456 | 2026-05-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146570 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1588 | VASHI WHITE OIL TERMINAL | training programmand refresher course to be organized | SOD | Marketing | WZ | 2026-05-31 | INSUFFICIENT SUPERVISION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-05-31 | AUD-2026-07-2000016456ACN-2026-07-4000146570 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016456ACN-2026-07-4000146570 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-07-2000016456 - ACN-2026-07-4000146570 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016456ACN-2026-07-4000146570 | AUD-2026-07-2000016456ACN-2026-07-4000146570 | 21 | 21 | 27 | 80 | 15 | 11 | 39 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | Training conducted | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153360 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes conducted | 2.1 | Fire drill conducted in last 6 months (surprise) | 1588 | VASHI WHITE OIL TERMINAL | Wind direction to be seen before operating Fire extinguisher,Refresher training to be conducted | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | OCCUPATIONAL HEALTH | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017371ACN-2026-09-4000153360 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153360 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153360 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153360 | AUD-2026-09-2000017371ACN-2026-09-4000153360 | 21 | 21 | 27 | 80 | 15 | 11 | 57 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | Training given | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153361 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes conducted | 2.2 | Double contingency scenario simulated; observations recorded | 1588 | VASHI WHITE OIL TERMINAL | Injured Person handling needs training | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | OCCUPATIONAL HEALTH | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017371ACN-2026-09-4000153361 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153361 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153361 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153361 | AUD-2026-09-2000017371ACN-2026-09-4000153361 | 21 | 21 | 27 | 80 | 15 | 11 | 57 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | regularly check done with lux meter | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153362 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1588 | VASHI WHITE OIL TERMINAL | regularly check should be done with lux meter | SOD | Marketing | WZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017371ACN-2026-09-4000153362 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153362 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153362 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153362 | AUD-2026-09-2000017371ACN-2026-09-4000153362 | 21 | 21 | 27 | 80 | 15 | 11 | 57 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | alignment checked and rectified | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153363 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.6 | CCTV functioning checked | 1588 | VASHI WHITE OIL TERMINAL | CAMERA ALIGNMENT TO BE DONE | SOD | Marketing | WZ | 2026-10-31 | INSUFFICIENT SUPERVISION | 4 | OCCUPATIONAL HEALTH | S1 | F4 | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153363 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153363 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153363 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153363 | AUD-2026-09-2000017371ACN-2026-09-4000153363 | 21 | 21 | 27 | 80 | 15 | 11 | 61 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | Spare Parts procured for HVLR | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153366 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1588 | VASHI WHITE OIL TERMINAL | Spare parts to be procured for HVLR rectification | SOD | Marketing | WZ | 2026-10-31 | INSUFFICIENT SUPERVISION | 10 | OCCUPATIONAL HEALTH | S2 | F5 | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153366 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153366 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153366 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017371ACN-2026-09-4000153366 | AUD-2026-09-2000017371ACN-2026-09-4000153366 | 21 | 21 | 27 | 80 | 15 | 11 | 61 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | training programmand refresher course organized | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153367 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1588 | VASHI WHITE OIL TERMINAL | training programmand refresher course to be organized | SOD | Marketing | WZ | 2026-10-31 | INSUFFICIENT SUPERVISION | 4 | OCCUPATIONAL HEALTH | S1 | F4 | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153367 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153367 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153367 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153367 | AUD-2026-09-2000017371ACN-2026-09-4000153367 | 21 | 21 | 27 | 80 | 15 | 11 | 61 | 58
NARAYANE KISHORKUMAR SUDAM | 2026-10-12 | GAKHAR NAVEEN | 2026-10-12 | regular training conducted of TT crew | VASHO WOT VISIT DATED 21.09.2026 | 2026-09-21 | AUD-2026-09-2000017371 | 2026-09-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000153368 | Closed | GAKHAR NAVEEN | 2026-10-12 | yes conducted | 2.15 | TT crew roadside emergency procedures checked | 1588 | VASHI WHITE OIL TERMINAL | regular training to be conducted of TT crew | SOD | Marketing | WZ | 2026-10-31 | INSUFFICIENT SUPERVISION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017371ACN-2026-09-4000153368 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017371ACN-2026-09-4000153368 | 2026-10-14 | 5.7538 | 406 | >20 | AUD-2026-09-2000017371 - ACN-2026-09-4000153368 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017371ACN-2026-09-4000153368 | AUD-2026-09-2000017371ACN-2026-09-4000153368 | 21 | 21 | 27 | 80 | 15 | 11 | 61 | 58
MANOJ KUMAR | 2026-10-12 | FOUZDAR RISHABH | 2026-10-12 | List of material has been sent to IT for disposal | SR MGMT INSPECTION 1155 ROORKEE DEPOT | 2026-03-19 14:00 | AUD-2026-03-2000011028 | 2026-03-17 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127358 | Closed | FOUZDAR RISHABH | 2026-10-12 | RFD for e-Scrap available in warehouse to be initiated. All balance scrap to be disposed by 30.3.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1155 | ROORKEE DEPOT | All balance scrap to be disposed by 30.3.2026 | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-12-31 | AUD-2026-03-2000011028ACN-2026-03-4000127358 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011028ACN-2026-03-4000127358 | 2026-09-03 | 46.7538 | 406 | >20 | AUD-2026-03-2000011028 - ACN-2026-03-4000127358 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011028ACN-2026-03-4000127358 | AUD-2026-03-2000011028ACN-2026-03-4000127358 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 58
SHINDE ANAND LAXMAN | 2026-10-12 | SUNITA | 2026-09-29 | MR-II Terminal is located within Mumbai refinery and OISD 118 is applicable for design layout. OISD 244 also confirms on the same. OISD 118 does not provide for internal physical segregation. Communication with MR on this matter atatched with. MR-II Terminal is not a seperate factory but a unit located within Factory premises of Mumbai Refinery. MR-II Terminal does not have its seperate factory license as Tanks, pumps etc are located in same tank farms and pump houses for both MR-II Terminal and Refinery. Thus nophysical segregation can be done MR-II marketing on its own. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126315 | Closed | SHINDE ANAND LAXMAN | 2026-10-12 | NPCB for Physical segregation of Haz and Non haz area | 1.5 | HQO / Zonal support required identified | 1554 | MR-II TERMINAL | To be re-applied for budget in April 2026 | SOD | Marketing | WZ | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-04-2000011147ACN-2026-04-4000126315 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126315 | 2026-10-16 | 3.7538 | 406 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126315 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126315 | AUD-2026-04-2000011147ACN-2026-04-4000126315 | 21 | 21 | 26 | 80 | 6 | 5 | 44 | 58
|  | SAXENA UMESH CHANDRA | 2026-10-12 | RSFPS of TK-24 has been rectified and checked for functionality. MEFG of TK-16 is also functioning after suction tube was opened, cleaned and fixed again. Hence the observation may be closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152277 | Completed | SAXENA UMESH CHANDRA | 2026-10-12 | Functionality of HVLR/RSFPS/HCD/ESD Checked. HVLR-4 and HCD worked fine at TWD P/H - Open Path and Point Type and Open Path Type atTK-23 and ESD-20 near Laboratory checked and found okay. Issue observed in RSFPS of TK-24. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1457 | INDORE DEPOT | 1) RSFPS of TK-24 to be rectified on priority as foam generation was very poor. 2) Foam generation from one of the MEFG was not satisfactory. To check and get it rectified. | SOD | Marketing | CEN | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152277 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152277 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152277 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017752ACN-2026-09-4000152277 |  | AUD-2026-09-2000017752ACN-2026-09-4000152277 | 21 |  | 27 | 80 | 0 | -3 | 57
|  | SAXENA UMESH CHANDRA | 2026-10-12 | Refresher cum induction training is being imparted to TT crew every month. Total 4 training sessions have been conducted in Sept-2026 covering 493 TT crew. Further, fire extinguishers have been checked by NEL for all their TTs between 21.09.2026 and 30.09.2026. (report enclosed). HPCL had also conducted camp for checking of fire extinguishers from 27.07.2026 to 29.07.2026. Hence the observation may kindlyu be considered as complied with. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.14 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152278 | Completed | SAXENA UMESH CHANDRA | 2026-10-12 | Yes, There was a water coming out from one of the Fire extinguisher whereas , 2nd fire extinuisher could not be operated due to malfunctioning of the same (TT No: MP09 HH 7821). | 2.14 | TT crew fire extinguisher usage checked | 1457 | INDORE DEPOT | Refresher training to be imparted to all the TT crew. Also, the periodical checking/testing of hose of Fire Extinuisher is to be done. | SOD | Marketing | CEN | 2026-10-31 |  | 5 |  | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017752ACN-2026-09-4000152278 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152278 | 2026-09-09 19:00 | 39.9622 | 425 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152278 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152278 |  | AUD-2026-09-2000017752ACN-2026-09-4000152278 | 21 |  | 27 | 80 | 0 | -3 | 61
|  | SAXENA UMESH CHANDRA | 2026-10-12 | Housekeeping is a regular activity and is being maintained. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152282 | Completed | SAXENA UMESH CHANDRA | 2026-10-12 | Housekeeping need improvement. PPE usage is done. | 3.15 | Housekeeping & PPE usage checked | 1457 | INDORE DEPOT | House keeping need improvement. | SOD | Marketing | CEN | 2026-09-30 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152282 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152282 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152282 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017752ACN-2026-09-4000152282 |  | AUD-2026-09-2000017752ACN-2026-09-4000152282 | 21 |  | 27 | 80 | 0 | -3 | 57
|  | SAXENA UMESH CHANDRA | 2026-10-12 | Fire engine sequence checked and verified. Working as per sequence. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152273 | Completed | SAXENA UMESH CHANDRA | 2026-10-12 | Location is having single fire contigency. However, Gatry permissive checked by operating 2 fire engines. | 2.2 | Double contingency scenario simulated; observations recorded | 1457 | INDORE DEPOT | Fire Engine sequence to be properly displayed and maintained. The fire engine failed to operate as per sequence. To check and get it corrected with the help of TAS vendor. | SOD | Marketing | CEN | 2026-09-30 |  | 8 |  | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017752ACN-2026-09-4000152273 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152273 | 2026-09-09 19:00 | 39.9622 | 394 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152273 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017752ACN-2026-09-4000152273 |  | AUD-2026-09-2000017752ACN-2026-09-4000152273 | 21 |  | 27 | 80 | 0 | -3 | 57
SHINDE ANAND LAXMAN | 2026-10-12 | SUNITA | 2026-09-29 | MOC as attached was initiated and routed to Refinery Fire and Safety. MR F&S has communicated that as MR-II is part of Refinery premises and OISD 116 is applicable for Fire Fighting facility. In OISD 116 there is no such requirement of HVLR panel being 60M away from target tank. OISD 244 also says that for location within Refinery boundary, OISD 116 shall be applicable for Fire Fighting facility. Confirmation from MR Fire and Safety attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154987 | Closed | SHINDE ANAND LAXMAN | 2026-10-12 | Working as per last service reports of June 2026. HVLR control panels are very close to target tanks | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1554 | MR-II TERMINAL | Location to review and look for shifting of electrical panels. MOC approval to be taken for the same | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154987 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154987 | 2026-10-16 | 3.7538 | 406 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154987 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154987 | AUD-2026-09-2000017375ACN-2026-09-4000154987 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 58
SHINDE ANAND LAXMAN | 2026-10-12 | SUNITA | 2026-09-24 | MOC no. 3100002362 (attached) was sent to MR to shift HVLR, HVLR Panels. Detailed communications were sent to Incharge Fire and Safety Mumbai Refinery multiple times. MR vide their communication dt 23.09.2026 (attached) informed that as MR-II Terminal is located within refinery premises, OISD 244 syas that OISD 116 shall be applicabe for Fire fighting facility located within boundary of Refinery. Same is applicable at M-II Terminal and Mahul terminal. As per OISD 116, there is no requirement of panel distance of 60M from target tank and HVLR itself can be operated manually. Accordingly the point is closed. Relevant records atatched | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146654 | Closed | SHINDE ANAND LAXMAN | 2026-10-12 | Working as per last service reports of June 2026. HVLR control panels are very close to target tanks | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1554 | MR-II TERMINAL | Location to review and look for shifting of electrical panels | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146654 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146654 | 2026-10-16 | 3.7538 | 406 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146654 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146654 | AUD-2026-07-2000016409ACN-2026-07-4000146654 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 58
SHINDE ANAND LAXMAN | 2026-10-12 | SUNITA | 2026-10-12 | First aid training conducted for all Officers, workmen and TT crew on 11-13 August 2026 through DISH approved trainer Dr Ranjit Kale. Certificates attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154988 | Closed | SUNITA | 2026-10-12 | YES | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1554 | MR-II TERMINAL | Yearly first aid training is due for location workmen as per factories Act. | SOD | Marketing | WZ | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154988 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154988 | 2026-10-16 | 3.7538 | 406 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154988 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154988 | AUD-2026-09-2000017375ACN-2026-09-4000154988 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 58
SHINDE ANAND LAXMAN | 2026-10-12 | SUNITA | 2026-10-12 | Gate meeting with TT crew are conducted regularly. Record attached | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000145549 | Closed | SUNITA | 2026-10-12 | Reviwed. Some deviations noted ex. daily gate meeting not conducted | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1554 | MR-II TERMINAL | 100% Compliance needed | SOD | Marketing | WZ | 2026-08-30 | POOR COMMUNICATION | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-08-30 | AUD-2026-07-2000016409ACN-2026-07-4000145549 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000145549 | 2026-10-16 | 3.7538 | 406 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000145549 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000145549 | AUD-2026-07-2000016409ACN-2026-07-4000145549 | 21 | 21 | 27 | 80 | 6 | 5 | 52 | 58
|  | SUNITA | 2026-10-12 | 4 New officers assigned for Mahul/MR-II in Sept 2026. 2-3 Officers will be utilized at Mahul Terminal Works out of these 4 New Joinees | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152900 | Completed | SUNITA | 2026-10-12 | Management staff for mahul Terminal Operations. | 1.5 | HQO / Zonal support required identified | 1585 | MAHUL TERMINAL | XX | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017701ACN-2026-09-4000152900 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152900 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152900 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152900 |  | AUD-2026-09-2000017701ACN-2026-09-4000152900 | 21 |  | 27 | 80 | 28 | 28 | 57
|  | SUNITA | 2026-10-12 | 4 New officers assigned for Mahul/MR-II in Sept 2026. 2-3 Officers will be utilized at Mahul Terminal Works out of these 4 New Joinees | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000152224 | Completed | SUNITA | 2026-10-12 | No nominated officers available in Mahul Terminal as per HR payroll. Only one officer sri Satish chandra was available and discussed about the Loaction constraints & ongoing Projects/operational activities. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1585 | MAHUL TERMINAL | To provide full fledged Officers at Mahul Terminal with coordination of HR & SOD SBU. | SOD | Marketing | WZ | 2027-03-31 |  | 15 |  | S3 | F5 | 2027-03-31 | AUD-2026-07-2000016410ACN-2026-09-4000152224 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152224 | 2026-10-17 | 2.7538 | 576 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152224 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-07-2000016410ACN-2026-09-4000152224 |  | AUD-2026-07-2000016410ACN-2026-09-4000152224 | 21 |  | 27 | 80 | 28 | 28 | 83
|  | SUNITA | 2026-10-12 | Foam Trolley topped up and mock drill done using HVLR foam application. Report and photos attached. | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152903 | Completed | SUNITA | 2026-10-12 | Foam trolley of HVLR1 to be topped up | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1585 | MAHUL TERMINAL | To top up the same immediately. | SOD | Marketing | WZ | 2026-09-20 |  | 4 |  | S2 | F2 | 2026-09-20 | AUD-2026-09-2000017701ACN-2026-09-4000152903 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152903 | 2026-10-17 | 2.7538 | 384 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152903 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152903 |  | AUD-2026-09-2000017701ACN-2026-09-4000152903 | 21 |  | 27 | 80 | 28 | 28 | 55
|  | SUNITA | 2026-10-12 | New CCTV Budget has been sought in 2022-23, 2023-24, 2024-25 and 2025-26. Budget was not alllcated. As per Guidance Budget was sought in 2025-26 also. Communication trail with HQO and NPCB proposal is atached. New CCTV will be imstalled when Budget is allocated. | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152901 | Completed | SUNITA | 2026-10-12 | Checked found OK. However advance CCTV with VA Facilities to be installed. | 2.6 | CCTV functioning checked | 1585 | MAHUL TERMINAL | To propose CCTV Projects in NPCB 2026-27.Followup with HQO for funds. | SOD | Marketing | WZ | 2027-12-31 |  | 4 |  | S2 | F2 | 2027-12-31 | AUD-2026-09-2000017701ACN-2026-09-4000152901 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152901 | 2026-10-17 | 2.7538 | 851 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152901 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152901 |  | AUD-2026-09-2000017701ACN-2026-09-4000152901 | 21 |  | 27 | 80 | 28 | 28 | 122
|  | SUNITA | 2026-10-12 | New CCTV Budget has been sought in 2022-23, 2023-24, 2024-25 and 2025-26. Budget was not alllcated. As per Guidance Budget was sought in 2025-26 also. Communication trail with HQO and NPCB proposal is atached. New CCTV will be imstalled when Budget is allocated. | MAHUL LOCATION VISIT DATED15.04.2026 | 2026-04-15 | AUD-2026-07-2000016410 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152226 | Completed | SUNITA | 2026-10-12 | Checked found OK. However advance CCTV with VA Facilities to be installed. | 2.6 | CCTV functioning checked | 1585 | MAHUL TERMINAL | To propose CCTV Projects in NPCB 2026-27 | SOD | Marketing | WZ | 2027-12-31 |  | 4 |  | S2 | F2 | 2027-12-31 | AUD-2026-07-2000016410ACN-2026-09-4000152226 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016410ACN-2026-09-4000152226 | 2026-10-17 | 2.7538 | 851 | >20 | AUD-2026-07-2000016410 - ACN-2026-09-4000152226 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016410ACN-2026-09-4000152226 |  | AUD-2026-07-2000016410ACN-2026-09-4000152226 | 21 |  | 27 | 80 | 28 | 28 | 122
|  | SUNITA | 2026-10-12 | New CCTV Budget has been sought in 2022-23, 2023-24, 2024-25 and 2025-26. Budget was not alllcated. As per Guidance Budget was sought in 2025-26 also. Communication trail with HQO and NPCB proposal is atached. New CCTV will be imstalled when Budget is allocated. | MAHUL LOCATION VISIT DATED24.07.2026 | 2026-07-24 | AUD-2026-09-2000017701 | 2026-07-24 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152902 | Completed | SUNITA | 2026-10-12 | CCTV with VA not availble at location. | 2.7 | VA alerts checked / analysed | 1585 | MAHUL TERMINAL | To propose CCTV Projects in NPCB 2026-27 | SOD | Marketing | WZ | 2027-12-31 |  | 4 |  | S2 | F2 | 2027-12-31 | AUD-2026-09-2000017701ACN-2026-09-4000152902 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017701ACN-2026-09-4000152902 | 2026-10-17 | 2.7538 | 851 | >20 | AUD-2026-09-2000017701 - ACN-2026-09-4000152902 | 532 | 8294 | 21 | 8294 | -437 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017701ACN-2026-09-4000152902 |  | AUD-2026-09-2000017701ACN-2026-09-4000152902 | 21 |  | 27 | 80 | 28 | 28 | 122
ALBY ABRAHAM ARACKAL | 2026-10-13 | SRIJIN S | 2026-10-13 | Mock drills are conducted on monthly basis and as per ERDMP scenarios. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000152414 | Closed | SRIJIN S | 2026-10-13 | All mock fire drills are single contingency. Observation recorded and corrective actions taken. Safety committee conducted on 11-06-2026. 8 Recommendation were recorded. | 2.2 | Double contingency scenario simulated; observations recorded | 1833 | COCHIN BLACK TERMINAL | Location to list out all ERDMP scenarios and Drills are to be conducted for all the given scenarios. | SOD | Marketing | CZR | 2026-10-31 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017851ACN-2026-09-4000152414 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152414 | 2026-09-08 16:00 | 41.0872 | 407 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152414 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152414 | AUD-2026-09-2000017851ACN-2026-09-4000152414 | 21 | 21 | 27 | 80 | 2 | 0 | 61 | 59
ALBY ABRAHAM ARACKAL | 2026-10-13 | SRIJIN S | 2026-10-13 | Repetetive point. mentioned in 3.7 | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152420 | Closed | SRIJIN S | 2026-10-13 |  | 3.10 | TFMS/SAP reconciliation checked | 1833 | COCHIN BLACK TERMINAL | Location to compile the data for all tanks, inline with HQO circular and integrate TFMS data with SAP | SOD | Marketing | CZR | 2026-12-31 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017851ACN-2026-09-4000152420 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152420 | 2026-09-08 16:00 | 41.0872 | 407 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152420 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152420 | AUD-2026-09-2000017851ACN-2026-09-4000152420 | 21 | 21 | 27 | 80 | 2 | 0 | 70 | 59
ALBY ABRAHAM ARACKAL | 2026-10-13 | SRIJIN S | 2026-10-13 | The same was informed to the lube sales officer. All the gift items segragated and are now being placed in a seperate room. The room is locked and key is avaible with lubes department. | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152421 | Closed | SRIJIN S | 2026-10-13 | House keeping is well maintained at terminal. PPE matrix is displayed | 3.15 | Housekeeping & PPE usage checked | 1833 | COCHIN BLACK TERMINAL | Location to coordinate with Lubes RO and complete reco for all the consumables / spares kept in canteen building | SOD | Marketing | CZR | 2026-10-31 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017851ACN-2026-09-4000152421 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152421 | 2026-09-08 16:00 | 41.0872 | 407 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152421 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152421 | AUD-2026-09-2000017851ACN-2026-09-4000152421 | 21 | 21 | 27 | 80 | 2 | 0 | 61 | 59
ALBY ABRAHAM ARACKAL | 2026-10-13 | SRIJIN S | 2026-10-13 | tank wise reco for all products maintained | GM O&D AUDIT Q2 26-27 | 2026-09-08 16:00 | AUD-2026-09-2000017851 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152419 | Closed | SRIJIN S | 2026-10-13 | Manual Reconciliation | 3.8 | Auto vs Manual reconciliation checked | 1833 | COCHIN BLACK TERMINAL | Advised location to maintain tank wise reco for all products | SOD | Marketing | CZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 4 | OCCUPATIONAL HEALTH | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017851ACN-2026-09-4000152419 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017851ACN-2026-09-4000152419 | 2026-09-08 16:00 | 41.0872 | 407 | >20 | AUD-2026-09-2000017851 - ACN-2026-09-4000152419 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017851ACN-2026-09-4000152419 | AUD-2026-09-2000017851ACN-2026-09-4000152419 | 21 | 21 | 27 | 80 | 2 | 0 | 57 | 59
|  | ANSHU KUMAR SINGH | 2026-10-13 | STP has been switched to Auto Mode and is functioning properly. | MIRAJ VISIT DATED01.09.2026 | 2026-09-01 | AUD-2026-09-2000017453 | 2026-09-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153084 | Completed | ANSHU KUMAR SINGH | 2026-10-13 | STP 1 functioning was found in manual mode rather in auto mode | 6.1 | Condition of auto switcher & functioning of STP in auto mode | 1504 | MIRAJ TERMINAL | Location should keep STP always in Auto mode and monitor its auto switching functionality | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-09-2000017453ACN-2026-09-4000153084 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017453ACN-2026-09-4000153084 | 2026-09-01 | 48.7538 | 394 | >20 | AUD-2026-09-2000017453 - ACN-2026-09-4000153084 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017453ACN-2026-09-4000153084 |  | AUD-2026-09-2000017453ACN-2026-09-4000153084 | 21 |  | 27 | 80 | 0 | -1 | 57
SABLE RONAK MOHANKUMAR | 2026-10-13 | SINGH PREETI | 2026-10-13 | Sensors installed in all Highmasts at Palanpur Terminal for auto-switching. | SR. MANAGEMENT INSPECTION Q1 26-27 PALAN | 2026-06-02 | AUD-2026-06-2000013929 | 2026-06-01 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000140815 | Closed | SINGH PREETI | 2026-10-13 | Sensors for auto-switching of High Masts to be explored and installed. | 6.18 | Additional Observations | 1385 | PALANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-07-01 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-07-01 | AUD-2026-06-2000013929ACN-2026-06-4000140815 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013929ACN-2026-06-4000140815 | 2026-08-22 22:00 | 57.8372 | 407 | >20 | AUD-2026-06-2000013929 - ACN-2026-06-4000140815 | 532 | 8294 | 21 | 8294 | 110 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013929ACN-2026-06-4000140815 | AUD-2026-06-2000013929ACN-2026-06-4000140815 | 21 | 21 | 27 | 80 | 1 | 1 | 44 | 59
SABLE RONAK MOHANKUMAR | 2026-10-13 | SINGH PREETI | 2026-10-13 | All guidelines mentioned in Empty TT Circular being followed at location, TTs being checked physically for emptiness and OGP being signed by two officers, before releasing the TT out of premises. All location officers have again being sensitized to follow the SOPfor releasing Empty TT. Supporting Documents attached. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000150753 | Closed | SINGH PREETI | 2026-10-13 | Location shall follow the empty TT release circular. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150753 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150753 | 2026-08-22 22:00 | 57.8372 | 407 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150753 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150753 | AUD-2026-08-2000016905ACN-2026-09-4000150753 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 59
SABLE RONAK MOHANKUMAR | 2026-10-13 | SINGH PREETI | 2026-10-13 | Action taken for VTS Deviations, Records also being maintained for action taken. Supporting documents attached. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000150757 | Closed | SINGH PREETI | 2026-10-13 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150757 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150757 | 2026-08-22 22:00 | 57.8372 | 407 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150757 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150757 | AUD-2026-08-2000016905ACN-2026-09-4000150757 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 59
SABLE RONAK MOHANKUMAR | 2026-10-13 | SINGH PREETI | 2026-10-13 | TT Pre-calibration checks being done, checklist records maintained. Photos being taken, and print records being maintained. Supporting documents attached. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150769 | Closed | SINGH PREETI | 2026-10-13 | TT GJ02AT4271 — date of calibration 28/7/26 — pre-calibration inspection record not available. TT Calibration pre-checklist to be maintained, Photos print to be taken and kept | 6.1 | Additional Observations | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150769 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150769 | 2026-08-22 22:00 | 57.8372 | 407 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150769 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150769 | AUD-2026-08-2000016905ACN-2026-09-4000150769 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Faulty lights have been repaired & replaced in the Tank Farm and backside of the TLF Gantry. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154497 | Closed | SUMIT KUMAR | 2026-10-13 | Record checked and as confirmed by location lux need improvement in Tank Farm area, Backside of TLF gantry. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1128 | MATHURA TERMINAL | Lux to be improved in mentioned area as per requirement | SOD | Marketing | NUZ | 2026-12-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000154497 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154497 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154497 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017615ACN-2026-09-4000154497 | AUD-2026-09-2000017615ACN-2026-09-4000154497 | 21 | 21 | 27 | 80 | 14 | 13 | 70 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Training has been imparted to security personnel on gate management and traffic management to improve vehicle movement control and prevent congestion at the main gate. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154498 | Closed | SUMIT KUMAR | 2026-10-13 | Gate security and supervisor are found to be active and responding well on sought details | 2.4 | Security alertness checked (night-halt / surprise checks) | 1128 | MATHURA TERMINAL | Security to be trained further on gate management. Vehicle movement & parking infront of main gate to be controlled to avoid congestion at gate entry. | SOD | Marketing | NUZ | 2026-10-31 | INSUFFICIENT SUPERVISION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-10-31 | AUD-2026-09-2000017615ACN-2026-09-4000154498 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000154498 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000154498 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017615ACN-2026-09-4000154498 | AUD-2026-09-2000017615ACN-2026-09-4000154498 | 21 | 21 | 27 | 80 | 14 | 13 | 61 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Manager TAS has cordinated with all location of NUZ, and training imparted. | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000147341 | Closed | SUMIT KUMAR | 2026-10-13 | Yes | 2.7 | VA alerts checked / analysed | 1128 | MATHURA TERMINAL | Manager TAS- Shri Sunny Gupta to coordinate with NUZ locations for improvement | SOD | Marketing | NUZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S1 | F4 | 2026-09-30 | AUD-2026-08-2000016610ACN-2026-08-4000147341 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147341 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147341 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016610ACN-2026-08-4000147341 | AUD-2026-08-2000016610ACN-2026-08-4000147341 | 21 | 21 | 27 | 80 | 14 | 13 | 57 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Housekeeping in Tank Farm Area and repairing of TT Rest room has been completed. | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147342 | Closed | SUMIT KUMAR | 2026-10-13 | Yes | 3.15 | Housekeeping & PPE usage checked | 1128 | MATHURA TERMINAL | Housekeeping needs improvement in Tank Farm, TWD Pump House. Also TT Crew Rest Room shed to be repaired and upkeeping to be done. | SOD | Marketing | NUZ | 2026-08-31 | INSUFFICIENT SUPERVISION | 4 | ENVIRONMENTAL | S1 | F4 | 2026-08-31 | AUD-2026-08-2000016610ACN-2026-08-4000147342 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147342 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147342 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016610ACN-2026-08-4000147342 | AUD-2026-08-2000016610ACN-2026-08-4000147342 | 21 | 21 | 27 | 80 | 14 | 13 | 52 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Repair of the TT Crew Rest Room shed and housekeeping in the Tank Farm and TWD Pump House have been completed. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155352 | Closed | SUMIT KUMAR | 2026-10-13 | Yes | 3.15 | Housekeeping & PPE usage checked | 1128 | MATHURA TERMINAL | Housekeeping needs improvement in Tank Farm, TWD Pump House. Also TT Crew Rest Room shed to be repaired and upkeeping to be done. | SOD | Marketing | NUZ | 2026-12-31 | INSUFFICIENT SUPERVISION | 15 | ENVIRONMENTAL | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000155352 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155352 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155352 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017615ACN-2026-09-4000155352 | AUD-2026-09-2000017615ACN-2026-09-4000155352 | 21 | 21 | 27 | 80 | 14 | 13 | 70 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | MOC has been closed. | SR MANAGEMENT AUDIT MATHURA | 2026-06-26 15:00 | AUD-2026-08-2000016610 | 2026-06-25 11:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147343 | Closed | SUMIT KUMAR | 2026-10-13 | Yes | 3.17 | MOC status reviewed | 1128 | MATHURA TERMINAL | Open MOCs to be closed. | SOD | Marketing | NUZ | 2026-08-31 | POOR COMMUNICATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-08-31 | AUD-2026-08-2000016610ACN-2026-08-4000147343 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016610ACN-2026-08-4000147343 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-08-2000016610 - ACN-2026-08-4000147343 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016610ACN-2026-08-4000147343 | AUD-2026-08-2000016610ACN-2026-08-4000147343 | 21 | 21 | 27 | 80 | 14 | 13 | 52 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Point repeated in Q2 audit. Kept open in Q2 audit and being closed herein | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138606 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | One ATF tank taken for cleaning and conversion of HSD to ATF tank nearing completion | 1.8 | Improvement plans discussed | 1895 | MANGALORE TERMINAL | To be completed at the earliest | SOD | Marketing | SWZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138606 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138606 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138606 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138606 | AUD-2026-06-2000013350ACN-2026-06-4000138606 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Point repeated in Q2 audit. Kept open in Q2 audit and being closed herein | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138608 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | CCTV functioning checked. Out of 78 cameras, 6 nos cameras are found down. | 2.6 | CCTV functioning checked | 1895 | MANGALORE TERMINAL | Location has taken up with CCTV vendor. Same to be expediated. | SOD | Marketing | SWZ | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 2 | ASSET INTEGRITY | S1 | F2 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138608 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138608 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138608 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138608 | AUD-2026-06-2000013350ACN-2026-06-4000138608 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | Point repeated in Q2 audit. Kept open in Q2 audit and being closed herein | MANGALORE_TML_Q1_SR.MGNT_INSPECTION | 2026-05-19 18:00 | AUD-2026-06-2000013350 | 2026-05-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000138612 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-09-11 | SIR/PTR No 1895/26-27/1 initated for Bitumen facility. Re-tendering to be done for 1895/25-26/4 for Cables, as H1 party has backed out. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1895 | MANGALORE TERMINAL | To be expedited. RFDs for Loading Arms, other Misc Steel scrap to be processed immediately and physical disposal to be completed by30.09.2026 | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-06-30 | AUD-2026-06-2000013350ACN-2026-06-4000138612 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013350ACN-2026-06-4000138612 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-06-2000013350 - ACN-2026-06-4000138612 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013350ACN-2026-06-4000138612 | AUD-2026-06-2000013350ACN-2026-06-4000138612 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Investigation has been completed based on TT Guardian site information, and the letter has been sent to the District Administration. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | TT GUARDIAN INFORMATION WILL BE REVIEWED | ACN-2026-09-4000155350 | Closed | SUMIT KUMAR | 2026-10-13 | Yes, discussed with LIC on various issues faced by Location on VTS wrt non commencement of trip immediately after TAS R3. | 3.3 | VTS deviations reviewed | 1128 | MATHURA TERMINAL | TT guardina site to be utilised and basis the investigation report letter to be sent to District administration. | SOD | Marketing | NUZ | 2026-12-31 | INSUFFICIENT SUPERVISION | 15 | ASSET INTEGRITY | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000155350 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155350 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155350 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017615ACN-2026-09-4000155350 | AUD-2026-09-2000017615ACN-2026-09-4000155350 | 21 | 21 | 27 | 80 | 14 | 13 | 70 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | All items of the kit are placed at the designated place. 21 nos of items being checked on monthly basis. records maintained. Shedanchored properly. Emergency trolley used in mock frill conducted in Aug 2026. | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147886 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | All items of emergency trolley are not available viz. fire extinguisher, first aid box at the respective designated place & trolleyshed was observed not anchored | 6.2 | Emergency trolley kit | 1895 | MANGALORE TERMINAL | All items of the kit to be placed at the designated place, with clear date of expiry for applicable items along with monthly upkeeping record. Emergency trolley to be used in each fire drill. Shed to be anchored properly. | SOD | Marketing | SWZ | 2026-08-15 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-15 | AUD-2026-08-2000016271ACN-2026-08-4000147886 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147886 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147886 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147886 | AUD-2026-08-2000016271ACN-2026-08-4000147886 | 21 | 21 | 27 | 80 | 2 | 2 | 50 | 59
KAUSHIK ANIL | 2026-10-13 | ANAND PRASAD JAISWARA | 2026-09-11 | Complied-Timely Cleaning done | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147894 | Closed | ANAND PRASAD JAISWARA | 2026-09-11 | Oil found on MFM cables for LP-11 MS. | 6.10 | Housekeeping | 1895 | MANGALORE TERMINAL | Same to be cleaned periodically. | SOD | Marketing | SWZ | 2026-08-10 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-10 | AUD-2026-08-2000016271ACN-2026-08-4000147894 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147894 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147894 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147894 | AUD-2026-08-2000016271ACN-2026-08-4000147894 | 21 | 21 | 27 | 80 | 2 | 2 | 49 | 59
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | Regular stock-loss monitoring, particularly for Black Oil products, is being carried out. TT dip checking at the main gate is also being conducted by officers. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155351 | Closed | SUMIT KUMAR | 2026-10-13 | Yes, all variations are approved by LIC with suitable remarks. | 3.9 | Abnormal variations / unused assets reviewed | 1128 | MATHURA TERMINAL | Regular monitoring of stock loss to be done at location especially black oils. TT dip checking at main gate to be done by all officers.checking at Gantry also to be intensified if variation is found advised to go for fresh dip elimination data and approval | SOD | Marketing | NUZ | 2026-12-31 | POOR COMMUNICATION | 15 | ASSET INTEGRITY | S3 | F5 | 2026-12-31 | AUD-2026-09-2000017615ACN-2026-09-4000155351 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155351 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155351 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017615ACN-2026-09-4000155351 | AUD-2026-09-2000017615ACN-2026-09-4000155351 | 21 | 21 | 27 | 80 | 14 | 13 | 70 | 59
|  | SUMIT KUMAR | 2026-10-13 | The location has recently inducted 10 TTs, comprising 7 White Oil and 3 Black Oil TTs. Sticker pasting have been completed for 8 TTs (6 White Oil and 2 Black Oil). The concerned transporters have been communicated regarding completion of the pending sticker pasting, and follow-up is in progress for the remaining 2 TTs. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155361 | Open | SUMIT KUMAR | 2026-10-13 | Mail/ letter to transporters for sticker payment by 31st Oct or to stop the TT’s from plying | 6.5 | NIL | 1128 | MATHURA TERMINAL | Mail/ letter to transporters for sticker payment by 31st Oct or to stop the TT’s from plying | SOD | Marketing | NUZ | 2027-03-31 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155361 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155361 | 2026-09-18 | 31.7538 | 576 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155361 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017615ACN-2026-09-4000155361 |  | AUD-2026-09-2000017615ACN-2026-09-4000155361 | 21 |  | 27 | 80 | 14 | 13 | 83
ARYA VIPIN KUMAR | 2026-10-13 | SUMIT KUMAR | 2026-10-13 | An email dated 13.10.2026 has been sent to HQO CPO requesting issuance of the LOA to the eligible transporters under the reserve category against the draw of lots. | SENIOR MANAGEMENT AUDIT Q2 | 2026-09-18 | AUD-2026-09-2000017615 | 2026-09-18 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155364 | Closed | SUMIT KUMAR | 2026-10-13 | Mail to HQO CPO for issuance of LOA to transporters under reserve category against draw of lots | 6.8 | NIL | 1128 | MATHURA TERMINAL | Mail to HQO CPO for issuance of LOA to transporters under reserve category against draw of lots | SOD | Marketing | NUZ | 2027-03-31 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S1 | F4 | 2027-03-31 | AUD-2026-09-2000017615ACN-2026-09-4000155364 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017615ACN-2026-09-4000155364 | 2026-09-18 | 31.7538 | 407 | >20 | AUD-2026-09-2000017615 - ACN-2026-09-4000155364 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017615ACN-2026-09-4000155364 | AUD-2026-09-2000017615ACN-2026-09-4000155364 | 21 | 21 | 27 | 80 | 14 | 13 | 83 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | TAS control room has been kept in an orderly manner | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147896 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | Housekeeping in TAS control room not upto the mark | 6.12 | Housekeeping | 1895 | MANGALORE TERMINAL | Housekeeping to be improved in TAS control room. | SOD | Marketing | SWZ | 2026-08-15 | INADEQUATE SAFETY CULTURE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-15 | AUD-2026-08-2000016271ACN-2026-08-4000147896 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147896 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147896 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147896 | AUD-2026-08-2000016271ACN-2026-08-4000147896 | 21 | 21 | 27 | 80 | 2 | 2 | 50 | 59
KAUSHIK ANIL | 2026-10-13 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | touch up done wherever required | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147895 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-10-13 | Cleaning/ touch up painting requirement observed in TTG | 6.11 | Maintenance activities | 1895 | MANGALORE TERMINAL | Cleaning/ touch up painting may be done on TT Gantry JBs. Other items like nuts, bolts & name plates etc. to be protected by applying grease during painting. | SOD | Marketing | SWZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016271ACN-2026-08-4000147895 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147895 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147895 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147895 | AUD-2026-08-2000016271ACN-2026-08-4000147895 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
KAUSHIK ANIL | 2026-10-13 | ANAND PRASAD JAISWARA | 2026-09-11 | Complied-Water channels created and cleaned | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147897 | Closed | ANAND PRASAD JAISWARA | 2026-09-11 | Found Water stagnation in TT Gantry | 6.13 | TTG Maintenance | 1895 | MANGALORE TERMINAL | Water stagnation in TT Gantry to be timely cleared. | SOD | Marketing | SWZ | 2026-08-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-08-10 | AUD-2026-08-2000016271ACN-2026-08-4000147897 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147897 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147897 | 532 | 8294 | 21 | 8294 | 70 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147897 | AUD-2026-08-2000016271ACN-2026-08-4000147897 | 21 | 21 | 27 | 80 | 2 | 2 | 49 | 59
KAUSHIK ANIL | 2026-10-13 | ANAND PRASAD JAISWARA | 2026-09-11 | Complied-Rusted Bolts Replaced | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147898 | Closed | ANAND PRASAD JAISWARA | 2026-09-11 | Bolts are found to be rusted at various product pipeline joints at TTG. | 6.14 | TTG Maintenance | 1895 | MANGALORE TERMINAL | Rusted Bolts to be cleaned/greased or replaced as required. | SOD | Marketing | SWZ | 2026-08-15 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-15 | AUD-2026-08-2000016271ACN-2026-08-4000147898 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147898 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147898 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147898 | AUD-2026-08-2000016271ACN-2026-08-4000147898 | 21 | 21 | 27 | 80 | 2 | 2 | 50 | 59
KAUSHIK ANIL | 2026-10-13 | ANAND PRASAD JAISWARA | 2026-09-11 | Complied-Gland provided | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147899 | Closed | ANAND PRASAD JAISWARA | 2026-09-11 | FLP gland not available in MFM JB at Bay 4 | 6.15 | TTG Maintenance | 1895 | MANGALORE TERMINAL | FLP gland to be provided in MFM JB at Bay 4 | SOD | Marketing | SWZ | 2026-08-15 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-15 | AUD-2026-08-2000016271ACN-2026-08-4000147899 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000147899 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000147899 | 532 | 8294 | 21 | 8294 | 65 | 70 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000147899 | AUD-2026-08-2000016271ACN-2026-08-4000147899 | 21 | 21 | 27 | 80 | 2 | 2 | 50 | 59
KAUSHIK ANIL | 2026-10-13 | ANAND PRASAD JAISWARA | 2026-09-11 | Complied-Kerb wall is Fixed | SR.MANAGEMENT INSPECTION Q2 MLR TML | 2026-07-29 17:00 | AUD-2026-08-2000016271 | 2026-07-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000148000 | Closed | ANAND PRASAD JAISWARA | 2026-09-11 | Kerb stones in Bay 3-4 are broken | 6.16 | TTG Maintenance | 1895 | MANGALORE TERMINAL | Broken kerb in Bay 3-4 to be repaired. | SOD | Marketing | SWZ | 2026-08-30 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-08-2000016271ACN-2026-08-4000148000 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016271ACN-2026-08-4000148000 | 2026-07-29 17:00 | 82.0455 | 407 | >20 | AUD-2026-08-2000016271 - ACN-2026-08-4000148000 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016271ACN-2026-08-4000148000 | AUD-2026-08-2000016271ACN-2026-08-4000148000 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | cbacs has been repaired | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146312 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | C bacs installed near planning room is non operational. | 2.8 | Access control systems checked | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146312 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146312 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146312 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146312 | AUD-2026-07-2000016503ACN-2026-07-4000146312 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | SOP boards sent for printing in Gujrati Language on Gantry | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146325 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | TT crew of GJ04W949 and GJ20J8833 was not able to read SOP boards available in Hindi/English at TT gantry as they can read only local language Gujrati. | 6.1 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146325 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146325 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146325 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146325 | AUD-2026-07-2000016503ACN-2026-07-4000146325 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | CCTV time stamp corrected | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146339 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | CCTV time stamp to be corrected. | 6.15 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146339 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146339 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146339 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146339 | AUD-2026-07-2000016503ACN-2026-07-4000146339 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | SOP has been sent for updation/approval to zone | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146330 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | Location to check inclusion of mechanical seal cooling arrangement for MS pump in location SOP. | 6.6 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146330 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146330 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146330 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146330 | AUD-2026-07-2000016503ACN-2026-07-4000146330 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | SLD of foam shed has been updated | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146331 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | SLD of Foam pump shed is not updated. | 6.7 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146331 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146331 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146331 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146331 | AUD-2026-07-2000016503ACN-2026-07-4000146331 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | PCC Under progress for foundation & base for test bench installation | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146332 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | Location to install test bench and put to use. | 6.8 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146332 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146332 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146332 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146332 | AUD-2026-07-2000016503ACN-2026-07-4000146332 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-13 | cable dressing has been done near HSD dyke valve | SR MANAGEMENT INSP OF VADODARA Q1 26-27 | 2026-06-24 18:00 | AUD-2026-07-2000016503 | 2026-06-24 08:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146345 | Closed | PANWAR JITENDRA SINGH | 2026-10-13 | Camera network cable near Dyke Valve-2 (HSD) was laid above ground level. The work has been recently carried out. | 6.21 |  | 1410 | VADODARA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-08-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000016503ACN-2026-07-4000146345 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016503ACN-2026-07-4000146345 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-07-2000016503 - ACN-2026-07-4000146345 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016503ACN-2026-07-4000146345 | AUD-2026-07-2000016503ACN-2026-07-4000146345 | 21 | 21 | 27 | 80 | 0 | -26 | 52 | 59
|  | SHETTY ANURANJAN | 2026-10-14 | FE-5 has been brought back into full functionality | VISIT OF JAIPUR TML ON 20.07.26, 18 & 21 | 2026-08-21 | AUD-2026-09-2000016770 | 2026-08-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151074 | Completed | SHETTY ANURANJAN | 2026-10-14 | FE-5 is not in working condition since March 2026. It is a matter of concern. This is not acceptable. | 1.3 | Pending issues reviewed | 1242 | JAIPUR TERMINAL | Pls bring FE-5 in working order as early as possible. Take quotation for D-check of at least two more engines and submit additionalbudget proposal | SOD | Marketing | NWF | 2026-09-30 |  | 12 |  | S3 | F4 | 2026-09-30 | AUD-2026-09-2000016770ACN-2026-09-4000151074 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000016770ACN-2026-09-4000151074 | 2026-09-30 | 19.7538 | 394 | >20 | AUD-2026-09-2000016770 - ACN-2026-09-4000151074 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000016770ACN-2026-09-4000151074 |  | AUD-2026-09-2000016770ACN-2026-09-4000151074 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | PO placed to LM power for replacement of lights in gantry,tankfarm,pumphouse and siding. The work has been completed. Hence complied | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122650 | Completed | DAS DARSHAN | 2026-10-14 | Lux level not meeting at majority facilities: Primary and secondary road, Tank operating valves, at few bays, tanks farm area etc. Most of the lights of flood light towers are also not working. Budget for replacement of lights is already approved and tender is under TE. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1292 | LUCKNOW DEPOT | Corrective action shall be completed on priority. | SOD | Marketing | NCR | 2026-03-31 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011009ACN-2026-03-4000122650 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122650 | 2026-09-03 | 46.7538 | 211 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122650 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011009ACN-2026-03-4000122650 |  | AUD-2026-03-2000011009ACN-2026-03-4000122650 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | DAS DARSHAN | 2026-10-14 | A pipeline is connected from the outlet of VRU dyke enclosure area and is connected in the slope area of drainage of ethanol gantryarea to ensure effective drainage in that area. Hence complied | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149668 | Completed | DAS DARSHAN | 2026-10-14 | The drain depth in the vicinity of the Ethanol Gantry is inadequate. The drains should be deepened and provided with an appropriateslope to ensure effective drainage of spilled product, if any. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Deepen the drains in the Ethanol Gantry area and provide adequate slope to ensure effective drainage. | SOD | Marketing | NCR | 2026-09-30 |  | 4 |  | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149668 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149668 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149668 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149668 |  | AUD-2026-08-2000017257ACN-2026-08-4000149668 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | Latest approved P&ID is displayed at prominent place in the field. Hence complied | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149669 | Completed | DAS DARSHAN | 2026-10-14 | The old approved P&ID displayed in the field at location. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Latest approved P&ID to be displayed at prominent place in the field. | SOD | Marketing | NCR | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149669 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149669 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149669 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149669 |  | AUD-2026-08-2000017257ACN-2026-08-4000149669 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | Concertina coil in Raiway siding areas near JB No-19 has been replaced with new one. Hence complied | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149664 | Completed | DAS DARSHAN | 2026-10-14 | The boundary wall requires civil repair at some places along with wall painting. The concertina coil installed along the periphery is intact, except in Raiway siding areas near JB No-19. | 3.16 | Earth pits / boundary / vegetation control checked | 1292 | LUCKNOW DEPOT | Concertina coil in Raiway siding areas near JB No-19 needs to be attended immediately. | SOD | Marketing | NCR | 2026-09-30 |  | 9 |  | S3 | F3 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149664 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149664 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149664 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017257ACN-2026-08-4000149664 |  | AUD-2026-08-2000017257ACN-2026-08-4000149664 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | The wicket gate is strictly kept locked after 2200 hrs to ensure the safety and security of the premises. Hence complied | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149661 | Completed | DAS DARSHAN | 2026-10-14 | Night Surprise Visit conducted on 12.08.2026 at 23:30 hrs. Wicked gate was found open although Security guards were found alert. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1292 | LUCKNOW DEPOT | The wicket gate shall be kept locked after 2200 hrs to ensure the safety and security of the premises. Location to ensure compliance. | SOD | Marketing | NCR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149661 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149661 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149661 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149661 |  | AUD-2026-08-2000017257ACN-2026-08-4000149661 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | The Faulty camera has been repaired and put in use. Hence complied | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149662 | Completed | DAS DARSHAN | 2026-10-14 |  | 2.6 | CCTV functioning checked | 1292 | LUCKNOW DEPOT | Faulty camera to be repaired and put in use | SOD | Marketing | NCR | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149662 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149662 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149662 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000017257ACN-2026-08-4000149662 |  | AUD-2026-08-2000017257ACN-2026-08-4000149662 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | DAS DARSHAN | 2026-10-14 | The rake unloading points have been repainted to make it prominently identifiable in the field.Also pipeline banding has been completed in the siding area. Hence complied. | ZONAL INSPECTION Q2-2026-27 LUCKNOW IRD | 2026-08-14 17:30 | AUD-2026-08-2000017257 | 2026-08-12 23:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000149672 | Completed | DAS DARSHAN | 2026-10-14 | The rake unloading points are not prominently identifiable in the field. Adequate markings/signages not provided. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1292 | LUCKNOW DEPOT | Provide and ensure /maintain adequate markings/signages for all rake unloading points to ensure clear identification. | SOD | Marketing | NCR | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-08-2000017257ACN-2026-08-4000149672 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017257ACN-2026-08-4000149672 | 2026-09-03 | 46.7538 | 394 | >20 | AUD-2026-08-2000017257 - ACN-2026-08-4000149672 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000017257ACN-2026-08-4000149672 |  | AUD-2026-08-2000017257ACN-2026-08-4000149672 | 21 |  | 27 | 80 | 0 | 0 | 57
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | UG tank dyke drain valves are kept closed at all times. | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155516 | Closed | JOSVIN SUNNY | 2026-10-14 | Dyke valve-1,2 & 3 operated - alarms activated in TAS system. Smoke detector above PLC Panel 1 operated and alarm generated. HCD atPump House tested sucessfully. | 2.11 | Dyke valve,SD, HCD checked | 1892 | KOZHIKODE DEPOT | Location to ensure UG tank dyke drain pipe valves to remain closed at all times. | SOD | Marketing | CZR | 2026-10-03 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-10-03 | AUD-2026-10-2000017709ACN-2026-10-4000155516 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155516 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155516 | 532 | 8294 | 21 | 8294 | 16 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155516 | AUD-2026-10-2000017709ACN-2026-10-4000155516 | 21 | 21 | 27 | 80 | 2 | -4 | 57 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | 1. Fire Organization chart is revised based on new employees reporting at location 2. MOC is been made for new joinees, on job training is done, nomination for various program should be done by the zonal hse ( moc 3300000764 ) | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155517 | Closed | JOSVIN SUNNY | 2026-10-14 | New Employees posted at location. Location Hands on training on O&M is being provided | 2.12 | Trainings | 1892 | KOZHIKODE DEPOT | 1. Fire Organization chart is to be revised based on new employees reporting at location 2. MOC is to be made for new joinees after requisite training | SOD | Marketing | CZR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155517 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155517 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155517 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155517 | AUD-2026-10-2000017709ACN-2026-10-4000155517 | 21 | 21 | 27 | 80 | 2 | -4 | 61 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | Po made and given to the vendor for the condution | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155518 | Closed | JOSVIN SUNNY | 2026-10-14 | Medical checkup is to be carried out for all TT crew once in 6 months. Last medical check done on 17-03-2026. | 2.16 | Eyesight / color-blindness awareness checked | 1892 | KOZHIKODE DEPOT | Medical checkup to be done for all TT crew once in 6 months - in September 2026 | SOD | Marketing | CZR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155518 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155518 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155518 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155518 | AUD-2026-10-2000017709ACN-2026-10-4000155518 | 21 | 21 | 27 | 80 | 2 | -4 | 61 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | drill is conduted at all the areas as per the erdmp document and regular o&m activities are covered under sop | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155513 | Closed | JOSVIN SUNNY | 2026-10-14 | Location has conducted last mock drill as part of comprehensive audit. SOPs are available in online portal in approved status | 2.2 | Double contingency scenario simulated; observations recorded | 1892 | KOZHIKODE DEPOT | Location to list out all ERDMP scenarios and Drills are to be conducted for all the given scenarios. Location to review and ensureall regular O&M activities are covered in approved SOP | SOD | Marketing | CZR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155513 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155513 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155513 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155513 | AUD-2026-10-2000017709ACN-2026-10-4000155513 | 21 | 21 | 27 | 80 | 2 | -4 | 61 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | log book is maintained | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155515 | Closed | JOSVIN SUNNY | 2026-10-14 | Location informed that AMC for ETP maintenance is placed | 2.5 | Emergency response preparedness reviewed | 1892 | KOZHIKODE DEPOT | Location to maintain ETP operations log book after periodic testing. New employees are to be trained on working methodlogy | SOD | Marketing | CZR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155515 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155515 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155515 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155515 | AUD-2026-10-2000017709ACN-2026-10-4000155515 | 21 | 21 | 27 | 80 | 2 | -4 | 61 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | intimated MRPL for changing top loading to bottom loading , sop board for bottom loading displayed at the ganrty | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155519 | Closed | JOSVIN SUNNY | 2026-10-14 | Some TTs of MRPL are top loading TTs. Location informed that Bay no. 4 is allocated for MRPL top loading TTs | 3.1 | TT fittings & discipline checked | 1892 | KOZHIKODE DEPOT | 1. To take up with MRPL for converting Top loading TTs to Bottom loading. SOP for swithcing over from Bottom to Top loading and Vice Versa is to be clearly made available to all concerned. 2. SOP for Bottom loading operations is to be displayed at Gantry | SOD | Marketing | CZR | 2026-11-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-11-30 | AUD-2026-10-2000017709ACN-2026-10-4000155519 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155519 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155519 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155519 | AUD-2026-10-2000017709ACN-2026-10-4000155519 | 21 | 21 | 27 | 80 | 2 | -4 | 65 | 59
HARINIVAS S | 2026-10-14 | JOSVIN SUNNY | 2026-10-14 | PR are generated for all NPCB project | GM O&D VISIT Q2 FY26-27 AT KOZHIKODE IRD | 2026-09-17 16:00 | AUD-2026-10-2000017709 | 2026-09-16 12:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155523 | Closed | JOSVIN SUNNY | 2026-10-14 | Capitalization of all the physically completed projects achieved | 4.3 | 2 projects to be completed for which the job is under progress | 1892 | KOZHIKODE DEPOT | PRs are to be submitted for all NPCB projects and ensure timely closure as per approved timelines. | SOD | Marketing | CZR | 2026-10-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-10-31 | AUD-2026-10-2000017709ACN-2026-10-4000155523 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017709ACN-2026-10-4000155523 | 2026-09-17 16:00 | 32.0872 | 408 | >20 | AUD-2026-10-2000017709 - ACN-2026-10-4000155523 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017709ACN-2026-10-4000155523 | AUD-2026-10-2000017709ACN-2026-10-4000155523 | 21 | 21 | 27 | 80 | 2 | -4 | 61 | 59
|  | SINGH BHOPENDRA | 2026-10-14 | NO Recommendation | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146669 | Completed | SINGH BHOPENDRA | 2026-10-14 |  | 1 |  | 1157 | BAREILLY DEPOT | XX | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146669 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146669 | 2026-07-16 | 95.7538 | 363 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146669 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000015610ACN-2026-07-4000146669 |  | AUD-2026-07-2000015610ACN-2026-07-4000146669 | 21 |  | 27 | 80 | 3 | 3 | 52
|  | RAHUL RAJ | 2026-10-14 | Medical box updation is being done on Monthly basis | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150329 | Completed | RAHUL RAJ | 2026-10-14 | List of item kept in medical box at security gate not updated. | 6.1 | Additional Observations | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-05 |  | 1 |  | S1 | F1 | 2026-09-05 | AUD-2026-08-2000016904ACN-2026-09-4000150329 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150329 | 2026-08-06 | 74.7538 | 369 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150329 | 532 | 8294 | 21 | 8294 | 44 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150329 |  | AUD-2026-08-2000016904ACN-2026-09-4000150329 | 21 |  | 27 | 80 | 2 | 2 | 53
|  | RAHUL RAJ | 2026-10-14 | Hydrant line layout modification is completed. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150330 | Completed | RAHUL RAJ | 2026-10-14 | Hydrant layout displayed at license area gate is not covering HVLRs. | 6.2 | Additional Observations | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150330 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150330 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150330 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150330 |  | AUD-2026-08-2000016904ACN-2026-09-4000150330 | 21 |  | 27 | 80 | 2 | 2 | 57
|  | RAHUL RAJ | 2026-10-14 | Hydrant line layout modification is completed. | SR MANAGEMENT INSP OF HAZIRA Q2 26-27 | 2026-08-06 | AUD-2026-08-2000016904 | 2026-08-05 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150331 | Completed | RAHUL RAJ | 2026-10-14 | Foam monitor identification number is not matching with the field and hydrant layout. | 6.3 | Additional Observations | 1412 | HAZIRA IRD (STP 1044) | Corrective action shall be taken | SOD | Marketing | NWR | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016904ACN-2026-09-4000150331 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016904ACN-2026-09-4000150331 | 2026-08-06 | 74.7538 | 394 | >20 | AUD-2026-08-2000016904 - ACN-2026-09-4000150331 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016904ACN-2026-09-4000150331 |  | AUD-2026-08-2000016904ACN-2026-09-4000150331 | 21 |  | 27 | 80 | 2 | 2 | 57
|  | RAHUL RAJ | 2026-10-14 | TK-05 : Product Dip checked again on , Product Dip[TAS Vs physical Dip] found within limit. for TK 01 Product Dip TAS Vs Physical Dip]: within limit. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131782 | Completed | RAHUL RAJ | 2026-10-14 | TK05: Reference height: As per record: 1226.6 CM, Actual in filed: 1226.6 CM Product Dip TAS Dip: 639.3 CM, Physical dip: 639.7 mm. Water Dip: TAS: nil, Physical: Nil TK01: Reference height: As per record: 1102.3 CM, Actual in filed: 1102.3 CM TAS Dip:856.0 CM, Physical dip: 856.2 mm. Water Dip: TAS: nil, Physical: Nil | 3.7 | Inventory physical dip of minimum two tanks taken | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 |  | 1 |  | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131782 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131782 | 2026-08-06 | 74.7538 | 279 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131782 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131782 |  | AUD-2026-05-2000012564ACN-2026-05-4000131782 | 21 |  | 27 | 80 | 2 | 2 | 40
|  | RAHUL RAJ | 2026-10-14 | ITDG letter and action taken letters are being filed for Vts deviated TT for records. | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131779 | Completed | RAHUL RAJ | 2026-10-14 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-07 |  | 1 |  | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131779 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131779 | 2026-08-06 | 74.7538 | 279 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131779 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131779 |  | AUD-2026-05-2000012564ACN-2026-05-4000131779 | 21 |  | 27 | 80 | 2 | 2 | 40
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | Road just outside Terminal emergency gate has been repaired & other observations are noted for improvement in future drills | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155018 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Drill conducted on TT gantry TT unloading valve maniold fire and Parking area TT fuel tank on fire. 1. Communication between teamsand fire chief found not effective. Mega phone is used at the end of drill. 2. Foam drums are positioned below monitor nozzle leading to possibility of hitting person handling foam drum and nozzle. 3. Communication from first fire responder to other teams was not thru VHF/other medium, leading to delayed response from team. 4. Performance of monitor and DCP found satisfactory. 5. Mutual aid member reported to site. IOCL LPG mutual aid meber expressed difficulity in locating the HPCL vadodara terminal, leading to delayed reporting. 6. Road just outside Terminal emergency gate found settled. 7. Crew of TTs other than on fire were not present in the TT cabin. 8. Emergency TT parking gate was opened and few trucks were lined up for exit from the TT Parking Area. For other trucks TT drivers did not respond. 9. Public annoucement system is not utilised during mock drill. 10. Security deployed at TT parkingis not having VHF for communicating any emergency in TT Parking area. | 2.2 | Double contingency scenario simulated; observations recorded | 1410 | VADODARA TERMINAL | Location to take correction action as per obseration recorded. | SOD | Marketing | NWR | 2026-10-30 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155018 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155018 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155018 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155018 | AUD-2026-09-2000017759ACN-2026-09-4000155018 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | daily updation is being carried out | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000155017 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Daily reports Auto reco and AIM hold shall be updated regularly. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1410 | VADODARA TERMINAL | Daily updation shall be ensured. | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155017 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155017 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155017 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155017 | AUD-2026-09-2000017759ACN-2026-09-4000155017 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | same has been carried out as per SOP | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155019 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Surprise night inspection has been done on 13.09.2026 by location | 2.4 | Security alertness checked (night-halt / surprise checks) | 1410 | VADODARA TERMINAL | Surprise Night Inspection to be done by Location as per SOP and record to be maintained | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155019 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155019 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155019 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155019 | AUD-2026-09-2000017759ACN-2026-09-4000155019 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | sprinkler nozzle cleaning completed | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000155023 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | 1. During random inspection of hose deployed in the field of HB 128, Both hoses were found rejected. 2. new HVLR No. 13 has not worked during testing. Since complied. 3. Sprinkler system tested quaterly. During testing of the firefighting system at MS Tank TK-101A, several dyke sprinkler nozzles were found choked, resulting in inadequate water discharge/coverage. The affected sprinklers included U-8, U-19 to U-22, L-09, and the section from U-14 to U-22. 4. Rim seal tested on TK101 worked satisfactory. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155023 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155023 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155023 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155023 | AUD-2026-09-2000017759ACN-2026-09-4000155023 | 21 | 21 | 27 | 80 | 0 | -26 | 70 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | same has been ensured from now | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155025 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | The TT safety checklist records were checked for the period from July 2026 to 10 September 2026. It is observed that all operational TTs have not been covered under the safety check as required by OISD 244. | 3.1 | TT fittings & discipline checked | 1410 | VADODARA TERMINAL | a. As per OISD 244, all operational TTs must be covered on a quarterly basis. b. All related records should be captured while filling out the safety checklist for TTs. This includes: PESO license details and validity Fire extinguisher testing and refill inputs Calibration certificate number and date c. A demonstration of fire extinguisher operation must be conducted during the TT safety check. | SOD | Marketing | NWR | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017759ACN-2026-09-4000155025 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155025 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155025 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155025 | AUD-2026-09-2000017759ACN-2026-09-4000155025 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | corrective action such as blacklisting of TTs has been initiated on the transporter to control the violations | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155026 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | The VTS deviation records were checked for the period from July to 10th September. The location is obtaining explanations from transporters for VTS violations and subsequently unblocking the TTs from Novex. However, the number of violations during the above period is very high and not showing any reduction. | 3.3 | VTS deviations reviewed | 1410 | VADODARA TERMINAL | The location must ensure the following: a. Route creation should be prioritized with strong follow-up by the Sales Officer. b. Daily monitoring must be carried out for VTS violations as per the completed reports recorded in the VTS portal, with reasons mentioned for each violation. c. Based on the records captured in the daily VTS reports, appropriate corrective actions should be taken to reduce VTS violations. | SOD | Marketing | NWR | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017759ACN-2026-09-4000155026 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155026 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155026 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155026 | AUD-2026-09-2000017759ACN-2026-09-4000155026 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | TTs checking towards EM locking have improved | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155027 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | a. Checked record from July to 10th Sept 2026. All Operating TTs have not checked by programmable key in every 15 days. | 3.5 | EM Lock SOP compliance verified | 1410 | VADODARA TERMINAL | a. All TTs checking to be covered by programmable key and record to be maintained. | SOD | Marketing | NWR | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017759ACN-2026-09-4000155027 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155027 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155027 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155027 | AUD-2026-09-2000017759ACN-2026-09-4000155027 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | report towards abnormal gain/loss during reco has been shared with zone on time to time basis | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155028 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Auto reconciliation is being done with 89 %. Duly signed records are available at location. | 3.8 | Auto vs Manual reconciliation checked | 1410 | VADODARA TERMINAL | a. The reasons for stock loss must be properly analysed, and justifications should be maintained at the location for record purposes. These reasons should be provided to the Zone as and when required. b. Pipeline quantity booking must be done in a timely manner to avoid AIM holds and to increase the auto-reconciliation percentage. The matter should be taken up with the Pipeline Department. | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155028 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155028 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155028 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155028 | AUD-2026-09-2000017759ACN-2026-09-4000155028 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | detailed analysis towards losses of naphtha has been carried out | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155029 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Location is maintaing records for abnormal variation however proper analysis is not being carried out. | 3.9 | Abnormal variations / unused assets reviewed | 1410 | VADODARA TERMINAL | Location shall take corrective action | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155029 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155029 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155029 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155029 | AUD-2026-09-2000017759ACN-2026-09-4000155029 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | water was received from HRRL refinery. Same was drained from tank & routed to ETP & then released to storm water drain. No layering& oil content found in this water, although discolouration was found in the same. Hence, water was hold back inside the terminal & not released outside the terminal to avoid any unwarranted issues | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000155030 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | outlet from dyke has provision to either divert to ETP/ OWS or to main storm water drain. Stagnant black/contaminated water was observed in Tank Farm No. 5, indicating inadequate drainage/housekeeping and possible hydrocarbon contamination. | 3.15 | Housekeeping & PPE usage checked | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155030 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155030 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155030 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155030 | AUD-2026-09-2000017759ACN-2026-09-4000155030 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | load has been distributed accordingly | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155035 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Location to review electrical load on emergency panel and emergency DG and take corrective action. | 6.1 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-12-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-09-2000017759ACN-2026-09-4000155035 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155035 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155035 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155035 | AUD-2026-09-2000017759ACN-2026-09-4000155035 | 21 | 21 | 27 | 80 | 0 | -26 | 70 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | MOC has been approved for changes in tank storage facility changes | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155038 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Tank farm SOP to be revised as per change of product in tanks (106 B MTO to be added for valve sequence) and also current ongoing changes for conversion of tanks to ATF to be included in revised SOP. | 6.4 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155038 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155038 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155038 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155038 | AUD-2026-09-2000017759ACN-2026-09-4000155038 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | same has been sealed | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155044 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Cable opening were observed in UG tank farm. | 6.10 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155044 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155044 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155044 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155044 | AUD-2026-09-2000017759ACN-2026-09-4000155044 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | corrective action & followup with vendor is being done | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155046 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | VA alerts were checked for the period from July 2026 to 10 September 2026. It has been observed that a large number of false alertsare appearing in the system. The location must coordinate with the VA vendor to reduce these false alerts and take timely action toavoid further escalation of VA alerts to the Zone. | 6.12 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155046 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155046 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155046 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155046 | AUD-2026-09-2000017759ACN-2026-09-4000155046 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | same has been maintained | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155048 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Batch formation is to be created after each PLT receipt, and the batch number must be maintained. BFT is to be carried out as per the batch formation, and records must be maintained for all batches. | 6.14 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155048 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155048 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155048 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155048 | AUD-2026-09-2000017759ACN-2026-09-4000155048 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | records has been maintained for the batches | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155049 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Dispatch of EBMS is to be carried out as per batch. The batch number must be maintained, and BFT is to be conducted in line with the batch formation. Records must be maintained for all batches. | 6.15 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155049 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155049 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155049 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155049 | AUD-2026-09-2000017759ACN-2026-09-4000155049 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | log book has been maintained | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155101 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | The log book for sample retention has been checked. The concerned officer and LIC must review, sign, and verify the log book on a regular basis. | 6.17 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155101 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155101 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155101 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155101 | AUD-2026-09-2000017759ACN-2026-09-4000155101 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | SOP Has been updated | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155039 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | HVLR SOP is not revised after installation of 1 additional HVLR. Signal sharing with Pipeline SOP not available. | 6.5 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155039 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155039 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155039 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155039 | AUD-2026-09-2000017759ACN-2026-09-4000155039 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | sop has been revised in TT gantry | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155040 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | SOP boards at TT Gantry for loading to be revised along with earthing diagram (top loading available) SOP board. | 6.6 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155040 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155040 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155040 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155040 | AUD-2026-09-2000017759ACN-2026-09-4000155040 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | TSV setting changed in field as per SOP | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155041 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | TT Parking, STP, Water tanker unloading SOP to be developed. SOP displayed in field checked and difference observed for TT Gantry, Calibration Shed. Field SOP mentions TSV setting 12 Kg/Cm2 however TSV was set on 14 KG/CM2 at foam shed. | 6.7 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155041 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155041 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155041 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155041 | AUD-2026-09-2000017759ACN-2026-09-4000155041 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-14 | PANWAR JITENDRA SINGH | 2026-10-14 | hose has been replaced | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155042 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | During random inspection of hose deployed in the field of HB 128, Both hoses were found rejected. | 6.8 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155042 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155042 | 2026-09-10 21:00 | 38.8788 | 408 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155042 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155042 | AUD-2026-09-2000017759ACN-2026-09-4000155042 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | "Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestalsfor 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. Bottom loading work completed at location and all bays converted to bottom loading. " | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127321 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | Maintenance activities was reviewed. Work is being carried out at railway sidings for Fire Water Sprinkler installation and at TT Gantry for bottom loading work, which is nearing to completion. | 4.2 | Maintenance activities reviewed | 1436 | SAGAR DEPOT | location to pace up and complete the work | SOD | Marketing | CEN | 2026-06-30 | POOR PLANNING OR RISK ASSESSMENT | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127321 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127321 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127321 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011238ACN-2026-03-4000127321 | AUD-2026-03-2000011238ACN-2026-03-4000127321 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | "1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. " | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127322 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | Project progress was reviewed for Railway Siding Sprinker work, TAS Revamping & TT Gantry Bottom Loading work. | 4.3 | Project progress reviewed | 1436 | SAGAR DEPOT | Location to follow up with vendor to expedite completion of work with set time frame. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 3 | PROCESS SAFETY | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127322 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127322 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127322 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011238ACN-2026-03-4000127322 | AUD-2026-03-2000011238ACN-2026-03-4000127322 | 21 | 21 | 26 | 80 | 4 | 2 | 44 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-10-14 | Manpower is provided and stock loss is maintained as per target | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146670 | Closed | SINGH BHOPENDRA | 2026-10-14 | due to stock issues and manpower issues at location required not focus is not being given | 1.3 | Pending issues reviewed | 1157 | BAREILLY DEPOT | to complete all pending observations as per timelines | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146670 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146670 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146670 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146670 | AUD-2026-07-2000015610ACN-2026-07-4000146670 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-10-14 | Manpower is provided and stock loss is maintained as per target | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-07-4000146671 | Closed | SINGH BHOPENDRA | 2026-10-14 | due to stock issues and manpower issues at location required not focus is not being given | 1.4 | Earlier action points status checked | 1157 | BAREILLY DEPOT | to complete all pending observations as per timelines | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146671 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146671 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146671 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146671 | AUD-2026-07-2000015610ACN-2026-07-4000146671 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-10-14 | Location procured the colour-blindness book and checked the TT driver colour blindness | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146679 | Closed | SINGH BHOPENDRA | 2026-10-14 | Checked | 2.16 | Eyesight / colour-blindness awareness checked | 1157 | BAREILLY DEPOT | XX | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146679 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146679 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146679 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146679 | AUD-2026-07-2000015610ACN-2026-07-4000146679 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-10-14 | Location to take corrective action | SR MANAGEMENT AUDIT BAREILLY | 2026-07-16 | AUD-2026-07-2000015610 | 2026-07-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146673 | Closed | CH RAGHU | 2026-07-31 | Checked and meet as per OISD Standard. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1157 | BAREILLY DEPOT | Boundary wall painting work done near the transformer area | SOD | Marketing | NUZ | 2026-08-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-08-30 | AUD-2026-07-2000015610ACN-2026-07-4000146673 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015610ACN-2026-07-4000146673 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-07-2000015610 - ACN-2026-07-4000146673 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015610ACN-2026-07-4000146673 | AUD-2026-07-2000015610ACN-2026-07-4000146673 | 21 | 21 | 27 | 80 | 3 | 3 | 52 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-05-02 | All TT are physicaly checked at TT gantry after MFM installation, TT release with correct dip only | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124801 | Closed | SINGH BHOPENDRA | 2026-05-02 | Bay No 6, UP83CT6212: Comp 1: 0mm, Comp 2: 0mm, Comp 3: +4mm Bay No 7, UP25BT3110: Comp 1: 0mm, Comp 2: +3mm, Comp 3: +0mm Bay No8, UP25GT3146: Comp 1: 0mm, Comp 2: +2mm, Comp 3: +2mm, Comp 4: +4mm | 3.2 | Post-loading dip checks verified | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124801 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124801 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124801 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124801 | AUD-2026-03-2000011014ACN-2026-03-4000124801 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-06-20 | As per the comments, the actual dip and physical dip of TK-03 are matching. For TK-06, the auto dip and physical dip readings have been corrected by the OEM, as the radar system is under the warranty period | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124802 | Closed | SINGH BHOPENDRA | 2026-06-20 | TK06: Tas Product Dip: 738.5 CM Actual product dip: 738.1 CM TK03: Tas Product Dip: 887.5 CM Actual product dip: 887.5 CM | 3.7 | Inventory physical dip of minimum two tanks taken | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124802 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124802 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124802 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124802 | AUD-2026-03-2000011014ACN-2026-03-4000124802 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-06-20 | Tree trimming has been completed, ensuring that the monitor view is clear and can accurately cover the required location | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124820 | Closed | SINGH BHOPENDRA | 2026-06-20 | Throw of M58 monitor in siding is blocked by tree. | 6.10 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124820 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124820 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124820 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124820 | AUD-2026-03-2000011014ACN-2026-03-4000124820 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 59
SONAR AMIT KUMAR | 2026-10-14 | SINGH BHOPENDRA | 2026-06-20 | The location officer is now signing the sample register daily, and all related records are being maintained systematically. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124821 | Closed | SINGH BHOPENDRA | 2026-06-20 | Sample retention register was not since 11.02.2026 and sample disposal was last signed on date 24.01.2026 | 6.11 |  | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124821 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124821 | 2026-07-16 | 95.7538 | 408 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124821 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124821 | AUD-2026-03-2000011014ACN-2026-03-4000124821 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | "1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147906 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | Out of 11 points, 6 points are closed and 5 points are still open. The open points are pertaining mainly to TAS Revamp, Railway siding and targeted to close by H1. | 1.4 | Earlier action points status checked | 1436 | SAGAR DEPOT | To ensure completion of Railway siding project by H1 and TAS Revamp Project by 31.08.2026. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-08-2000016370ACN-2026-08-4000147906 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147906 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147906 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147906 | AUD-2026-08-2000016370ACN-2026-08-4000147906 | 21 | 21 | 27 | 80 | 4 | 2 | 57 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | "1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. " | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000147908 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | To expedite completion of Sprinkler Line Project at Railway siding and also expediting TAS Revamp Project. | 1.8 | Improvement plans discussed | 1436 | SAGAR DEPOT | Already covered above under point no. 1.4. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-08-2000016370ACN-2026-08-4000147908 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147908 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147908 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147908 | AUD-2026-08-2000016370ACN-2026-08-4000147908 | 21 | 21 | 27 | 80 | 4 | 2 | 57 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | Dip variation verified in presence of TAS vendor with manual dip and veriation issue restored. | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000147914 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | Physical Dip checked for TK17 (MS), TK18 (HSD) and TK14 (Ethanol). Observed variation in actual Dip V/s TAS Dip due to ongoing TAS Revamp Project. The work is underway. | 3.7 | Inventory physical dip of minimum two tanks taken | 1436 | SAGAR DEPOT | Location to follow up with TAS vendor and expedite completion of Project latest by 31.08.2026. | SOD | Marketing | CEN | 2026-08-20 | POOR EQUIPMENT MAINTENANCE | 2 | PROCESS SAFETY | S2 | F1 | 2026-08-20 | AUD-2026-08-2000016370ACN-2026-08-4000147914 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147914 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147914 | 532 | 8294 | 21 | 8294 | 60 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147914 | AUD-2026-08-2000016370ACN-2026-08-4000147914 | 21 | 21 | 27 | 80 | 4 | 2 | 51 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | "1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. " | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016370 | 2026-08-06 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147918 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | 1) TAS Revamp Project still underway. Targeted to complete by 31.08.2026 2) Railway siding Fire Sprinkler line to be completed. Targeted to complete it by 31.08.2026 | 4.3 | Project progress reviewed | 1436 | SAGAR DEPOT | Targeted to complete by 31.08.2026. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-08-2000016370ACN-2026-08-4000147918 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016370ACN-2026-08-4000147918 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-08-2000016370 - ACN-2026-08-4000147918 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016370ACN-2026-08-4000147918 | AUD-2026-08-2000016370ACN-2026-08-4000147918 | 21 | 21 | 27 | 80 | 4 | 2 | 57 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | 1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. 4. Tank paining done for TK17 and TK18. | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130679 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | The following Project work is under progress at location: 1) Rly Siding Sprinkler Work 2) Rly Siding Modification of FW system and cross over 3) TAS Revamp Work 4) Tank Painting | 4.3 | Project progress reviewed | 1436 | SAGAR DEPOT | Location to expedite project work and ensure closure of project activites in a time bound manner. | SOD | Marketing | CEN | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-05-2000012507ACN-2026-05-4000130679 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130679 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130679 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130679 | AUD-2026-05-2000012507ACN-2026-05-4000130679 | 21 | 21 | 27 | 80 | 4 | 2 | 61 | 59
BANTHIYA RITESH DEELIP | 2026-10-14 | PANWAR VIPIN SINGH | 2026-10-14 | 1. Major work completed at siding area ( including 44 no. sprinkler segments, Laying of 1589 m hydrant pipeline, 240 no. of pedestals for 8 inch pipeline, 44 no. track supports, 345 No. of box supports for sprinkler line segments. 2. Bottom loading work completed at location and all bays converted to bottom loading. 3. TAS Revamping project SAT completed. 4. Tank painting work completed for TK17 and TK18 | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000130681 | Closed | PANWAR VIPIN SINGH | 2026-10-14 | Nil | 6.1 | High priority areas requiring immediate action. | 1436 | SAGAR DEPOT | Expediting work of all the 4 ongoing Project activities and ensure completion in time bound manner. | SOD | Marketing | CEN | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-05-2000012507ACN-2026-05-4000130681 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130681 | 2026-08-07 19:00 | 72.9622 | 408 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130681 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-05-2000012507ACN-2026-05-4000130681 | AUD-2026-05-2000012507ACN-2026-05-4000130681 | 21 | 21 | 27 | 80 | 4 | 2 | 61 | 59
|  | KUMAR ANIMESH | 2026-10-14 | Lube billing related issue taken up with Regional Office, we are in close coordination with regional office. | SENIOR MANAGMENT AUDIT : BALASORE | 2026-03-12 17:00 | AUD-2026-03-2000011313 | 2026-03-11 08:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122641 | Completed | KUMAR ANIMESH | 2026-10-14 | Dealer meeting was held on 10.3.2026 during the visit of ED-Retail and only points related to Lubes invoices raised | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1636 | BALASORE DEPOT | lubes not uplifted by dealers against invoices made in last 6 months advised to uplift in this month | SOD | Marketing | ECZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011313ACN-2026-03-4000122641 | OR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011313ACN-2026-03-4000122641 | 2026-09-26 17:30 | 23.0247 | 211 | >20 | AUD-2026-03-2000011313 - ACN-2026-03-4000122641 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011313ACN-2026-03-4000122641 |  | AUD-2026-03-2000011313ACN-2026-03-4000122641 | 21 |  | 26 | 80 | 12 | 12 | 31
CHOPPA SANTHOSH KUMAR | 2026-10-14 | PP AKHIL | 2026-10-14 | All the points under Safe 100 and MDSA 24-25 are complied and closed in SAP SAFE 100 46 /46 Closed. MDSA 24-25 14/14 Closed. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123491 | Closed | PP AKHIL | 2026-10-14 | Recent review recommendations were reviewed along with pending audit points of SSA & MDSA | 1.4 | Earlier action points status checked | 1937 | SURYAPET TERMINAL | All MDSA 24-25 Points are complied. 14/14 Points are complied and same updated in SAP vide Audit Number AUD-2025-03-2000001637 | SOD | Marketing | SCR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123491 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123491 | 2026-08-04 18:45 | 75.9726 | 408 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123491 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123491 | AUD-2026-03-2000011061ACN-2026-03-4000123491 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 59
CHOPPA SANTHOSH KUMAR | 2026-10-14 | PP AKHIL | 2026-10-14 | Emergency exit gate sealed and register maintained with seal number for opening and closing of emergency gate. Repainting done on ethanol unloading pump bulk air eliminator and faded pipes and valves etc. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-08-4000147026 | Closed | PP AKHIL | 2026-10-14 | Full field round completed, gantry, tank farm-1 and tank farm-2, product pump house, MCC sub-station, control room, Security , emergency exit gate | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1937 | SURYAPET TERMINAL | Emergency exit gate seal on lock not available, to ensure seal for the lock . Ethanol unloading pump bulk air eliminator painting peeled off and corrosion visible , to be repainted. | SOD | Marketing | SCR | 2026-08-05 | FATIGUE AND STRESS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-05 | AUD-2026-08-2000016363ACN-2026-08-4000147026 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147026 | 2026-08-04 18:45 | 75.9726 | 408 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147026 | 532 | 8294 | 21 | 8294 | 75 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147026 | AUD-2026-08-2000016363ACN-2026-08-4000147026 | 21 | 21 | 27 | 80 | 0 | 0 | 49 | 59
CHOPPA SANTHOSH KUMAR | 2026-10-14 | PP AKHIL | 2026-10-14 | Tank 1C ,MEFG position changed and ensured foam generation near collection pit | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147032 | Closed | PP AKHIL | 2026-10-14 | MEFG to be shifted to proper position near collection pit for routing to Dyke Valves | 6.3 |  | 1937 | SURYAPET TERMINAL | MEFG to be shifted to proper position near collection pit for routing to Dyke Valves | SOD | Marketing | SCR | 2026-08-30 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-08-30 | AUD-2026-08-2000016363ACN-2026-08-4000147032 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147032 | 2026-08-04 18:45 | 75.9726 | 408 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147032 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147032 | AUD-2026-08-2000016363ACN-2026-08-4000147032 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 59
CHOPPA SANTHOSH KUMAR | 2026-10-14 | PP AKHIL | 2026-10-14 | New hooter fixed at security gate and connected with Emergency gate. | AUDIT UPLOAD IN SAP | 2026-08-04 18:45 | AUD-2026-08-2000016363 | 2026-08-04 09:15 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147033 | Closed | PP AKHIL | 2026-10-14 | Emergency Gate (EGKMS) Local Hooter found working but hooter at Security to be made functional | 6.4 |  | 1937 | SURYAPET TERMINAL | Emergency Gate (EGKMS) Local Hooter found working but hooter at Security to be made functional | SOD | Marketing | SCR | 2026-08-30 | INSTRUMENTATION OR ALARM FAILURES | 5 | EMERGENCY | S1 | F5 | 2026-08-30 | AUD-2026-08-2000016363ACN-2026-08-4000147033 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016363ACN-2026-08-4000147033 | 2026-08-04 18:45 | 75.9726 | 408 | >20 | AUD-2026-08-2000016363 - ACN-2026-08-4000147033 | 532 | 8294 | 21 | 8294 | 50 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016363ACN-2026-08-4000147033 | AUD-2026-08-2000016363ACN-2026-08-4000147033 | 21 | 21 | 27 | 80 | 0 | 0 | 52 | 59
|  | RANA PULKIT | 2026-10-15 | net placed on sample room gate | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125613 | Completed | RANA PULKIT | 2026-10-15 | Net to be placed on gate of sample room to block birds/insect entry | 6.4 | SAMPLE ROOM | 1509 | SHOLAPUR TERMINAL | location to take necessary corrective action | SOD | Marketing | WZ | 2026-03-31 | INADEQUATE SAFETY CULTURE | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011316ACN-2026-03-4000125613 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125613 | 2026-09-19 | 30.7538 | 211 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125613 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125613 |  | AUD-2026-03-2000011316ACN-2026-03-4000125613 | 21 |  | 26 | 80 | 0 | 0 | 31
|  | RANA PULKIT | 2026-10-15 | scrap disposal is in process, same observation in 3.9 is kept open till complied | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125610 | Completed | RANA PULKIT | 2026-10-15 | Location has identified Miscellanous scrap, disposal to be expedited | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1509 | SHOLAPUR TERMINAL | location to dispose misc. scrap | SOD | Marketing | WZ | 2026-04-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011316ACN-2026-03-4000125610 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125610 | 2026-09-19 | 30.7538 | 241 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125610 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125610 |  | AUD-2026-03-2000011316ACN-2026-03-4000125610 | 21 |  | 26 | 80 | 0 | 0 | 35
|  | RANA PULKIT | 2026-10-15 | refer remarks of Audit no. AUD-2026-03-2000011316 3.9 for status of scrap disposal | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146556 | Completed | RANA PULKIT | 2026-10-15 | Location is under process to scrap misc. items | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1509 | SHOLAPUR TERMINAL | scrap disposal to be completed by 30.04.2026 | SOD | Marketing | WZ | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146556 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146556 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146556 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146556 |  | AUD-2026-07-2000016455ACN-2026-07-4000146556 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-10-15 | refer remarks of 3.20 | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146553 | Completed | RANA PULKIT | 2026-10-15 | Location is under process to scrap misc. items | 3.9 | Abnormal variations / unused assets reviewed | 1509 | SHOLAPUR TERMINAL | scrap disposal to be completed by 31.12.2026 | SOD | Marketing | WZ | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 4 | ENVIRONMENTAL | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146553 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146553 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146553 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146553 |  | AUD-2026-07-2000016455ACN-2026-07-4000146553 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-10-15 | auction has been done, refeer remarks of 3.20 | SHOLAPUR LOCAION VISIT 20.05.2026 | 2026-05-21 | AUD-2026-07-2000016455 | 2026-05-20 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000146559 | Completed | RANA PULKIT | 2026-10-15 | Location has identified Miscellanous scrap, disposal to be expedited | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1509 | SHOLAPUR TERMINAL | location to dispose misc. scrap | SOD | Marketing | WZ | 2026-08-31 | POOR EQUIPMENT MAINTENANCE | 4 | ENVIRONMENTAL | S2 | F2 | 2026-08-31 | AUD-2026-07-2000016455ACN-2026-07-4000146559 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016455ACN-2026-07-4000146559 | 2026-09-19 | 30.7538 | 364 | >20 | AUD-2026-07-2000016455 - ACN-2026-07-4000146559 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-07-2000016455ACN-2026-07-4000146559 |  | AUD-2026-07-2000016455ACN-2026-07-4000146559 | 21 |  | 27 | 80 | 0 | 0 | 52
|  | RANA PULKIT | 2026-10-15 | being complied as per schedule. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153371 | Completed | RANA PULKIT | 2026-10-15 | OISD 2022-23 Total points-21 Complied-21 MDSA 2025-26 Total points-70 Complied-44 SSA 2025-26 Total points-43 Complied-43 | 3.10 | TFMS/SAP reconciliation checked | 1509 | SHOLAPUR TERMINAL | Pending points to be complied as per scheduled timelines and action plan | SOD | Marketing | WZ | 2026-12-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017372ACN-2026-09-4000153371 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153371 | 2026-09-19 | 30.7538 | 486 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153371 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153371 |  | AUD-2026-09-2000017372ACN-2026-09-4000153371 | 21 |  | 27 | 80 | 0 | 0 | 70
|  | RANA PULKIT | 2026-10-15 | being complied as per schedule. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153372 | Completed | RANA PULKIT | 2026-10-15 | OISD 2022-23 Total points-21 Complied-21 MDSA 2025-26 Total points-70 Complied-40 SSA 2025-26 Total points-43 Complied-33 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1509 | SHOLAPUR TERMINAL | Pending points to be complied as per scheduled timelines and action plan | SOD | Marketing | WZ | 2026-12-31 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-09-2000017372ACN-2026-09-4000153372 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153372 | 2026-09-19 | 30.7538 | 486 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153372 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153372 |  | AUD-2026-09-2000017372ACN-2026-09-4000153372 | 21 |  | 27 | 80 | 0 | 0 | 70
|  | RANA PULKIT | 2026-10-15 | timelines being followed | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153373 | Completed | RANA PULKIT | 2026-10-15 | 2 projects are in progress at location. | 4.3 | Project progress reviewed | 1509 | SHOLAPUR TERMINAL | to be completed as per timelines | SOD | Marketing | WZ | 2026-10-31 | THIRD PARTY ERRORS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017372ACN-2026-09-4000153373 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153373 | 2026-09-19 | 30.7538 | 425 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153373 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153373 |  | AUD-2026-09-2000017372ACN-2026-09-4000153373 | 21 |  | 27 | 80 | 0 | 0 | 61
|  | RANA PULKIT | 2026-10-15 | PM jobs being done on time, no AIM hold due PM jobs. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153374 | Completed | RANA PULKIT | 2026-10-15 | Following is the PM performance of location for last 3 month being done 100% by end of mont | 4.4 | Quality of PM compliance reviewed | 1509 | SHOLAPUR TERMINAL | ensure completion of PM jobs well before month end to avoid any AIM hold due to non-completion of PM Jobs | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153374 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153374 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153374 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153374 |  | AUD-2026-09-2000017372ACN-2026-09-4000153374 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-10-15 | HVLR-7 made functional, tested for its reach and foam generation | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153375 | Completed | RANA PULKIT | 2026-10-15 | HVLR 7 to be made functional. | 6.1 | Safety | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153375 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153375 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153375 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153375 |  | AUD-2026-09-2000017372ACN-2026-09-4000153375 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-10-15 | Mirror trolley is being used for inspection of bottom of TTs | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153376 | Completed | RANA PULKIT | 2026-10-15 | Mirror trolley to be used for checking the bottom of the TT. | 6.2 | SECURITY | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153376 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153376 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153376 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153376 |  | AUD-2026-09-2000017372ACN-2026-09-4000153376 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-10-15 | Platform fabricated and being used. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153377 | Completed | RANA PULKIT | 2026-10-15 | Platform to be made for TT entry gate to be used for checking the inside of the TT. | 6.3 | Safety | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153377 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153377 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153377 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153377 |  | AUD-2026-09-2000017372ACN-2026-09-4000153377 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-10-15 | eye-wash unit cleaned, and functionality checked. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153378 | Completed | RANA PULKIT | 2026-10-15 | Eye wash near TLF pump house to be cleaned and to be taken back in use. | 6.4 | Safety | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153378 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153378 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153378 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153378 |  | AUD-2026-09-2000017372ACN-2026-09-4000153378 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | RANA PULKIT | 2026-10-15 | All bays made soil free. | SHOLAPUR LOCATION VISIT 31.08.2026 | 2026-08-31 | AUD-2026-09-2000017372 | 2026-08-31 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000153379 | Completed | RANA PULKIT | 2026-10-15 | bay to bay separation soil to be removed. | 6.5 | Safety | 1509 | SHOLAPUR TERMINAL | Location to take necessary corrective action | SOD | Marketing | WZ | 2026-09-30 | THIRD PARTY ERRORS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017372ACN-2026-09-4000153379 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017372ACN-2026-09-4000153379 | 2026-09-19 | 30.7538 | 394 | >20 | AUD-2026-09-2000017372 - ACN-2026-09-4000153379 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017372ACN-2026-09-4000153379 |  | AUD-2026-09-2000017372ACN-2026-09-4000153379 | 21 |  | 27 | 80 | 0 | 0 | 57
|  | SATYENDRA CHOURASIA | 2026-10-15 | Follow up with VVSPL_SRS for MFM based accounting is being carried out | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-08-4000147044 | Completed | SATYENDRA CHOURASIA | 2026-10-15 | MFM based accounting not being done . VVSPL MFM to be calibrated , Hence, PLT booking presenlty done thru manual tank dips. | 5.1 | MFM based accounting at Pipeline and OMC location | 1919 | SECUNDERABAD TERMINAL | To follow up with VVSPL_SRS for MFM based accounting | SOD | Marketing | SCR | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-08-2000016364ACN-2026-08-4000147044 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147044 | 2026-08-06 19:00 | 73.9622 | 394 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147044 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147044 |  | AUD-2026-08-2000016364ACN-2026-08-4000147044 | 21 |  | 27 | 80 | 1 | -12 | 57
|  | SATYENDRA CHOURASIA | 2026-10-15 | EGKMS box is working now. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147901 | Completed | SATYENDRA CHOURASIA | 2026-10-15 | Emergency exit gate hooter/alarm in security cabin is not working | 6.5 |  | 1919 | SECUNDERABAD TERMINAL | To take with vendor for rectification | SOD | Marketing | SCR | 2026-10-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-31 | AUD-2026-08-2000016364ACN-2026-08-4000147901 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147901 | 2026-08-06 19:00 | 73.9622 | 425 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147901 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-08-2000016364ACN-2026-08-4000147901 |  | AUD-2026-08-2000016364ACN-2026-08-4000147901 | 21 |  | 27 | 80 | 1 | -12 | 61
|  | SATYENDRA CHOURASIA | 2026-10-15 | New Electrical gloves have been procured. | AUDIT UPLOAD IN SAP | 2026-08-06 19:00 | AUD-2026-08-2000016364 | 2026-08-06 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-08-4000147902 | Completed | SATYENDRA CHOURASIA | 2026-10-15 | Electrical gloves for 440 V to be replaced as leakage observed | 6.6 |  | 1919 | SECUNDERABAD TERMINAL | New Electrical gloves to be provided. | SOD | Marketing | SCR | 2026-10-14 | POOR PLANNING OR RISK ASSESSMENT | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-14 | AUD-2026-08-2000016364ACN-2026-08-4000147902 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016364ACN-2026-08-4000147902 | 2026-08-06 19:00 | 73.9622 | 408 | >20 | AUD-2026-08-2000016364 - ACN-2026-08-4000147902 | 532 | 8294 | 21 | 8294 | 5 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016364ACN-2026-08-4000147902 |  | AUD-2026-08-2000016364ACN-2026-08-4000147902 | 21 |  | 27 | 80 | 1 | -12 | 59
AILAVARAPU VENKATA KRISHNA MURTY | 2026-10-15 | DIWAKAR KAMLESH KUMAR | 2026-10-15 | 1. Corrective action taken on Earthpit No: 213 2. Alarm and Hooter of EGKMS made functional and operational. 3. Security guard has been infoprmed on EGKMS. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143386 | Closed | DIWAKAR KAMLESH KUMAR | 2026-10-15 | 1. Earthpit No: 213 checked and observed values IR 2.44 OHMS GR 0.44 OHMS. 2. Emergency Gate checked , Alarm and Hooter did not operate. 3. Security guard was not aware regarding the functioning. | 3.16 | Earth pits / boundary / vegetation control checked | 3708 | VISAKH NBOT | 1, 2, 3) Corective action to be taken | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143386 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143386 | 2026-09-18 17:30 | 31.0247 | 409 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143386 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015047ACN-2026-07-4000143386 | AUD-2026-07-2000015047ACN-2026-07-4000143386 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 59
AILAVARAPU VENKATA KRISHNA MURTY | 2026-10-15 | DIWAKAR KAMLESH KUMAR | 2026-10-15 | Alarm and Hooter of EGKMS has been restotred and necessary correction has been done. Now it is in working status. | AUDIT UPLOAD IN SAP | 2026-06-17 21:00 | AUD-2026-07-2000015047 | 2026-06-17 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143389 | Closed | DIWAKAR KAMLESH KUMAR | 2026-10-15 | Full field round completed Alarm and Hooter at Emergency Gate checked did not operate and Security guard was not aware regarding the functioning. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 3708 | VISAKH NBOT | Alarm and Hooter at Emergency Gate checked to be made fucntional and Security guard to be trained regarding its functioning. | SOD | Marketing | SCR | 2026-06-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015047ACN-2026-07-4000143389 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015047ACN-2026-07-4000143389 | 2026-09-18 17:30 | 31.0247 | 409 | >20 | AUD-2026-07-2000015047 - ACN-2026-07-4000143389 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015047ACN-2026-07-4000143389 | AUD-2026-07-2000015047ACN-2026-07-4000143389 | 21 | 21 | 27 | 80 | 2 | 1 | 44 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | Gate meeting with TT crew are conducted regularly. Record attached | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126316 | Closed | SUNITA | 2026-10-12 | Reviwed. Some deviations noted ex. daily gate meeting not conducted | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1554 | MR-II TERMINAL | 100% Compliance needed | SOD | Marketing | WZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126316 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126316 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126316 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126316 | AUD-2026-04-2000011147ACN-2026-04-4000126316 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 59
|  | ASHIRBADA MISHRA | 2026-10-15 | Sample room faded sticker removed and sample room name was duly painted. | Q2_FY26-27_CBE_SR.MANAGEMENT INSPECTION | 2026-08-28 17:00 | AUD-2026-09-2000017811 | 2026-08-28 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154833 | Completed | ASHIRBADA MISHRA | 2026-10-15 | Name of the Sample room is faded out. | 6.2 | Additional Observations | 1856 | COIMBATORE DEPOT | Sample room name to be re-written. | SOD | Marketing | SZ | 2026-10-31 |  | 1 |  | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017811ACN-2026-09-4000154833 | TN | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017811ACN-2026-09-4000154833 | 2026-08-28 17:00 | 52.0455 | 425 | >20 | AUD-2026-09-2000017811 - ACN-2026-09-4000154833 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017811ACN-2026-09-4000154833 |  | AUD-2026-09-2000017811ACN-2026-09-4000154833 | 21 |  | 27 | 80 | 0 | 1 | 61
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | Night inspection sheduled followed . Record attached for 2026 | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154985 | Closed | SUNITA | 2026-10-12 | Last night inspection on 17.05.2026 | 2.4 | Security alertness checked (night-halt / surprise checks) | 1554 | MR-II TERMINAL | Monthly one night inspection to be ensured | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154985 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154985 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154985 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154985 | AUD-2026-09-2000017375ACN-2026-09-4000154985 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | MOC was sent to MR to shift HVLR panels 60M away. MR Fire and Safety replied that since MR-II Terminal is in MR premises , OISD 116is applicable instead of OISD 117. IN OISD 116 there is no such requirement of panel being 60M away from target tank. Communications attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154986 | Closed | SUNITA | 2026-10-12 | Reviwed. | 2.5 | Emergency response preparedness reviewed | 1554 | MR-II TERMINAL | Location to initate MOC for shifting of HVLRs of tank farm to meet distance norms as per OISD | SOD | Marketing | WZ | 2026-09-30 | POOR COMMUNICATION | 8 | ASSET INTEGRITY | S4 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154986 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154986 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154986 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017375ACN-2026-09-4000154986 | AUD-2026-09-2000017375ACN-2026-09-4000154986 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | All Reporting Contract TTs Checked in Q2. Records attached | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154989 | Closed | SUNITA | 2026-10-12 | TT Checking is lacking behind target. | 3.1 | TT fittings & discipline checked | 1554 | MR-II TERMINAL | Operations officers need to fully enagage in the same | SOD | Marketing | WZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154989 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154989 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154989 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154989 | AUD-2026-09-2000017375ACN-2026-09-4000154989 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-09-29 | HCD audio Visual hooters of Baliga make Ex tpye oter procured and installed. Procurement document attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154990 | Closed | SUNITA | 2026-09-29 | Audio Visual alarms not availbale in field for HCD | 3.12 | Critical alarms checked & corrective actions reviewed | 1554 | MR-II TERMINAL | Field Audio Visula alarms needed for HCD | SOD | Marketing | WZ | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017375ACN-2026-09-4000154990 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154990 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154990 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154990 | AUD-2026-09-2000017375ACN-2026-09-4000154990 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | Compliances are in progress. More than 50% points are already closed. Open points 30 nos. 30.09.2026. Compliance will be done by 31.10.2026 | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146660 | Closed | SUNITA | 2026-10-12 | MDSA conducted in March 2026. Location to expedite compliances | 3.18 | OISD/MDSA/SSA compliance reviewed | 1554 | MR-II TERMINAL | More than 60 points pending compliance | SOD | Marketing | WZ | 2026-10-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-10-31 | AUD-2026-07-2000016409ACN-2026-07-4000146660 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146660 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146660 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146660 | AUD-2026-07-2000016409ACN-2026-07-4000146660 | 21 | 21 | 27 | 80 | 6 | 5 | 61 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-09-29 | Compliance in progress. More than 50% points complied. Satus report as of 26.09.2026 attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000154992 | Closed | SUNITA | 2026-09-29 | MDSA conducted in March 2026. More than 50 points pending compliance | 3.18 | OISD/MDSA/SSA compliance reviewed | 1554 | MR-II TERMINAL | .Location to expedite compliances | SOD | Marketing | WZ | 2026-10-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017375ACN-2026-09-4000154992 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154992 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154992 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154992 | AUD-2026-09-2000017375ACN-2026-09-4000154992 | 21 | 21 | 27 | 80 | 6 | 5 | 61 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | 100% TTs are checked as majority TT are Ex MI and Same are found under calibrated. Having a Calibration tower inside terminal will add to comlications like additional, manpower, W&M liasoning, officer for W&M person. Accordingly, facility is not made operational. Communication from Operations team attached. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146655 | Closed | SHINDE ANAND LAXMAN | 2026-10-15 | YES 100% for Volume based TTs as TT are found under calibrated. It is causing lot man hour losses and non effective use of TAS | 3.2 | Post-loading dip checks verified | 1554 | MR-II TERMINAL | Location to develop facility for cross verification of TT Calibration | SOD | Marketing | WZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146655 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146655 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146655 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146655 | AUD-2026-07-2000016409ACN-2026-07-4000146655 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-10-12 | 100% TTs are checked as majority TT are Ex MI and Same are found under calibrated. HAving a Calibration tower inside terminal will add to comlications like additional, manpower, W&M liasoning, officer for W&M person. Accordingly, facility is not made operational. Communication from Operations team attached. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126318 | Closed | SUNITA | 2026-10-12 | YES 100% for Volume based TTs as TT are found under calibrated. It is causing lot man hour losses and non effective use of TAS | 3.2 | Post-loading dip checks verified | 1554 | MR-II TERMINAL | Location to develop facility for cross verification of TT Calibration | SOD | Marketing | WZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 2 | ASSET INTEGRITY | S1 | F2 | 2026-09-30 | AUD-2026-04-2000011147ACN-2026-04-4000126318 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126318 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126318 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126318 | AUD-2026-04-2000011147ACN-2026-04-4000126318 | 21 | 21 | 26 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-15 | SUNITA | 2026-09-24 | Tender for supply to Kochi and Ram Nagar is no longer available. Hence MOC is not needed. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126319 | Closed | SUNITA | 2026-09-24 | YES, Location has issued letters. Night driving regular for Kochi terminal and Ram Nagar Lubes | 3.3 | VTS deviations reviewed | 1554 | MR-II TERMINAL | Location to take MOC approval or modify routes for these two locations | SOD | Marketing | WZ | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 2 | OCCUPATIONAL HEALTH | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126319 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126319 | 2026-10-16 | 3.7538 | 409 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126319 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126319 | AUD-2026-04-2000011147ACN-2026-04-4000126319 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 59
|  | DIGRA SUNIL KUMAR | 2026-10-15 | Housekeepig of our ware house has been planeed wth segregation of scrp material and removal of scrap material to builda common accumulation of the same for initiating the scrap RFD prposal to clear the junk. Further clearing of old documents and records also planned. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152014 | Completed | DIGRA SUNIL KUMAR | 2026-09-29 | Housekeeping to be improved. | 3.15 | Housekeeping & PPE usage checked | 1256 | JAMMU DEPOT | Location advised to improve overall housekeeping. | SOD | Marketing | NFZ | 2026-09-15 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-15 | AUD-2026-09-2000017601ACN-2026-09-4000152014 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152014 | 2026-09-04 | 45.7538 | 379 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152014 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017601ACN-2026-09-4000152014 |  | AUD-2026-09-2000017601ACN-2026-09-4000152014 | 21 |  | 27 | 80 | 1 | -4 | 55
|  | DIGRA SUNIL KUMAR | 2026-10-15 | The Segregation of the material is being done and shodrtly RFD initiation would be done along with valuation of the same. | LOCATION VISIT-JAMMU_02-04.09.26 | 2026-09-04 | AUD-2026-09-2000017601 | 2026-09-02 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152015 | Completed | DIGRA SUNIL KUMAR | 2026-09-29 | Scrap observed at Location pending for disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1256 | JAMMU DEPOT | Location advised to process RFD and expedite disposal. | SOD | Marketing | NFZ | 2026-09-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017601ACN-2026-09-4000152015 | JK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017601ACN-2026-09-4000152015 | 2026-09-04 | 45.7538 | 394 | >20 | AUD-2026-09-2000017601 - ACN-2026-09-4000152015 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017601ACN-2026-09-4000152015 |  | AUD-2026-09-2000017601ACN-2026-09-4000152015 | 21 |  | 27 | 80 | 1 | -4 | 57
KATAKAM SRINIVAS | 2026-10-15 | BAGADE AMAR ARUN | 2026-10-15 | Tender for the modification in the pipeline has been floated and under technical evaluation. | ZONAL VISIT REPORT 19.02.26 AKOLA IRD | 2026-02-20 | AUD-2026-03-2000011118 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122487 | Closed | BAGADE AMAR ARUN | 2026-10-15 | Requirement-14 KL Total Qty as on date -14.2 KL. The strainer installed in the 1 KL foam tank is located in a constrained position, making cleaning and maintenance difficult. | 2.9 | Foam inventory verified | 1485 | AKOLA DEPOT | Strainer on foam line for 1 KL Foam bladder Tank near Fire Engine Shed to be repositioned | SOD | Marketing | WZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011118ACN-2026-03-4000122487 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011118ACN-2026-03-4000122487 | 2026-08-24 | 56.7538 | 409 | >20 | AUD-2026-03-2000011118 - ACN-2026-03-4000122487 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011118ACN-2026-03-4000122487 | AUD-2026-03-2000011118ACN-2026-03-4000122487 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 59
KATAKAM SRINIVAS | 2026-10-15 | BAGADE AMAR ARUN | 2026-10-15 | Bag checking facility has been provided adjacent to DFMD so that bag checking and metal detection can be check simultaneously by security. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000146514 | Closed | BAGADE AMAR ARUN | 2026-10-15 | Location has 3 turnstiles for access control system and are working. Bags are checked before DFMD. To make arrangement for checking the bags after DFMD. Also to check the funcationality of Multispot functioning of DFMD. Also women security check arrangements aremade after C back | 2.8 | Access control systems checked | 1485 | AKOLA DEPOT | To make arrangement for checking the bags after DFMD To have the facility of women sercurty check before C Back | SOD | Marketing | WZ | 2026-07-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-07-31 | AUD-2026-06-2000013155ACN-2026-07-4000146514 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146514 | 2026-08-24 | 56.7538 | 409 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146514 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013155ACN-2026-07-4000146514 | AUD-2026-06-2000013155ACN-2026-07-4000146514 | 21 | 21 | 27 | 80 | 3 | 3 | 48 | 59
KATAKAM SRINIVAS | 2026-10-15 | BAGADE AMAR ARUN | 2026-10-15 | Repetitive point of Audit AUD-2026-09-2000017374 with Part Code 3.18. | ZONAL VIST AKOLA IRD 02.06.2026 | 2026-06-02 | AUD-2026-06-2000013155 | 2026-06-02 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000146517 | Closed | BAGADE AMAR ARUN | 2026-10-15 | OISD 2022-23 Total points-20 Complied-20 MDSA 2025-26 Total points-33 Complied-21 SSA 2025-26 Total points-32 Complied-28 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1485 | AKOLA DEPOT | Location to comply the points in time bound manner | SOD | Marketing | WZ | 2026-09-30 | INADEQUATE SAFETY CULTURE | 9 | PROCESS SAFETY | S3 | F3 | 2026-09-30 | AUD-2026-06-2000013155ACN-2026-07-4000146517 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013155ACN-2026-07-4000146517 | 2026-08-24 | 56.7538 | 409 | >20 | AUD-2026-06-2000013155 - ACN-2026-07-4000146517 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013155ACN-2026-07-4000146517 | AUD-2026-06-2000013155ACN-2026-07-4000146517 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 59
KATAKAM SRINIVAS | 2026-10-15 | BAGADE AMAR ARUN | 2026-10-15 | Information boards regarding height and capacity are replaced. | AKOLA LOCATION VISIT 24.08.2026 | 2026-08-24 | AUD-2026-09-2000017374 | 2026-08-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154980 | Closed | BAGADE AMAR ARUN | 2026-10-15 | Information board regarding tank details is damaged. Need to be replaced. | 6.1 | Informational Boards/Signs | 1485 | AKOLA DEPOT | Location to take necessary action. | SOD | Marketing | WZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-30 | AUD-2026-09-2000017374ACN-2026-09-4000154980 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017374ACN-2026-09-4000154980 | 2026-08-24 | 56.7538 | 409 | >20 | AUD-2026-09-2000017374 - ACN-2026-09-4000154980 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017374ACN-2026-09-4000154980 | AUD-2026-09-2000017374ACN-2026-09-4000154980 | 21 | 21 | 27 | 80 | 3 | 3 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-16 | SUNITA | 2026-10-12 | Issue is taken up with Mumbai refinery HR security team and CISF. Communication trail attached. | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000126328 | Closed | SUNITA | 2026-10-12 | CISF operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 6.1 | CISF operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 1554 | MR-II TERMINAL | Location to take with MR Security head | SOD | Marketing | WZ | 2026-04-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 2 | ASSET INTEGRITY | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126328 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126328 | 2026-10-16 | 3.7538 | 410 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126328 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011147ACN-2026-04-4000126328 | AUD-2026-04-2000011147ACN-2026-04-4000126328 | 21 | 21 | 26 | 80 | 6 | 5 | 35 | 59
SHINDE ANAND LAXMAN | 2026-10-16 | SUNITA | 2026-10-12 | Issue is taken up with Mumbai refinery HR security team and CISF. Communication trail attached. | MR 2 VISIT 29.06.2026 | 2026-06-29 | AUD-2026-07-2000016409 | 2026-06-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000146665 | Closed | SUNITA | 2026-10-12 | CISF operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 6.1 | CISF still operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 1554 | MR-II TERMINAL | Location to take with MR Security head | SOD | Marketing | WZ | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-07-2000016409ACN-2026-07-4000146665 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016409ACN-2026-07-4000146665 | 2026-10-16 | 3.7538 | 410 | >20 | AUD-2026-07-2000016409 - ACN-2026-07-4000146665 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000016409ACN-2026-07-4000146665 | AUD-2026-07-2000016409ACN-2026-07-4000146665 | 21 | 21 | 27 | 80 | 6 | 5 | 57 | 59
SHINDE ANAND LAXMAN | 2026-10-16 | SUNITA | 2026-09-29 | Follow up is maintained with Mumbai Refinery security incharge shri Amod Mahajan . Latest communication dt 29.09.2026 attached. | LOCATION VISIT MR2 21.07.2026 | 2026-07-21 | AUD-2026-09-2000017375 | 2026-07-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000154994 | Closed | SUNITA | 2026-09-29 | CISF operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 6.1 | CISF still operates only one gate at a time. This leads to pile of TTs inside the terminal which is safety threat | 1554 | MR-II TERMINAL | Location to maintain follow up with Head HR Security for CISF related issues such as night patroling, outside patroling, Lady guard, vehile parking outside emergency gate and Both B and C gate operations etc. | SOD | Marketing | WZ | 2026-11-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-11-30 | AUD-2026-09-2000017375ACN-2026-09-4000154994 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017375ACN-2026-09-4000154994 | 2026-10-16 | 3.7538 | 410 | >20 | AUD-2026-09-2000017375 - ACN-2026-09-4000154994 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017375ACN-2026-09-4000154994 | AUD-2026-09-2000017375ACN-2026-09-4000154994 | 21 | 21 | 27 | 80 | 6 | 5 | 65 | 59
KAPIL DEV | 2026-10-16 | PANWAR JITENDRA SINGH | 2026-10-14 | online density has been recorded in SAP | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155047 | Closed | PANWAR JITENDRA SINGH | 2026-10-14 | Online density to be recorded in SAP as per SOP. | 6.13 |  | 1410 | VADODARA TERMINAL | Corrective action shall be taken | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155047 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155047 | 2026-09-10 21:00 | 38.8788 | 410 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155047 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155047 | AUD-2026-09-2000017759ACN-2026-09-4000155047 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
KAPIL DEV | 2026-10-16 | PANWAR JITENDRA SINGH | 2026-10-16 | issue of police verification of driver has been resolved & TT is being reporting & getting filled on regular basis | SR MANAGEMENT INSP OF VADODARA Q2 26-27 | 2026-09-10 21:00 | AUD-2026-09-2000017759 | 2026-09-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000155100 | Closed | PANWAR JITENDRA SINGH | 2026-10-16 | Records have been checked for TTs that are not reporting. The location has provided reasons for the non‑reporting TTs. Action is required for TT No. GJ06BY1706, which has a police verification issue. | 6.16 |  | 1410 | VADODARA TERMINAL | Location to initiate action as per ITDG for non-reporting TT No GJ06BY1706 and submit action taken report. | SOD | Marketing | NWR | 2026-10-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-09-2000017759ACN-2026-09-4000155100 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017759ACN-2026-09-4000155100 | 2026-09-10 21:00 | 38.8788 | 410 | >20 | AUD-2026-09-2000017759 - ACN-2026-09-4000155100 | 532 | 8294 | 21 | 8294 | -10 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017759ACN-2026-09-4000155100 | AUD-2026-09-2000017759ACN-2026-09-4000155100 | 21 | 21 | 27 | 80 | 0 | -26 | 61 | 59
[5 empty] | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000133473 | Open |  |  | Physical dip has been checked for TK P5 and Tank D1. Tank P5 - Physical dip of 270.9 cms against TAS dip of 271.0 cms . Water physical dip observed 4.3 cms against TAS dip of 3.3 cms Variation : 10 mm. Tank D1 - Physical dip of 577.8 cms against TAS dip of 577.9 cms . Water physical dip observed 0.0 cms against TAS dip of 0.0 cms Variation : nil. Tank D1 Physical density 823.0 against TAS tank density of 808.5 , variation of 15.5 is observed. | 3.7 | Inventory physical dip of minimum two tanks taken | 1915 | RAMAGUNDAM DEPOT | Location to take up with TAS vendor and ensure that variations in water dip remain with in tolerance limit of 5 mm and density variation within tolerance limit. | SOD | Marketing | SCR | 2026-06-10 |  | 5 |  | S1 | F5 | 2026-06-10 | AUD-2026-06-2000012788ACN-2026-06-4000133473 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133473 | 2026-08-26 18:00 | 54.0038 | 282 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133473 | 532 | 8294 | 21 | 8294 | 131 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012788ACN-2026-06-4000133473 |  | AUD-2026-06-2000012788ACN-2026-06-4000133473 | 21 |  | 27 | 80 | 2 | 2 | 41
[5 empty] | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133476 | Open |  |  | Emergency gate EGMS Key hooter not working | 6.1 |  | 1915 | RAMAGUNDAM DEPOT | Emergency gate EGMS Key hooter to be rectified | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012788ACN-2026-06-4000133476 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133476 | 2026-08-26 18:00 | 54.0038 | 302 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133476 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012788ACN-2026-06-4000133476 |  | AUD-2026-06-2000012788ACN-2026-06-4000133476 | 21 |  | 27 | 80 | 2 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000133479 | Open |  |  | Solar generation for 39 KW plant is only 75% | 6.4 |  | 1915 | RAMAGUNDAM DEPOT | Solar generation for 39 KW plant is only 75% , to be analysed with help of consultant | SOD | Marketing | SCR | 2026-05-31 |  | 5 |  | S1 | F5 | 2026-05-31 | AUD-2026-06-2000012788ACN-2026-06-4000133479 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133479 | 2026-08-26 18:00 | 54.0038 | 272 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133479 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-06-2000012788ACN-2026-06-4000133479 |  | AUD-2026-06-2000012788ACN-2026-06-4000133479 | 21 |  | 27 | 80 | 2 | 2 | 39
|  | KUMAR MANISH | 2026-10-16 | E File Note 133716 has been submitted for the Dip Elimination. Complied. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130051 | Completed | KUMAR MANISH | 2026-10-16 | Yes, Location is advised to expedite approval for Dip Elimanation sustenance and TFMS-SAP sustenance. | 1.6 | Expectations clearly communicated to officers | 1424 | JABALPUR DEPOT | Location to give Target date for submission of EFN for Dip Elimination sustenance and TFMS-SAP sustenance. | SOD | Marketing | CEN | 2026-06-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012101ACN-2026-05-4000130051 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130051 | 2026-09-26 17:30 | 23.0247 | 302 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130051 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012101ACN-2026-05-4000130051 |  | AUD-2026-05-2000012101ACN-2026-05-4000130051 | 21 |  | 27 | 80 | 0 | 0 | 44
|  | KUMAR MANISH | 2026-10-16 | Location has made the ATR for the Complinace of the MDSA point , currently 25 Points complied , and point alos considered in the next audit hence close as per advice from zone. | LOCATION VISIT AT JABALPUR IRD | 2026-05-09 19:00 | AUD-2026-05-2000012101 | 2026-05-08 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130054 | Completed | KUMAR MANISH | 2026-10-16 | Nil OISD and SSA points are open. Comprehensive MDSA was carried out in Dec' 2025, wherein out of 40 points, 15 points are compliedand 25 are still open. Targeted to complete it by Dec' 2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1424 | JABALPUR DEPOT | Location to expedite closure of remaining 25 open points in time bound manner. | SOD | Marketing | CEN | 2026-12-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-12-31 | AUD-2026-05-2000012101ACN-2026-05-4000130054 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012101ACN-2026-05-4000130054 | 2026-09-26 17:30 | 23.0247 | 486 | >20 | AUD-2026-05-2000012101 - ACN-2026-05-4000130054 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012101ACN-2026-05-4000130054 |  | AUD-2026-05-2000012101ACN-2026-05-4000130054 | 21 |  | 27 | 80 | 0 | 0 | 70
|  | KUMAR MANISH | 2026-10-16 | EFN no 133716 Submitted for Dip Elimination. Complied. | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000154042 | Completed | KUMAR MANISH | 2026-10-16 | Yes, Location is advised to expedite approval for Dip Elimanation sustenance and TFMS-SAP sustenance. | 1.6 | Expectations clearly communicated to officers | 1424 | JABALPUR DEPOT | Location to give Target date for submission of EFN for Dip Elimination sustenance and TFMS-SAP sustenance. | SOD | Marketing | CEN | 2026-11-15 | INSUFFICIENT SUPERVISION | 2 | PROCESS SAFETY | S1 | F2 | 2026-11-15 | AUD-2026-09-2000017560ACN-2026-09-4000154042 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154042 | 2026-09-26 17:30 | 23.0247 | 440 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154042 | 532 | 8294 | 21 | 8294 | -26 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154042 |  | AUD-2026-09-2000017560ACN-2026-09-4000154042 | 21 |  | 27 | 80 | 0 | 0 | 63
|  | KUMAR MANISH | 2026-10-16 | Security Cabin camera repaired and is now functional.- Complied. | LOCATION VISIT AT JABALPUR IRD | 2026-09-26 17:30 | AUD-2026-09-2000017560 | 2026-09-25 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000154044 | Completed | KUMAR MANISH | 2026-10-16 | Out of 71 CCTV, 01 camera is down (Near Security Cabin). Further, recording is available for 90 days. Recording verified randomly at various location. Recording of Security cabin is also not available for random dates in the month of June, July and August 2026. | 2.6 | CCTV functioning checked | 1424 | JABALPUR DEPOT | Location to get reapired Security Cabin camera at the earliest and ensure functionality of the same. The recordings of Security cabin to be checked for the mentioned period. | SOD | Marketing | CEN | 2026-10-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-31 | AUD-2026-09-2000017560ACN-2026-09-4000154044 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017560ACN-2026-09-4000154044 | 2026-09-26 17:30 | 23.0247 | 425 | >20 | AUD-2026-09-2000017560 - ACN-2026-09-4000154044 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017560ACN-2026-09-4000154044 |  | AUD-2026-09-2000017560ACN-2026-09-4000154044 | 21 |  | 27 | 80 | 0 | 0 | 61
|  |  |  | Repeat observation. Hence closing this as this an earlier audit observation is open. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151550 | Open | KESHETTI SAI MANISH | 2026-10-16 | Emphasis on Timely response, Safety, Samriddhi 2.0,Scrap disposal, Surprise TT inspections, Stock loss analysis, Solar Generation and Electricity consumption , Innovation using AI , Timely completion of Projects. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1915 | RAMAGUNDAM DEPOT | Additional Projects identification and to be taken in samriddhi 2.0 in addition to the current one. | SOD | Marketing | SCR | 2026-11-30 |  | 9 |  | S3 | F3 | 2026-11-30 | AUD-2026-09-2000017500ACN-2026-09-4000151550 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151550 | 2026-08-26 18:00 | 54.0038 | 455 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151550 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017500ACN-2026-09-4000151550 |  | AUD-2026-09-2000017500ACN-2026-09-4000151550 | 21 |  | 27 | 80 | 2 | 2 | 65
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-09-4000151551 | Open |  |  | Reviewed all the points as per the BCM - Samriddhi, EBMS QC checkings,Stock loss analysis, Operational Activites,Outage plan, TAS Reports, Transportation , VTS , Audit Status, Projects status. | 1.2 | Performance review conducted | 1915 | RAMAGUNDAM DEPOT | Detailed analysis on Stock Loss to be done and coordinate with VJTL and plan to achieve target. | SOD | Marketing | SCR | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017500ACN-2026-09-4000151551 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151551 | 2026-08-26 18:00 | 54.0038 | 425 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151551 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017500ACN-2026-09-4000151551 |  | AUD-2026-09-2000017500ACN-2026-09-4000151551 | 21 |  | 27 | 80 | 2 | 2 | 61
|  |  |  | Sprinkler cleaning carried out in Sep 2026 | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151554 | Open | KESHETTI SAI MANISH | 2026-10-16 | HVLR - 03 & MEFG near TkK4 and Sprinklers operated. Some sprinklers were found to be choked. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1915 | RAMAGUNDAM DEPOT | Blockage of sprinklers to be cleared | SOD | Marketing | SCR | 2026-09-10 |  | 5 |  | S1 | F5 | 2026-09-10 | AUD-2026-09-2000017500ACN-2026-09-4000151554 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151554 | 2026-08-26 18:00 | 54.0038 | 374 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151554 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151554 |  | AUD-2026-09-2000017500ACN-2026-09-4000151554 | 21 |  | 27 | 80 | 2 | 2 | 54
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151555 | Open |  |  | Spill kit for TG22T1025 found to be missing | 2.15 | TT crew roadside emergency procedures checked | 1915 | RAMAGUNDAM DEPOT | Leak control kit/spill kit to made available with the TT | SOD | Marketing | SCR | 2026-10-31 |  | 9 |  | S3 | F3 | 2026-10-31 | AUD-2026-09-2000017500ACN-2026-09-4000151555 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151555 | 2026-08-26 18:00 | 54.0038 | 425 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151555 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017500ACN-2026-09-4000151555 |  | AUD-2026-09-2000017500ACN-2026-09-4000151555 | 21 |  | 27 | 80 | 2 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151556 | Open |  |  | There is a reduction in VTS deviations. But stoppage violations increased. | 3.3 | VTS deviations reviewed | 1915 | RAMAGUNDAM DEPOT | Location to take up with Direct Sales for resolution | SOD | Marketing | SCR | 2026-09-30 |  | 6 |  | S2 | F3 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151556 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151556 | 2026-08-26 18:00 | 54.0038 | 394 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151556 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017500ACN-2026-09-4000151556 |  | AUD-2026-09-2000017500ACN-2026-09-4000151556 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151557 | Open |  |  | Tank : TkD2 Product : HSD TAS dip : 9302 mm Physical dip : 9309 mm Temperature @ TAS : 30.1 deg C Temperature actual : 31.5 deg C Density @ TAS : 816 Kg/m3 Density actual : 818.7 Kg/m3 Tank : TkK4 Product : MS TAS dip : 2919 mm Physical dip : 2923 mm Water dip Actual : 0 mm Water dip @ TAS : 1.6 mm Temperature @ TAS : 29.6 deg C Temperature actual : 31 deg C Density TAS : 742.7 Kg/m3 Density actual : 735 Kg/m3 | 3.7 | Inventory physical dip of minimum two tanks taken | 1915 | RAMAGUNDAM DEPOT | Location to take up with TAS vendor and ensure that variations remain with in tolerance limit. | SOD | Marketing | SCR | 2026-09-30 |  | 4 |  | S4 | F1 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151557 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151557 | 2026-08-26 18:00 | 54.0038 | 394 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151557 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151557 |  | AUD-2026-09-2000017500ACN-2026-09-4000151557 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151558 | Open |  |  | Reviewed the MFM vs BCU reports, LP-05 is currently offline, remaining bays are in working condition. | 3.11 | MFM vs BCU totalizer comparison checked | 1915 | RAMAGUNDAM DEPOT | LP-05 functionality to be restored. | SOD | Marketing | SCR | 2026-10-31 |  | 4 |  | S2 | F2 | 2026-10-31 | AUD-2026-09-2000017500ACN-2026-09-4000151558 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151558 | 2026-08-26 18:00 | 54.0038 | 425 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151558 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151558 |  | AUD-2026-09-2000017500ACN-2026-09-4000151558 | 21 |  | 27 | 80 | 2 | 2 | 61
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151561 | Open |  |  | Yes. The ongoing NPCB projects are reviewed & advised location complete the jobs within target dates for TT new exit gate balance projects. | 4.4 | Quality of PM compliance reviewed | 1915 | RAMAGUNDAM DEPOT | Completion of NPCB projects within timelines | SOD | Marketing | SCR | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151561 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151561 | 2026-08-26 18:00 | 54.0038 | 394 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151561 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151561 |  | AUD-2026-09-2000017500ACN-2026-09-4000151561 | 21 |  | 27 | 80 | 2 | 2 | 57
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000151562 | Open |  |  | Scrap last disposed in Feb 2026. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1915 | RAMAGUNDAM DEPOT | Scrap generated in FY 26-27 to be disposed | SOD | Marketing | SCR | 2026-12-31 |  | 3 |  | S3 | F1 | 2026-12-31 | AUD-2026-09-2000017500ACN-2026-09-4000151562 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151562 | 2026-08-26 18:00 | 54.0038 | 486 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151562 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151562 |  | AUD-2026-09-2000017500ACN-2026-09-4000151562 | 21 |  | 27 | 80 | 2 | 2 | 70
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151565 | Open |  |  | Water Drain Pipe allignment not proper in HSD Tank D2 | 6.3 |  | 1915 | RAMAGUNDAM DEPOT | Water Drain Pipe allignment to be corrected in HSD Tank D2 | SOD | Marketing | SCR | 2026-09-15 |  | 1 |  | S1 | F1 | 2026-09-15 | AUD-2026-09-2000017500ACN-2026-09-4000151565 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151565 | 2026-08-26 18:00 | 54.0038 | 379 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151565 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151565 |  | AUD-2026-09-2000017500ACN-2026-09-4000151565 | 21 |  | 27 | 80 | 2 | 2 | 55
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151566 | Open |  |  | Paint Removed and Rusting in joint of Roof Plate of Tk TKP 4 | 6.4 |  | 1915 | RAMAGUNDAM DEPOT | Rust to be removed and Paint to be applied in the affected area | SOD | Marketing | SCR | 2026-09-10 |  | 4 |  | S4 | F1 | 2026-09-10 | AUD-2026-09-2000017500ACN-2026-09-4000151566 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151566 | 2026-08-26 18:00 | 54.0038 | 374 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151566 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017500ACN-2026-09-4000151566 |  | AUD-2026-09-2000017500ACN-2026-09-4000151566 | 21 |  | 27 | 80 | 2 | 2 | 54
[5 empty] | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151571 | Open |  |  | Provision of LLOP, Overspeeding, High Temperature simulation not available in FEs | 6.9 |  | 1915 | RAMAGUNDAM DEPOT | Provision of LLOP, Overspeeding, High Temperature simulation to be provided in FEs | SOD | Marketing | SCR | 2026-09-07 |  | 6 |  | S2 | F3 | 2026-09-07 | AUD-2026-09-2000017500ACN-2026-09-4000151571 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151571 | 2026-08-26 18:00 | 54.0038 | 371 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151571 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-09-2000017500ACN-2026-09-4000151571 |  | AUD-2026-09-2000017500ACN-2026-09-4000151571 | 21 |  | 27 | 80 | 2 | 2 | 53
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | VTS deviations have come down. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123043 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Interacted with all 5 officer at location. Their respective roles and responsibilities, performance, and expectations were discussed | 1.1 | Interaction with all officers (1–1.5 hrs) | 1915 | RAMAGUNDAM DEPOT | Officers to immediately act on flagged issues in operational control center. VTS deviations in I&C customer routes to be completetly eliminated. | SOD | Marketing | SCR | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | EMERGENCY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000010863ACN-2026-03-4000123043 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123043 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123043 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123043 | AUD-2026-03-2000010863ACN-2026-03-4000123043 | 21 | 21 | 26 | 80 | 2 | 2 | 26 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | 3 NPCB projects completed this year. Separate TT entry and exit project is likely to be completed by 31-12-2026 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123044 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Respective roles and responsibilities, performance, and expectations were discussed. A comprehensive review was carried out covering adherence to systems and SOPs, inspection of tank trucks, EM lock integrity, overall terminal preparedness | 1.2 | Performance review conducted | 1915 | RAMAGUNDAM DEPOT | NPCB projects particularly TT exit-Entry gate is lagging. Location to focus on completing NPCB projects in given timelines. | SOD | Marketing | SCR | 2026-05-30 | THIRD PARTY ERRORS | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-30 | AUD-2026-03-2000010863ACN-2026-03-4000123044 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123044 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123044 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123044 | AUD-2026-03-2000010863ACN-2026-03-4000123044 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Currently open. As it is a repeat observation in another inspection, closing this one. | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123045 | Closed | KESHETTI SAI MANISH | 2026-10-16 | bottom loading facility commisioned. Top loading trucks to be converted | 1.3 | Pending issues reviewed | 1915 | RAMAGUNDAM DEPOT | Balance Top loading trucks to be converted to bottom loading in timebound manner | SOD | Marketing | SCR | 2026-05-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-05-30 | AUD-2026-03-2000010863ACN-2026-03-4000123045 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123045 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123045 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123045 | AUD-2026-03-2000010863ACN-2026-03-4000123045 | 21 | 21 | 26 | 80 | 2 | 2 | 39 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | All audit observations completed for MDSA & SSA of FY 2025-26 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123046 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Recent review recommendations were reviewed along with pending audit points of SSA & MDSA | 1.4 | Earlier action points status checked | 1915 | RAMAGUNDAM DEPOT | Review of MDSA & SSA with action required | SOD | Marketing | SCR | 2026-03-31 | THIRD PARTY ERRORS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010863ACN-2026-03-4000123046 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123046 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123046 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123046 | AUD-2026-03-2000010863ACN-2026-03-4000123046 | 21 | 21 | 26 | 80 | 2 | 2 | 31 | 59
SINGWAL DEEPAK | 2026-10-16 | YASH SHARMA | 2026-10-16 | Light fixtures are provided in MCC room to meet the desired lux level as per norms. | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149439 | Closed | YASH SHARMA | 2026-10-16 | Lux level checked at TT Gantry, MCC Room, Control Room, Admin Bldg, Foam shed etc. Lux level was inadequate at MCC room. Additionallight fixtures are required to be provided in MCC room | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1435 | GWALIOR DEPOT | Light fixtures are required to be provided in MCC room to meet the desired lux level as per norms. | SOD | Marketing | CEN | 2026-09-15 | POOR PLANNING OR RISK ASSESSMENT | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-09-15 | AUD-2026-08-2000017055ACN-2026-08-4000149439 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149439 | 2026-08-22 19:00 | 57.9622 | 410 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149439 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017055ACN-2026-08-4000149439 | AUD-2026-08-2000017055ACN-2026-08-4000149439 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 59
SINGWAL DEEPAK | 2026-10-16 | YASH SHARMA | 2026-10-16 | Licenece Key to be taken from Sagar Depot to integration TAS SCDA with Safety PLC and activate the safety provision. | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000149440 | Closed | YASH SHARMA | 2026-10-16 | Gantry permissive checked by putting 2 Fire Engines in Local mode. | 2.5 | Emergency response preparedness reviewed | 1435 | GWALIOR DEPOT | The Gantry permissive failed to stopped TT loading operation. Location to take up with TAS vendor for rectification of the same on top priority. | SOD | Marketing | CEN | 2026-08-26 | THIRD PARTY ERRORS | 15 | PROCESS SAFETY | S3 | F5 | 2026-08-26 | AUD-2026-08-2000017055ACN-2026-08-4000149440 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149440 | 2026-08-22 19:00 | 57.9622 | 410 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149440 | 532 | 8294 | 21 | 8294 | 54 | 60 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017055ACN-2026-08-4000149440 | AUD-2026-08-2000017055ACN-2026-08-4000149440 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 59
SINGWAL DEEPAK | 2026-10-16 | YASH SHARMA | 2026-10-16 | Earthpit shall be reconditioned and re-checked will be done. | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149445 | Closed | YASH SHARMA | 2026-10-16 | Earth pit checked for VCB | 3.16 | Earth pits / boundary / vegetation control checked | 1435 | GWALIOR DEPOT | Resistance observed beyond permissible limit. Location to check and get it rectified. Also, the Earth pit due date to be amended for most of the earth pits. | SOD | Marketing | CEN | 2026-09-15 | POOR EQUIPMENT MAINTENANCE | 8 | ASSET INTEGRITY | S2 | F4 | 2026-09-15 | AUD-2026-08-2000017055ACN-2026-08-4000149445 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149445 | 2026-08-22 19:00 | 57.9622 | 410 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149445 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017055ACN-2026-08-4000149445 | AUD-2026-08-2000017055ACN-2026-08-4000149445 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 59
SINGWAL DEEPAK | 2026-10-16 | YASH SHARMA | 2026-10-16 | Toll updation for revised route of 2 Retail Outlets to be incorporated thru SO. | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000149446 | Closed | YASH SHARMA | 2026-10-16 | Had meeting with Transporters at location to understand their issues, if any. During interaction various topic related to TT planning, TT violations, ITDG guidelines were discussed and addressed to the satisfaction. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1435 | GWALIOR DEPOT | Toll updation for revised route of 2 Retail Outlets to be incorporated thru SO. | SOD | Marketing | CEN | 2026-09-15 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-15 | AUD-2026-08-2000017055ACN-2026-08-4000149446 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149446 | 2026-08-22 19:00 | 57.9622 | 410 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149446 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000017055ACN-2026-08-4000149446 | AUD-2026-08-2000017055ACN-2026-08-4000149446 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 59
SINGWAL DEEPAK | 2026-10-16 | YASH SHARMA | 2026-10-16 |  | LOCATION VISIT AT GWALIOR IRD | 2026-08-22 19:00 | AUD-2026-08-2000017055 | 2026-08-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTINGCHECKED. SMOKE D | ACN-2026-08-4000149449 | Closed |  |  | Checked. Smoke Detector Hooter of Control Room found non-functional. | 5.2 | Functioning of all Hooters in control room | 1435 | GWALIOR DEPOT | Location to get it functional on priority | SOD | Marketing | CEN | 2026-08-26 | POOR EQUIPMENT MAINTENANCE | 15 | ASSET INTEGRITY | S3 | F5 | 2026-08-26 | AUD-2026-08-2000017055ACN-2026-08-4000149449 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000017055ACN-2026-08-4000149449 | 2026-08-22 19:00 | 57.9622 | 410 | >20 | AUD-2026-08-2000017055 - ACN-2026-08-4000149449 | 532 | 8294 | 21 | 8294 | 54 | 60 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000017055ACN-2026-08-4000149449 | AUD-2026-08-2000017055ACN-2026-08-4000149449 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | All audit observations completed for MDSA, SSA and TAS of FY 2025-26 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123707 | Closed | KESHETTI SAI MANISH | 2026-10-16 | MDSA, TAS , SSA compliances are revieved .Advised location to ensure 100 % compliance as per target date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1915 | RAMAGUNDAM DEPOT | 100% Compliance as per target dates | SOD | Marketing | SCR | 2026-09-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-03-2000010863ACN-2026-03-4000123707 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123707 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123707 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123707 | AUD-2026-03-2000010863ACN-2026-03-4000123707 | 21 | 21 | 26 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | 3 NPCB projects completed this year. Separate TT entry and exit project is likely to be completed by 31-12-2026 | AUDIT UPLOAD IN SAP | 2026-02-13 19:30 | AUD-2026-03-2000010863 | 2026-02-13 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123708 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Yes. NPCB projects are reviewed & advised location complete the jobs within timelines. | 4.3 | Project progress reviewed | 1915 | RAMAGUNDAM DEPOT | Completion of NPCB projects within timelines | SOD | Marketing | SCR | 2026-09-30 | INADEQUATE SAFETY CULTURE | 4 | PROCESS SAFETY | S1 | F4 | 2026-09-30 | AUD-2026-03-2000010863ACN-2026-03-4000123708 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010863ACN-2026-03-4000123708 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-03-2000010863 - ACN-2026-03-4000123708 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010863ACN-2026-03-4000123708 | AUD-2026-03-2000010863ACN-2026-03-4000123708 | 21 | 21 | 26 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | 3 NPCB projects completed this year. Separate TT entry and exit project is likely to be completed by 31-12-2026 | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000133465 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Respective roles and responsibilities, performance, and expectations were discussed. A comprehensive review was carried out covering adherence to systems and SOPs, inspection of tank trucks, EM lock integrity, overall terminal preparedness | 1.2 | Performance review conducted | 1915 | RAMAGUNDAM DEPOT | NPCB projects particularly TT exit-Entry gate to be expedited and completed by July 2026 . The Other ongoing projects of HCD , highmast lights and plug valves for siding to be completed by June 2026. | SOD | Marketing | SCR | 2026-07-30 | OUTDATED OR COMPLEX SOPS | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-30 | AUD-2026-06-2000012788ACN-2026-06-4000133465 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133465 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133465 | 532 | 8294 | 21 | 8294 | 81 | 90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133465 | AUD-2026-06-2000012788ACN-2026-06-4000133465 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Observation of previous inspection. Currently open. As it is a repeat observation, closing this one. | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000133466 | Closed | KESHETTI SAI MANISH | 2026-10-16 | bottom loading facility commisioned. Top loading trucks to be converted | 1.3 | Pending issues reviewed | 1915 | RAMAGUNDAM DEPOT | Balance Top loading trucks to be converted to bottom loading in timebound manner | SOD | Marketing | SCR | 2026-09-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012788ACN-2026-06-4000133466 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133466 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133466 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133466 | AUD-2026-06-2000012788ACN-2026-06-4000133466 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | All audit observations completed for MDSA, SSA and TAS of FY 2025-26 | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000133467 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Recent review recommendations were reviewed along with pending audit points of SSA & MDSA | 1.4 | Earlier action points status checked | 1915 | RAMAGUNDAM DEPOT | Pending audit points of SSA & MDSA to be completed by 30.09.2026 | SOD | Marketing | SCR | 2026-09-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012788ACN-2026-06-4000133467 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133467 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133467 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133467 | AUD-2026-06-2000012788ACN-2026-06-4000133467 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | All CCTV in working condition as of 1st week of Sep 2026 | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000133468 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Checked . 2 cameras are not working. One camera sent to OEM for repair and the other camera cable issue , nw Cable to be provided. | 2.6 | CCTV functioning checked | 1915 | RAMAGUNDAM DEPOT | Location to ensure the 2 nos CCTV put back into service on priority basis. | SOD | Marketing | SCR | 2026-06-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-06-2000012788ACN-2026-06-4000133468 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133468 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133468 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133468 | AUD-2026-06-2000012788ACN-2026-06-4000133468 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | 40 of 40 Cameras have been made active | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122836 | Closed | ROY TAVARES | 2026-10-16 | 32 Cameras out of 40 are active under VA, Balance Cameras are to be made active. | 2.7 | VA alerts checked / analysed | 1797 | GULBARGA NEW IRD | Balance 8 Cameras are to be made active. | SOD | Marketing | SWZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 12 | ASSET INTEGRITY | S3 | F4 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122836 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122836 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122836 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122836 | AUD-2026-03-2000010764ACN-2026-03-4000122836 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | Earlier pending points of Q4 2025-26 have been complied report maintained seperatly | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-06-4000138568 | Closed | ROY TAVARES | 2026-10-16 | 6 points pending out of 17 | 1.4 | Earlier action points status checked | 1797 | GULBARGA NEW IRD | Pending observations to be complied at the earliest | SOD | Marketing | SWZ | 2026-09-30 | INADEQUATE SAFETY CULTURE | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-30 | AUD-2026-06-2000013300ACN-2026-06-4000138568 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138568 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138568 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138568 | AUD-2026-06-2000013300ACN-2026-06-4000138568 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | All audit observations completed for MDSA, SSA and TAS of FY 2025-26 | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000133474 | Closed | KESHETTI SAI MANISH | 2026-10-16 | MDSA, TAS , SSA compliances are revieved .Advised location to ensure 100 % compliance as per target date. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1915 | RAMAGUNDAM DEPOT | 100% Compliance as per target dates | SOD | Marketing | SCR | 2026-09-30 | INADEQUATE SAFETY CULTURE | 5 | PROCESS SAFETY | S1 | F5 | 2026-09-30 | AUD-2026-06-2000012788ACN-2026-06-4000133474 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133474 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133474 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133474 | AUD-2026-06-2000012788ACN-2026-06-4000133474 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | 40 cameras have been functional in VA | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-06-4000138573 | Closed | ROY TAVARES | 2026-10-16 | 40 Cameras are active for VA out of which 37 are working. The VA are not working of 3 non-functional cameras. | 2.7 | VA alerts checked / analysed | 1797 | GULBARGA NEW IRD | The VA of 3 non-working cameras are to be made functional after correction of the cameras. | SOD | Marketing | SWZ | 2026-07-31 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S4 | F2 | 2026-07-31 | AUD-2026-06-2000013300ACN-2026-06-4000138573 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138573 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138573 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-06-2000013300ACN-2026-06-4000138573 | AUD-2026-06-2000013300ACN-2026-06-4000138573 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | 3 NPCB projects completed this year. Separate TT entry and exit project is likely to be completed by 31-12-2026 | AUDIT UPLOAD IN SAP | 2026-05-21 18:30 | AUD-2026-06-2000012788 | 2026-05-21 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-06-4000133475 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Yes. The 4 nos ongoing NPCB projects are reviewed & advised location complete the jobs within target dates i.e. July end for TT newexit gate and June end for the balance 3 projects. | 4.3 | Project progress reviewed | 1915 | RAMAGUNDAM DEPOT | Completion of NPCB projects within timelines | SOD | Marketing | SCR | 2026-07-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-07-31 | AUD-2026-06-2000012788ACN-2026-06-4000133475 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012788ACN-2026-06-4000133475 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-06-2000012788 - ACN-2026-06-4000133475 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012788ACN-2026-06-4000133475 | AUD-2026-06-2000012788ACN-2026-06-4000133475 | 21 | 21 | 27 | 80 | 2 | 2 | 48 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | EM Lock random verification with Intelligent keydone | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138577 | Closed | ROY TAVARES | 2026-10-16 | EM Lock SOP being maintained. Advised LIC to use intelligent key and records to be maintained | 3.5 | EM Lock SOP compliance verified | 1797 | GULBARGA NEW IRD | Advised LIC to use intelligent key and records to be maintained | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138577 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138577 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138577 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138577 | AUD-2026-06-2000013300ACN-2026-06-4000138577 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | ethanol TT dip rods verification is been done. Shortages are booked in applicable cases | GULBARGA_IRD_Q1_SR.MGNT_INSPECTION | 2026-05-21 18:00 | AUD-2026-06-2000013300 | 2026-05-21 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-06-4000138578 | Closed | ROY TAVARES | 2026-10-16 | Yes records maintained. However, Physical verification of ethanol TT dip rod to be done for each TT. There is abnormal variation between MFM reading and Tank dip levels. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1797 | GULBARGA NEW IRD | Location to cross verify ethanol TT dip rods and action to be taken for variation between MFM reading and tank dip levels | SOD | Marketing | SWZ | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-06-2000013300ACN-2026-06-4000138578 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000013300ACN-2026-06-4000138578 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-06-2000013300 - ACN-2026-06-4000138578 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000013300ACN-2026-06-4000138578 | AUD-2026-06-2000013300ACN-2026-06-4000138578 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | New electrical gloves and medicine procured. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000151552 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Mock drills are being conducted regularly and shortcomings are being disseminated to the teams. Emergency Trolley checked. Some items were not available and some were not found in the correct place. Emergency gloves date expired. Some medicines/ ointments date expired | 2.5 | Emergency response preparedness reviewed | 1915 | RAMAGUNDAM DEPOT | Missing Emergency items to be replaced and items to be put in correct place. New Electrical Gloves to be arranged. Expired medicines/ ointments to be replaced. | SOD | Marketing | SCR | 2026-09-07 | COMPLACENCY OR RISK NORMALIZATION | 5 | EMERGENCY | S1 | F5 | 2026-09-07 | AUD-2026-09-2000017500ACN-2026-09-4000151552 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151552 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151552 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151552 | AUD-2026-09-2000017500ACN-2026-09-4000151552 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Earth pit rectified. Currently earth pit readings are within limits. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000151559 | Closed | KESHETTI SAI MANISH | 2026-10-16 | EP 98: Individual - 1.16 Ohm Grid - 0.90 Ohm EP 53: Individual - 2.8 Ohm Grid - 0.52 Ohm | 3.16 | Earth pits / boundary / vegetation control checked | 1915 | RAMAGUNDAM DEPOT | Individual resistance value of EP 53 is greater than 2 Ohm, to be rectified. | SOD | Marketing | SCR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 3 | PROCESS SAFETY | S3 | F1 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151559 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151559 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151559 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151559 | AUD-2026-09-2000017500ACN-2026-09-4000151559 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Repeat observation. Hence closing this as this an earlier audit observation is open. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151563 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Emergency gate EGMS Key hooter not working | 6.1 |  | 1915 | RAMAGUNDAM DEPOT | Emergency gate EGMS Key hooter to be rectified | SOD | Marketing | SCR | 2026-09-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 3 | EMERGENCY | S3 | F1 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151563 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151563 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151563 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151563 | AUD-2026-09-2000017500ACN-2026-09-4000151563 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Repeat observation. Hence closing this as this an earlier audit observation is open. | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151564 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Solar generation for 39 KW plant is only 75% | 6.2 |  | 1915 | RAMAGUNDAM DEPOT | Solar generation for 39 KW plant is only 75% , to be analysed with help of consultant | SOD | Marketing | SCR | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | ENVIRONMENTAL | S2 | F4 | 2026-09-30 | AUD-2026-09-2000017500ACN-2026-09-4000151564 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151564 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151564 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017500ACN-2026-09-4000151564 | AUD-2026-09-2000017500ACN-2026-09-4000151564 | 21 | 21 | 27 | 80 | 2 | 2 | 57 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Name plates mentioned for pumps | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151569 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Sequence of Fire Engines not mentioned correctly | 6.7 |  | 1915 | RAMAGUNDAM DEPOT | Correct sequencing to be mentioned of all Fes | SOD | Marketing | SCR | 2026-08-27 | FAILURE TO FOLLOW PROCEDURES | 2 | PROCESS SAFETY | S2 | F1 | 2026-08-27 | AUD-2026-09-2000017500ACN-2026-09-4000151569 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151569 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151569 | 532 | 8294 | 21 | 8294 | 53 | 60 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151569 | AUD-2026-09-2000017500ACN-2026-09-4000151569 | 21 | 21 | 27 | 80 | 2 | 2 | 52 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Water leakage arrested during the pump AMC visit in Sep 2026 | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151570 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Water Leakage observed in Jockey 2 | 6.8 |  | 1915 | RAMAGUNDAM DEPOT | Water leakage to be arrested | SOD | Marketing | SCR | 2026-09-07 | HARSH WORKING CONDITIONS | 3 | ASSET INTEGRITY | S1 | F3 | 2026-09-07 | AUD-2026-09-2000017500ACN-2026-09-4000151570 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151570 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151570 | 532 | 8294 | 21 | 8294 | 42 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017500ACN-2026-09-4000151570 | AUD-2026-09-2000017500ACN-2026-09-4000151570 | 21 | 21 | 27 | 80 | 2 | 2 | 53 | 59
LINGAMPALLI SRIHARSHA | 2026-10-16 | KESHETTI SAI MANISH | 2026-10-16 | Relay replaced and Display in working condition | AUDIT UPLOAD IN SAP | 2026-08-26 18:00 | AUD-2026-09-2000017500 | 2026-08-26 10:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000151572 | Closed | KESHETTI SAI MANISH | 2026-10-16 | Display Panel of FE-1 was blank at start | 6.10 |  | 1915 | RAMAGUNDAM DEPOT | Display Panel to be repaired | SOD | Marketing | SCR | 2026-09-15 | THIRD PARTY ERRORS | 6 | ASSET INTEGRITY | S2 | F3 | 2026-09-15 | AUD-2026-09-2000017500ACN-2026-09-4000151572 | MH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017500ACN-2026-09-4000151572 | 2026-08-26 18:00 | 54.0038 | 410 | >20 | AUD-2026-09-2000017500 - ACN-2026-09-4000151572 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017500ACN-2026-09-4000151572 | AUD-2026-09-2000017500ACN-2026-09-4000151572 | 21 | 21 | 27 | 80 | 2 | 2 | 55 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | LIC conducts interactive session with Officers explaining about applicable standards, daily assigned jobs and other discussion related to work related issued faced by officers | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150400 | Closed | ROY TAVARES | 2026-10-16 | Gulbarga IRD Team of officers are fully motivated with enthusiasm and zeal to perform at peak of their potential to not only meet the set Goals & Targets but also excel in the same. | 1.1 | Interaction with all officers | 1797 | GULBARGA NEW IRD | Officers were appreciated for their efforts and maintaining the Depot in super notch level. They were advised to maintain the same tempo and ensure 100% Safety and compliance to SOP. LIC was advised to guide the officers in getting updated on all OISD standards applicable to Depot. | SOD | Marketing | SWZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150400 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150400 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150400 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150400 | AUD-2026-08-2000016952ACN-2026-08-4000150400 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | LIC has interacted with individual officers and explained individual expectation based upon role assigned | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150401 | Closed | ROY TAVARES | 2026-10-16 | Reviewed performance of all Officers and officers were found focussed on the Goals and Targets with emphasis on process/efficiency improvement | 1.2 | Performance review conducted | 1797 | GULBARGA NEW IRD | Team to focus on G&T for the year and come up with improvements process and work efficency. LIC advised to review the individual performance and advise officers to ensure 100% achievement. | SOD | Marketing | SWZ | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150401 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150401 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150401 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150401 | AUD-2026-08-2000016952ACN-2026-08-4000150401 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | File note for Dip elimation with backup has been initiated and forwarded to zone for approval | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150402 | Closed | ROY TAVARES | 2026-10-16 | Dip elimination to be completed at the earliest | 1.3 | Pending issues reviewed | 1797 | GULBARGA NEW IRD | 1. Location to expedite and achieve dip elimination at the earliest. | SOD | Marketing | SWZ | 2026-09-30 | POOR COMMUNICATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150402 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150402 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150402 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150402 | AUD-2026-08-2000016952ACN-2026-08-4000150402 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | Proposal has been initiated by location with backup for completing saledeed of 19.25 acres and for railway track maintenance initaited and forwarded to zone for approval | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150404 | Closed | ROY TAVARES | 2026-10-16 | 1. Funds for completing sale deed of 19.25 acres railway siding land 2. Additional fund in M&R code towards for payment to IOC towards railway track inspection & maintenance charges, For tank, structures and pipeline painting | 1.5 | HQO / Zonal support required identified | 1797 | GULBARGA NEW IRD | Proposal to be initiated and to be sent to zone | SOD | Marketing | SWZ | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016952ACN-2026-08-4000150404 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150404 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150404 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150404 | AUD-2026-08-2000016952ACN-2026-08-4000150404 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | 1.Proposal has been initiated and forwarded to zone for approval 2.Rain portective covers have been put on DU and kept at proper places | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-08-4000150405 | Closed | ROY TAVARES | 2026-10-16 | 1) 150 KVA Solar Proposal 2) Expansion area DUs are in Open | 1.8 | Improvement plans discussed | 1797 | GULBARGA NEW IRD | 1) Proposal to be sent to Zone/ HPRE 2) Covers to be put on Dus | SOD | Marketing | SWZ | 2026-09-10 | FAILURE TO FOLLOW PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016952ACN-2026-08-4000150405 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150405 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150405 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150405 | AUD-2026-08-2000016952ACN-2026-08-4000150405 | 21 | 21 | 27 | 80 | 5 | 5 | 54 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | Flow of MEFG near TK6 checked and rectified. Leakage of strainer nearTK-01 attended | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150410 | Closed | ROY TAVARES | 2026-10-16 | HVLR3 and sprinkler of TK1 was operated By officer Shubam Vishwakarma , MEFG near TK14 and TK6 was operated ,TK1 sprinkler testing was done , strainer was found to be leaking | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1797 | GULBARGA NEW IRD | Flow of MEFG near TK6 to be checked and rectified. Leakage of strainer nearTK-01 to be rectified | SOD | Marketing | SWZ | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-15 | AUD-2026-08-2000016952ACN-2026-08-4000150410 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150410 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150410 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016952ACN-2026-08-4000150410 | AUD-2026-08-2000016952ACN-2026-08-4000150410 | 21 | 21 | 27 | 80 | 5 | 5 | 55 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | 1. Proper housekeeping required at Emergency Trolley Shed Area. 2.Housekeeping of TT Gantry to be improved 3.Grass behind TW pump house to be cleared 4. Area Infront of unloading bay (Old mother foam tank area) 5. Planning room, security room housekepeing done | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150414 | Closed | ROY TAVARES | 2026-10-16 | House keeping to be improved | 3.15 | Housekeeping & PPE usage checked | 1797 | GULBARGA NEW IRD | 1. Proper housekeeping required at Emergency Trolley Shed Area. 2.Housekeeping of TT Gantry to be improved 3.Grass behind TW pump house to be cleared 4. Area Infront of unloading bay (Old mother foam tank area) to be cleaned. 5. Planning room, security room housekepeing to be improved | SOD | Marketing | SWZ | 2026-09-15 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-15 | AUD-2026-08-2000016952ACN-2026-08-4000150414 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150414 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150414 | 532 | 8294 | 21 | 8294 | 34 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150414 | AUD-2026-08-2000016952ACN-2026-08-4000150414 | 21 | 21 | 27 | 80 | 5 | 5 | 55 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | Random checking of EBP is been done and records are maintained in SAP by individual officers | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150411 | Closed | ROY TAVARES | 2026-10-16 | Records of ethanol blending percentage checks for first-load TTs are being maintained at the location in SAP for month of July26 was 15.22 % . Random checking was done for TT no:AP02TC9862, EBP percentage was found to be 18.0 % (without correction) | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1797 | GULBARGA NEW IRD | Random checking of TTs for EBP to be done on regular basis and Blending percentage of 20% to be maintained | SOD | Marketing | SWZ | 2026-09-01 | FAILURE TO FOLLOW PROCEDURES | 6 | PROCESS SAFETY | S3 | F2 | 2026-09-01 | AUD-2026-08-2000016952ACN-2026-08-4000150411 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150411 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150411 | 532 | 8294 | 21 | 8294 | 48 | 50 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-08-2000016952ACN-2026-08-4000150411 | AUD-2026-08-2000016952ACN-2026-08-4000150411 | 21 | 21 | 27 | 80 | 5 | 5 | 53 | 59
CHANDRAKANTH JOSHI | 2026-10-16 | ROY TAVARES | 2026-10-16 | Ethanol dips rods are been verified with weights and measures certificate and action taken wherever applicable | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-08-4000150413 | Closed | ROY TAVARES | 2026-10-16 | Yes records maintained. However, Physical verification of ethanol TT dip rod to be done for each TT. There is abnormal variation between MFM reading and Tank dip levels. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1797 | GULBARGA NEW IRD | Location to cross verify ethanol TT dip rods and action to be taken for variation between MFM reading and tank dip levels | SOD | Marketing | SWZ | 2026-09-01 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S2 | F2 | 2026-09-01 | AUD-2026-08-2000016952ACN-2026-08-4000150413 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150413 | 2026-08-19 18:00 | 61.0038 | 410 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150413 | 532 | 8294 | 21 | 8294 | 48 | 50 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016952ACN-2026-08-4000150413 | AUD-2026-08-2000016952ACN-2026-08-4000150413 | 21 | 21 | 27 | 80 | 5 | 5 | 53 | 59
|  | ROY TAVARES | 2026-10-16 | All 40 cameras are now funstional in VA portal | GULBARGA LOCATION VISIT Q2 | 2026-08-19 18:00 | AUD-2026-08-2000016952 | 2026-08-18 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-08-4000150408 | Completed | ROY TAVARES | 2026-10-16 | VA is enabled on 40 cameras, with 37 cameras functioning normally. The remaining 3 non-functional cameras are not available for VA monitoring | 2.7 | VA alerts checked / analysed | 1797 | GULBARGA NEW IRD | All 40 cameras are now funstional in VA portal | SOD | Marketing | SWZ | 2026-09-20 |  | 8 |  | S4 | F2 | 2026-09-20 | AUD-2026-08-2000016952ACN-2026-08-4000150408 | KA | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016952ACN-2026-08-4000150408 | 2026-08-19 18:00 | 61.0038 | 384 | >20 | AUD-2026-08-2000016952 - ACN-2026-08-4000150408 | 532 | 8294 | 21 | 8294 | 29 | 30 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-08-2000016952ACN-2026-08-4000150408 |  | AUD-2026-08-2000016952ACN-2026-08-4000150408 | 21 |  | 27 | 80 | 5 | 5 | 55
|  | SINGH YUGAL KISHOR | 2026-10-17 |  | SMA_REWARI TERMINAL_Q2 | 2026-09-10 17:00 | AUD-2026-09-2000017364 | 2026-09-08 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000153356 | Completed |  |  | Project Progress reviewed, A total of 08 projects for FY 2025–26, along with one carry-over project from FY 2024–25, were taken up by the location. Out of the total 09 projects, two have been completed. | 4.3 | Project progress reviewed | 1334 | HPCL REWARI IRD | Remaining 7 projects to be completed | SOD | Marketing | NZ | 2027-03-31 |  | 1 |  | S1 | F1 | 2027-03-31 | AUD-2026-09-2000017364ACN-2026-09-4000153356 | HR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017364ACN-2026-09-4000153356 | 2026-09-10 17:00 | 39.0455 | 576 | >20 | AUD-2026-09-2000017364 - ACN-2026-09-4000153356 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-09-2000017364ACN-2026-09-4000153356 |  | AUD-2026-09-2000017364ACN-2026-09-4000153356 | 21 |  | 27 | 80 | 1 | 1 | 83
SABLE RONAK MOHANKUMAR | 2026-10-17 | SINGH PREETI | 2026-10-14 | Trained personnel with HVD/HZA endorsement available at location, Mr. Mukeshji Bhakorda, Contract worker with MDPL, Palanpur (License No. GJ08 20050013729 dated 29.11.2025 valid till 10.03.2030), who is capable of Moving TTs in case of any emergency. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-09-4000150756 | Closed | SINGH PREETI | 2026-10-14 | Location to identify such person. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-10 | INADEQUATE SAFETY CULTURE | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-10 | AUD-2026-08-2000016905ACN-2026-09-4000150756 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150756 | 2026-08-22 22:00 | 57.8372 | 411 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150756 | 532 | 8294 | 21 | 8294 | 39 | 40 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150756 | AUD-2026-08-2000016905ACN-2026-09-4000150756 | 21 | 21 | 27 | 80 | 1 | 1 | 54 | 59
SABLE RONAK MOHANKUMAR | 2026-10-17 | SINGH PREETI | 2026-10-15 | Ramp up and down qty in BCU is adjusted so that Ethanol is loaded through inline blending with MS. And now Ethanol content is foundaccording to E20. | SR. MANAGEMENT INS PALANPUR Q2 26-27 | 2026-08-22 22:00 | AUD-2026-08-2000016905 | 2026-08-22 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-09-4000150770 | Closed | SINGH PREETI | 2026-10-15 | Ethanol Ramp up, down quantity to be checked for Bay No. 7 | 6.1 | Additional Observations | 1385 | PALANPUR TERMINAL | XX | SOD | Marketing | NWR | 2026-09-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-09-30 | AUD-2026-08-2000016905ACN-2026-09-4000150770 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016905ACN-2026-09-4000150770 | 2026-08-22 22:00 | 57.8372 | 411 | >20 | AUD-2026-08-2000016905 - ACN-2026-09-4000150770 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-08-2000016905ACN-2026-09-4000150770 | AUD-2026-08-2000016905ACN-2026-09-4000150770 | 21 | 21 | 27 | 80 | 1 | 1 | 57 | 59
MEENA HEMANT KUMAR | 2026-10-17 |  |  | Power is in auto mode, necessary ratification done during SAT | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153122 | Closed | MEENA HEMANT KUMAR | 2026-10-17 | Checked dip of following Tts: 1. RJ05GC0499: ok/ok/+1 mm Dip rod checked and found okay. 2. RJ02GB4727: ok/ok/+2 mm 3. RJ11GC1953; ok/+1 mm/+1 mm 4. RJ05GC1086: ok/+1 mm/+1 mm 5. RJ14 GJ1142: ok/+1 mm/ok 6. RJ34GB 1933: -1 mm/ok/+1 mm Power and turbo loading is done in manual mode through glass jar. Power dosing has to be done in auto mode through additive dosing skid | 3.2 | Post-loading dip checks verified | 1233 | BHARATPUR TERMINAL | Power and turbo loading is done in manual mode through glass jar. Power dosing has to be done in auto mode through additive dosing skid | SOD | Marketing | NWF | 2026-11-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153122 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153122 | 2026-09-16 17:45 | 33.0143 | 411 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153122 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153122 | AUD-2026-09-2000017503ACN-2026-09-4000153122 | 21 | 21 | 27 | 80 | 2 | 1 | 65 | 59
MEENA HEMANT KUMAR | 2026-10-17 |  |  | Total 120 KL bio-diesel has been consumed, Ethanol percentage is being checked on daily basis whenever any deviation observed mattar is taken with vendor. Ethanol prover has been checked during Q-2. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153124 | Closed | MEENA HEMANT KUMAR | 2026-10-17 | Bio diesel PO quantity to be utilised by intank blending. As discussed, location can unload even 40 KL bio diesel TT in 22 kl UG tank. TT has to be unloaded in two days. Bio diesel unloaded can be transferred to other spare UG/AG tank for B7. Ethanol blending % checked for following two TTs: 1. RJ05GC1086: Top sample: 17+1.07 = 18.07%, bottom sample: 18+1.07=19.07% 2. RJ11GC 1953: Top sample: 17.5+1.07= 18.57%, bottom sample: 17.5+1.07= 18.57% | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1233 | BHARATPUR TERMINAL | 1. Bio diesel PO qty to be consumed 2. Ethanol blending % is less than 19%. It needs to be checked and record to be maintained. Reason of lesser ethanol blending % to be cross checked through TAS vendor. Ethanol prover meter shuld also be verified. | SOD | Marketing | NWF | 2026-11-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-11-30 | AUD-2026-09-2000017503ACN-2026-09-4000153124 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153124 | 2026-09-16 17:45 | 33.0143 | 411 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153124 | 532 | 8294 | 21 | 8294 | -41 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153124 | AUD-2026-09-2000017503ACN-2026-09-4000153124 | 21 | 21 | 27 | 80 | 2 | 1 | 65 | 59
MEENA HEMANT KUMAR | 2026-10-17 |  |  | 1. Self TAS audit audit completed on 16.10.2026. 2. only one point of antivirus installation is pending, which is being done with the help of central IS team 3. User access modification has been done as per TAS circular. | VISIT TO BHARATPUR IRD ON 16TH SEPT Q2 | 2026-09-16 17:45 | AUD-2026-09-2000017503 | 2026-09-16 09:50 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000153129 | Closed | MEENA HEMANT KUMAR | 2026-10-17 | 1. Loaction has not carried out self TAS audit in last one year. This is violation of SOP. TAS officer needs to conduct the same despite when TAS is under revamp. There are many check list points which are required to be checked during TAS revamp period also. 2. 9 points out of total 28 recom of last TAS audit (23-27 Sept 2025) is still balance to be complied. 6 points of OISD out of 21 points, 1 point of MDSA, 2 points of HLSA out of 12 points and 1 point of T4S audit are pending as on date. Location assured that all points will be complied by this month end. 3. TAS user access (admin access) was given to Safety officer and S&D Officer. This isviolation of SOP. Admin access was given to TAS vendor also. Pls ensure strict compliance of circular of TAS User access. 4. Sr. Management inspection points (22 points are pending out of 62 points) are to be complied in SAP. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1233 | BHARATPUR TERMINAL | 1. Loaction has not carried out self TAS audit in last one year. This is violation of SOP. TAS officer needs to conduct the same despite when TAS is under revamp. There are many check list points which are required to be checked during TAS revamp period also. 2. 9 points out of total 28 recom of last TAS audit (23-27 Sept 2025) is still balance to be complied. 6 points of OISD out of 21 points, 1 point of MDSA, 2 points of HLSA out of 12 points and 1 point of T4S audit are pending as on date. Location assured that all points will be complied by this month end. 3. TAS user access (admin access) was given to Safety officer and S&D Officer. This isviolation of SOP. Admin access was given to TAS vendor also. Pls ensure strict compliance of circular of TAS User access. 4. Sr. Management inspection points are to be complied in SAP. | SOD | Marketing | NWF | 2026-10-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 8 | PROCESS SAFETY | S2 | F4 | 2026-10-31 | AUD-2026-09-2000017503ACN-2026-09-4000153129 | RJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017503ACN-2026-09-4000153129 | 2026-09-16 17:45 | 33.0143 | 411 | >20 | AUD-2026-09-2000017503 - ACN-2026-09-4000153129 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-09-2000017503ACN-2026-09-4000153129 | AUD-2026-09-2000017503ACN-2026-09-4000153129 | 21 | 21 | 27 | 80 | 2 | 1 | 61 | 59
NEHARA AJAY | 2026-10-17 |  |  | Earthing Work for Pipeline End in TLF PH completed. | SRMANAGEMENT INSPECTION Q1 26-27 KANDLA | 2026-05-22 | AUD-2026-06-2000012347 | 2026-05-21 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-06-4000137175 | Closed | NEHARA AJAY | 2026-10-17 | Earthing missing for pipe line end in TLF pump house. | 6.1 |  | 1583 | KANDLA TERMINAL | Corrective action to be taken | SOD | Marketing | NWR | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-10-30 | AUD-2026-06-2000012347ACN-2026-06-4000137175 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-06-2000012347ACN-2026-06-4000137175 | 2026-08-16 | 64.7538 | 411 | >20 | AUD-2026-06-2000012347 - ACN-2026-06-4000137175 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-06-2000012347ACN-2026-06-4000137175 | AUD-2026-06-2000012347ACN-2026-06-4000137175 | 21 | 21 | 27 | 80 | 2 | 2 | 44 | 59
SUJEET KUMAR | 2026-10-17 | SAXENA UMESH CHANDRA | 2026-10-17 | Hexane T K28 was under inspection and cleaning. Auto posting of dip is now enabled for all tanks. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152279 | Closed | SAXENA UMESH CHANDRA | 2026-10-17 | Auto dips are posted for all tanks except TK-28. TK-28 Hexane UG Tank is put under exception for Tank cleaning. Exception valid till 30.09.2026 | 3.8 | Auto vs Manual reconciliation checked | 1457 | INDORE DEPOT | Location to ensure posting dip for TK28 from 01.10.2026 onwards. | SOD | Marketing | CEN | 2026-10-01 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 4 | PROCESS SAFETY | S1 | F4 | 2026-10-01 | AUD-2026-09-2000017752ACN-2026-09-4000152279 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152279 | 2026-09-09 19:00 | 39.9622 | 411 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152279 | 532 | 8294 | 21 | 8294 | 18 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017752ACN-2026-09-4000152279 | AUD-2026-09-2000017752ACN-2026-09-4000152279 | 21 | 21 | 27 | 80 | 0 | -3 | 57 | 59
SUJEET KUMAR | 2026-10-17 | SAXENA UMESH CHANDRA | 2026-10-17 | Both MOCs viz Inspection of Hexane TK28 & Foam Pumps repair have been closed. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-09-4000152284 | Closed | SAXENA UMESH CHANDRA | 2026-10-17 | 2 MOC are open - (1) Foam Pumps and (2) Hexane UG Tank-28 | 3.17 | MOC status reviewed | 1457 | INDORE DEPOT | Open MOC to be closed at the earliest. | SOD | Marketing | CEN | 2026-10-15 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 4 | PROCESS SAFETY | S1 | F4 | 2026-10-15 | AUD-2026-09-2000017752ACN-2026-09-4000152284 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152284 | 2026-09-09 19:00 | 39.9622 | 411 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152284 | 532 | 8294 | 21 | 8294 | 4 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017752ACN-2026-09-4000152284 | AUD-2026-09-2000017752ACN-2026-09-4000152284 | 21 | 21 | 27 | 80 | 0 | -3 | 59 | 59
SUJEET KUMAR | 2026-10-17 | SAXENA UMESH CHANDRA | 2026-10-17 | Valuation report received. Committee is formed. Scrap shall be disposed-of thereafter as per procedure. | LOCATION VISIT AT INDORE IRD | 2026-09-09 19:00 | AUD-2026-09-2000017752 | 2026-09-08 09:40 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-09-4000152286 | Closed | SAXENA UMESH CHANDRA | 2026-10-17 | Miscellaneous scrap items available at location to be disposed off on priority. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1457 | INDORE DEPOT | RFD to be initiated for disposing of accumulated scrap items. | SOD | Marketing | CEN | 2026-10-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | ENVIRONMENTAL | S1 | F4 | 2026-10-31 | AUD-2026-09-2000017752ACN-2026-09-4000152286 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017752ACN-2026-09-4000152286 | 2026-09-09 19:00 | 39.9622 | 411 | >20 | AUD-2026-09-2000017752 - ACN-2026-09-4000152286 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-09-2000017752ACN-2026-09-4000152286 | AUD-2026-09-2000017752ACN-2026-09-4000152286 | 21 | 21 | 27 | 80 | 0 | -3 | 61 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | Location conducted fire drills for all the scenarios including fire scenario at T/W siding while starting unloading operations as per scenario suggested by auditing team during the inspection. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155651 | Closed | BUDHI VEERAIAH | 2026-10-18 | LIC confirmed that all the fire drills conducted at location in of surprise in nature. location has prepared the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1644 | KOLKATA-I TERMINAL | Location to ensure to complete all the fire scenario as per ERDMP in the mock drills. | SOD | Marketing | EZ | 2026-10-10 | COMPLACENCY OR RISK NORMALIZATION | 5 | EMERGENCY | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155651 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155651 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155651 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017513ACN-2026-10-4000155651 | AUD-2026-10-2000017513ACN-2026-10-4000155651 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | All the officers who recently transferred and newly recruited were given firefighting training in class room with several PPts on firefighting equipment usage and also participated in fire drills as per the fire organization team responsibilities. All the new officers actively participated in recent Level2 ERDMP drills. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155656 | Closed | BUDHI VEERAIAH | 2026-10-18 | DSO to ensure to have hands on training to all the officers. All officer must know the positioning of the different fire fire fighting equipments. [Repeat Point] | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1644 | KOLKATA-I TERMINAL | More hands on training on safety critical equipment to be acquired by all the officers. DSO to provide safety training to all officers as per the OISD guideline and record maintained. | SOD | Marketing | EZ | 2026-10-10 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155656 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155656 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155656 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017513ACN-2026-10-4000155656 | AUD-2026-10-2000017513ACN-2026-10-4000155656 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | All the observations and recommendations of the drill during the audit inspection were discussed among the fire organization teams to cover all the activities like usage of Stretcher , first aid medical kit for injured persons, timely communication to OMC members, Fire dept., reporting of ambulance at site etc. in the successive drills .All the events were ensured in the recently conducted Level 2 drill also. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-10-4000155652 | Closed | BUDHI VEERAIAH | 2026-10-18 | Scenario : Electrical fire in one of the panel in MCC room (Pump house) was conducted during normal operational hour. 1. CO2 discharge found satisfactory.Hand gloves were used 2. There was slight delay in ESD operation 3. There was slight delay in reportin of Rescue Team leader 4. Stretcher was not used 5. Role of officers to be strictly defined in FOC and members should act accrodingly. 6. Information to OMC members, Fire Dept, nearest hospital was not sent and accrodingly they didn't reported. Ambulance was not called. | 2.2 | Double contingency scenario simulated; observations recorded | 1644 | KOLKATA-I TERMINAL | All the observation and recommendation of the drill to be implemented in the next and subsequent drill | SOD | Marketing | EZ | 2026-10-10 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155652 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155652 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155652 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017513ACN-2026-10-4000155652 | AUD-2026-10-2000017513ACN-2026-10-4000155652 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | LIC regularly reviews on a daily basis along with TAS officer on the events of critical alarms like alarms of Dyke valves open, ROSOVs, ESDs, Smoke detectors , Gantry permissive failures periodically and reporting is being maintained if any abnormalities found. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | LIC REGULARLY REVIEWS ON A DAILY BASIS A | ACN-2026-10-4000155662 | Closed | BUDHI VEERAIAH | 2026-10-18 | Critical Alarms checked and no abnormal observations recorded | 3.12 | Critical alarms checked & corrective actions reviewed | 1644 | KOLKATA-I TERMINAL | LIC to review the critical alarms periodically and report if any abnormalities found. | SOD | Marketing | EZ | 2026-10-10 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155662 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155662 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155662 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017513ACN-2026-10-4000155662 | AUD-2026-10-2000017513ACN-2026-10-4000155662 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | LIC reviewed the K Factor and meter factor in system and in BCU along with assistance of TAS officer. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155663 | Closed | MAJUMDER BIRAJ | 2026-10-18 | K factor changes reviewed and found matching with BCU | 3.13 | K-factor changes reviewed (if any) | 1644 | KOLKATA-I TERMINAL | LIC to periodically review the K Factor and meter factor in system and in BCU | SOD | Marketing | EZ | 2026-10-10 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155663 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155663 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155663 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017513ACN-2026-10-4000155663 | AUD-2026-10-2000017513ACN-2026-10-4000155663 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | Earth pit boards updated with earthing testing details like Earth pit no, connected equipment details, testing date and due date etc. in all places both in BB-I and BB-II. Earth pit inspection records maintained. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-10-4000155666 | Closed | BUDHI VEERAIAH | 2026-10-18 | Earthpit board to be corrected in BB-I and BB-II wherein due date is over. It was given to understand that the checking is completed but updation of board is pending. | 3.16 | Earth pits / boundary / vegetation control checked | 1644 | KOLKATA-I TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-10-10 | POOR EQUIPMENT MAINTENANCE | 10 | ASSET INTEGRITY | S2 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155666 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155666 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155666 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-10-2000017513ACN-2026-10-4000155666 | AUD-2026-10-2000017513ACN-2026-10-4000155666 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
MAJUMDER BIRAJ | 2026-10-18 | BUDHI VEERAIAH | 2026-10-18 | Housekeeping has been improved with regular field follow up with housekeeping teams of both BB 1 & BB 2 at all places like Admin Building area , Fire Water tank Farm area, TT Gantry , TT parking area and drains inside and outside of the premises at places likeTT parking , Product pump house etc. | KOLKATA TERMINAL Q2 FY 26-27 INSPECTION | 2026-09-18 | AUD-2026-10-2000017513 | 2026-09-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-10-4000155668 | Closed | BUDHI VEERAIAH | 2026-10-18 | Visit in TTG, TWG, Scrapyard, TTPH, TWPH, Control room, Security room, Admin carried out. Housekeeping & SOP adherence found satisfactory | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1644 | KOLKATA-I TERMINAL | Housekeepin in Admin Building Water tank Farm area/TTG / TT Parking / BB-II to be improved. | SOD | Marketing | EZ | 2026-10-10 | INADEQUATE SAFETY CULTURE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-10-10 | AUD-2026-10-2000017513ACN-2026-10-4000155668 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-10-2000017513ACN-2026-10-4000155668 | 2026-09-18 | 31.7538 | 412 | >20 | AUD-2026-10-2000017513 - ACN-2026-10-4000155668 | 532 | 8294 | 21 | 8294 | 9 | 10 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-10-2000017513ACN-2026-10-4000155668 | AUD-2026-10-2000017513ACN-2026-10-4000155668 | 21 | 21 | 27 | 80 | 0 | -7 | 58 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | Location ensuring to complete all the fire scenario as per ERDMP in the mock drills. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143420 | Closed | ISLAM SK WAHIUL | 2026-10-18 | LIC confirmed that all the fire drills conducted at location in of surprise in nature. As advised in last inspection, location has prepared the calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1650 | HALDIA TERMINAL | Location to ensure to complete all the fire scenario as per ERDMP in the mock drills. | SOD | Marketing | EZ | 2026-09-30 | POOR COMMUNICATION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-09-30 | AUD-2026-07-2000015092ACN-2026-07-4000143420 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143420 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143420 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143420 | AUD-2026-07-2000015092ACN-2026-07-4000143420 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | Old lights repaired and lux level of secondary roads are now satisfactory. NPCB approved project for procurement of lights is underprogress. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143422 | Closed | ISLAM SK WAHIUL | 2026-10-18 | Lux level checked : TT gantry : Required : 60 and observed : 220 Secondary roads : Required 10 and observed 8 at several places | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1650 | HALDIA TERMINAL | It was advised to improve the lux levels on the secondary roads by repairing the old lights. NPCB also approved for procurement of lights. Projects to be executed timely so as to comply this point | SOD | Marketing | EZ | 2026-09-30 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-09-30 | AUD-2026-07-2000015092ACN-2026-07-4000143422 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143422 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143422 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015092ACN-2026-07-4000143422 | AUD-2026-07-2000015092ACN-2026-07-4000143422 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | Non-functional CCTV cameras are made online in close co-ordination with vendor. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143424 | Closed | ISLAM SK WAHIUL | 2026-10-18 | Location has total of 68 CCTV Camera and 3 of them were not active on the date of visit | 2.6 | CCTV functioning checked | 1650 | HALDIA TERMINAL | Random video recording of the CCTV at main gate area were checked and it was advised to make the non functional CCTV to be made functional at the earliest in close coordination with vendor. | SOD | Marketing | EZ | 2026-06-30 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143424 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143424 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143424 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143424 | AUD-2026-07-2000015092ACN-2026-07-4000143424 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | VMS implemented. Nil case of visitors entry without VMS is ensured. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-07-4000143426 | Closed | ISLAM SK WAHIUL | 2026-10-18 | Access control system found functional. It was noted that the VMS service is not operational. | 2.8 | Access control systems checked | 1650 | HALDIA TERMINAL | VMS to be implemented. Nil case of visitors entry without VMS to be ensured | SOD | Marketing | EZ | 2026-07-31 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143426 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143426 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143426 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143426 | AUD-2026-07-2000015092ACN-2026-07-4000143426 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | Location created secondary route wherever applicable. ATF TTs loaded ex Haldia TOPs are tracked for route deviation and abnormal stoppages. Necessary ITDG action taken if applicable. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-07-4000143429 | Closed | ISLAM SK WAHIUL | 2026-10-18 | Review of VTS deviation done on regular basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC | 3.3 | VTS deviations reviewed | 1650 | HALDIA TERMINAL | Location is advised to create the secondary route wherever applicable. ATF TTs loaded ex Haldia TOPs to be tracked for route deviations, abnormal stoppages en route to ASF stations.Necessary actions as per ITDG, if applicable to be taken. | SOD | Marketing | EZ | 2026-06-30 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-07-2000015092ACN-2026-07-4000143429 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143429 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143429 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM |  | AUD-2026-07-2000015092ACN-2026-07-4000143429 | AUD-2026-07-2000015092ACN-2026-07-4000143429 | 21 | 21 | 27 | 80 | 5 | 5 | 44 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | Pumps from mahul received at Haldia Terminal. Installation job in progress. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-07-4000143439 | Closed | ISLAM SK WAHIUL | 2026-10-18 | MS unloading line project was reviewed and depot ensured to close all the project within timeline. | 4.3 | Project progress reviewed | 1650 | HALDIA TERMINAL | It is advised to get the pumps from mahul at the earliest. | SOD | Marketing | EZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S1 | F4 | 2026-09-30 | AUD-2026-07-2000015092ACN-2026-07-4000143439 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143439 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143439 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143439 | AUD-2026-07-2000015092ACN-2026-07-4000143439 | 21 | 21 | 27 | 80 | 5 | 5 | 57 | 59
KUNDU DEBARUN | 2026-10-18 | ISLAM SK WAHIUL | 2026-10-18 | 1. Double safety harness provided for TT locking shed and TT security checking platform 2. Insulation rubber on the swing ladder at TTG, TT locking shed, TT security checking platform are replaced. 4. Only non sparking tool is used in the licenced area. 5. Used DCPs are immedaitely removed and refilled. 6. Communication arrangement for emergency scenario in TT parking is done. Security is available. PA is also active. | HALDIA TERMINAL Q1 FY 26-27 INSPECTION | 2026-06-04 15:00 | AUD-2026-07-2000015092 | 2026-06-02 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-07-4000143441 | Closed | ISLAM SK WAHIUL | 2026-10-18 | 1. Double safety harness to be provided for TT locking shed and TT security checking platform 2. Wear and tear found w.r.t Insulation rubber on the swing ladder at TTG, TT locking shed, TT security checking platform 3. Validity of User matrix in TAS to be madehaving expiry on 01-10-26 for all user and 05-10-26 for LIC and further extended by 6 months every time. 4. It is advised to use non sparking tool only in the licenced area. 5. 25 KG DCP and 9 KG empty DCP found lying in field. To be removed immediately after use and to be refilled. 6. Communication arrangement for emergency scenario (ESD/ pager/ Permanent Security) in TT parking to be done. | 6.1 | Additional Observations | 1650 | HALDIA TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-07-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-07-31 | AUD-2026-07-2000015092ACN-2026-07-4000143441 | WB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015092ACN-2026-07-4000143441 | 2026-08-20 00:14 | 60.7441 | 412 | >20 | AUD-2026-07-2000015092 - ACN-2026-07-4000143441 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-07-2000015092ACN-2026-07-4000143441 | AUD-2026-07-2000015092ACN-2026-07-4000143441 | 21 | 21 | 27 | 80 | 5 | 5 | 48 | 59
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-11 | AUD-2026-03-2000011022 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125389 | Open |  |  | Lux requirement/ Lux achieved: 1. Gantry platform: 82/60 2. Gantry ground area: 62 3. Road bet PH and Gantry: 3/10 4. Tank farm2 valve manifold area: 35/60 5. Prod PH: 90/100 6. UG Tank farm: 14/ 7. Control room: 520/400 8. Near TK9 in dyke 2: 15/60 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1242 | JAIPUR TERMINAL | Lux level is poor in many operating areas, specially on Road and tank farm. It is a serious concern. Location needs to workout action plan and share the same by this month end with details of tender. Job is to be completed by Q1 2026-2027 | SOD | Marketing | NWF | 2026-06-30 |  | 12 |  | S3 | F4 | 2026-06-30 | AUD-2026-03-2000011022ACN-2026-03-4000125389 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011022ACN-2026-03-4000125389 | 2026-09-30 | 19.7538 | 302 | >20 | AUD-2026-03-2000011022 - ACN-2026-03-4000125389 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011022ACN-2026-03-4000125389 |  | AUD-2026-03-2000011022ACN-2026-03-4000125389 | 21 |  | 26 | 80 | 0 | 0 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125071 | Open |  |  | MDSA Pending Points nil and SSA three pending points work in progress | 3.18 | OISD/MDSA/SSA compliance reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Compliance of Pending SSA points to be expedited | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011314ACN-2026-03-4000125071 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125071 | 2026-09-17 20:00 | 31.9205 | 302 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125071 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011314ACN-2026-03-4000125071 |  | AUD-2026-03-2000011314ACN-2026-03-4000125071 | 21 |  | 26 | 80 | 3 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125072 | Open |  |  | Transporters meet done . Transporters requested for updation of Toll routes as they are not receiving Toll charges reimbursements for some tolls. TT TDG violations such speed violations, route deviations , unauthorised stoppages were discussed during the meeting | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1992 | VISAKH WHITE OIL TERMINAL | Toll routes updation to be completed in coordination with sales officers | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011314ACN-2026-03-4000125072 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125072 | 2026-09-17 20:00 | 31.9205 | 241 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125072 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011314ACN-2026-03-4000125072 |  | AUD-2026-03-2000011314ACN-2026-03-4000125072 | 21 |  | 26 | 80 | 3 | 2 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125074 | Open |  |  | NPCB projects of Marine loading arm at SS Jetty and Signal sharing with OMC are delayed | 4.3 | Project progress reviewed | 1992 | VISAKH WHITE OIL TERMINAL | To follow up with vendor for supply of Marine loading arm. To take up with IOC for completion of signal sharing works . | SOD | Marketing | SCR | 2026-05-30 |  | 5 |  | S1 | F5 | 2026-05-30 | AUD-2026-03-2000011314ACN-2026-03-4000125074 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125074 | 2026-09-17 20:00 | 31.9205 | 271 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125074 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011314ACN-2026-03-4000125074 |  | AUD-2026-03-2000011314ACN-2026-03-4000125074 | 21 |  | 26 | 80 | 3 | 2 | 39
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125093 | Open |  |  | MDSA two Pending Points and SSA two pending points work in progress | 3.18 | OISD/MDSA/SSA compliance reviewed | 3708 | VISAKH NBOT | Compliance of Pending MDSA and SSA points to be expedited | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125093 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125093 | 2026-09-18 17:30 | 31.0247 | 211 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125093 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011315ACN-2026-03-4000125093 |  | AUD-2026-03-2000011315ACN-2026-03-4000125093 | 21 |  | 26 | 80 | 2 | 1 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125096 | Open |  |  | Smoke Detector system integration with TAS is pending | 6.1 |  | 3708 | VISAKH NBOT | Smoke Detector system integration with TAS to be expedited | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-03-2000011315ACN-2026-03-4000125096 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125096 | 2026-09-18 17:30 | 31.0247 | 241 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125096 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011315ACN-2026-03-4000125096 |  | AUD-2026-03-2000011315ACN-2026-03-4000125096 | 21 |  | 26 | 80 | 2 | 1 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125098 | Open |  |  | Bitumen Tanks cleaning and internal inspection is pending | 6.4 |  | 3708 | VISAKH NBOT | to be done | SOD | Marketing | SCR | 2026-12-30 |  | 5 |  | S1 | F5 | 2026-12-30 | AUD-2026-03-2000011315ACN-2026-03-4000125098 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125098 | 2026-09-18 17:30 | 31.0247 | 485 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125098 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011315ACN-2026-03-4000125098 |  | AUD-2026-03-2000011315ACN-2026-03-4000125098 | 21 |  | 26 | 80 | 2 | 1 | 70
|  |  |  | Necessary changes to be made in coordination with Vendor | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125556 | Open | AGARWAL VIPUL | 2026-03-18 | The ERDMP of Bahadurgarh has been reviewed. Scenarios related to L-1, L-2, and L-3 were also examined. It was observed that under the failure cases, one scenario mentioned as “Receiving line from jetty full bore failure for products (Sl. No. 08)” is not relevant to the location. Further monthly Mock drill reports has been reviewed and all possible scenerios were covered. | 2.5 | Emergency response preparedness reviewed | 1216 | BAHADURGARH TERMINAL | The ERDMP should be reviewed and updated to remove or modify the non-applicable scenario to ensure location-specific accuracy. | SOD | Marketing | NZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125556 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125556 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125556 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125556 |  | AUD-2026-03-2000011128ACN-2026-03-4000125556 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | PO placed additional budget will be taken and executed. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125571 | Open | AGARWAL VIPUL | 2026-03-18 | Boundary Wall - The boundary wall requires civil repair and repainting. At several locations, the plaster has deteriorated and is found to be dislodged. The concertina coil placed along the periphery and is intact. However, provision of broken glass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. | 3.16 | Earth pits / boundary / vegetation control checked | 1216 | BAHADURGARH TERMINAL | Civil work and painting of boundary wall to be ensured | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125571 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125571 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125571 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125571 |  | AUD-2026-03-2000011128ACN-2026-03-4000125571 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | MCS tender floated. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125574 | Open | AGARWAL VIPUL | 2026-03-18 | MDSA - Last MDSA/Comprehensive audit was conducted on 02 -05 Dec 2024 - Communication of MOV's with MCS is not established in field due to MCS obsolution | 3.18 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | Communication between the MOVs and the MCS should be re-established by upgrading or replacing the obsolete MCS system to ensure proper monitoring and control from the control room. | SOD | Marketing | NZ | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125574 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125574 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125574 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125574 |  | AUD-2026-03-2000011128ACN-2026-03-4000125574 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | compliance of Balance Points is under progress | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125575 | Open | AGARWAL VIPUL | 2026-03-18 | MDSA - Last MDSA/Comprehensive audit was conducted on on 24- 28 Nov 2025 - Tot 43 observation were there , out of which 07 points are complied, Remaining to be complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | The remaining observations should be addressed and complied with at the earliest to ensure full closure. | SOD | Marketing | NZ | 2026-10-31 |  | 8 |  | S2 | F4 | 2026-10-31 | AUD-2026-03-2000011128ACN-2026-03-4000125575 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125575 | 2026-09-05 | 44.7538 | 425 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125575 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011128ACN-2026-03-4000125575 |  | AUD-2026-03-2000011128ACN-2026-03-4000125575 | 21 |  | 26 | 80 | 9 | 9 | 61
|  |  |  | Actions initiated for all points. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125576 | Open | AGARWAL VIPUL | 2026-03-18 | SSA - 03-10 Sep 2025 - Total observations are 34 in no. and as on date 32 complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1216 | BAHADURGARH TERMINAL | The remaining observations should be addressed and complied with at the earliest to ensure full closure. | SOD | Marketing | NZ | 2027-03-31 |  | 2 |  | S2 | F1 | 2027-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125576 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125576 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125576 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125576 |  | AUD-2026-03-2000011128ACN-2026-03-4000125576 | 21 |  | 26 | 80 | 9 | 9 | 83
|  |  |  | LPR generation and Tendering process will be initiated after receipt of additional Budget | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125578 | Open | AGARWAL VIPUL | 2026-03-18 | Painting of Hydrant Line required at several placed in TWG / TFA / and around peripheral sections | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Hydrant line painting work to be carried out | SOD | Marketing | NZ | 2026-10-31 | FAILURE TO FOLLOW PROCEDURES | 10 | ASSET INTEGRITY | S2 | F5 | 2026-10-31 | AUD-2026-03-2000011128ACN-2026-03-4000125578 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125578 | 2026-09-05 | 44.7538 | 425 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125578 | 532 | 8294 | 21 | 8294 | -11 | 10 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011128ACN-2026-03-4000125578 |  | AUD-2026-03-2000011128ACN-2026-03-4000125578 | 21 |  | 26 | 80 | 9 | 9 | 61
|  |  |  | Additiona funs will be required to be taken. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125584 | Open | AGARWAL VIPUL | 2026-03-18 | The 12 ATF line laid in the Tank Farm area is observed to have corrosion at the 6 o’clock position, with clamping done at several locations to prevent leakage. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The pipeline should be thoroughly inspected and the affected section repaired or replaced as required. | SOD | Marketing | NZ | 2027-03-31 |  | 2 |  | S1 | F2 | 2027-03-31 | AUD-2026-03-2000011128ACN-2026-03-4000125584 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125584 | 2026-09-05 | 44.7538 | 576 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125584 | 532 | 8294 | 21 | 8294 | -162 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125584 |  | AUD-2026-03-2000011128ACN-2026-03-4000125584 | 21 |  | 26 | 80 | 9 | 9 | 83
|  |  |  | Inspection by 30.06.2026. And replacement if required shall be done by 31.03.2027 | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125586 | Open | AGARWAL VIPUL | 2026-03-18 | Pitting corrosion was observed on the HSD line at the Tank Wagon Gantry. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The line should be inspected and necessary corrective actions, including repair or replacement of the affected section, should be carried out. | SOD | Marketing | NZ | 2026-09-30 |  | 1 |  | S1 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125586 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125586 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125586 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125586 |  | AUD-2026-03-2000011128ACN-2026-03-4000125586 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | Vendor is being lined up for job and necessary coordination with Discom | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125589 | Open | AGARWAL VIPUL | 2026-03-18 | 4 pole structure if observed to be rusting. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The 4-pole structure observed to be rusting should be inspected and necessary corrective actions such as rust removal, surface treatment, and protective painting should be carried out to prevent further deterioration. | SOD | Marketing | NZ | 2026-06-30 |  | 2 |  | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011128ACN-2026-03-4000125589 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125589 | 2026-09-05 | 44.7538 | 302 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125589 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125589 |  | AUD-2026-03-2000011128ACN-2026-03-4000125589 | 21 |  | 26 | 80 | 9 | 9 | 44
|  |  |  | Started job. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125592 | Open | AGARWAL VIPUL | 2026-03-18 | In the MCC room, it has been observed that the fuses used in the electrical panel do not match the approved SLD and are of higher rating. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The fuses should be replaced with the correct rating as per the approved SLD to ensure electrical safety and proper protection of the system. | SOD | Marketing | NZ | 2026-09-30 |  | 3 |  | S3 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125592 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125592 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125592 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125592 |  | AUD-2026-03-2000011128ACN-2026-03-4000125592 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | Inspection by 30.06.2026. And replacement if required shall be done by 31.03.2027 | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125594 | Open | AGARWAL VIPUL | 2026-03-18 | The ATF line laid in the Tank Wagon Gantry area requires painting, as pitting corrosion has been observed. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | The line should be inspected and necessary surface treatment and painting should be carried out to prevent further corrosion. | SOD | Marketing | NZ | 2026-09-30 |  | 3 |  | S3 | F1 | 2026-09-30 | AUD-2026-03-2000011128ACN-2026-03-4000125594 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125594 | 2026-09-05 | 44.7538 | 394 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125594 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125594 |  | AUD-2026-03-2000011128ACN-2026-03-4000125594 | 21 |  | 26 | 80 | 9 | 9 | 57
|  |  |  | Procremenst commenced. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125596 | Open | AGARWAL VIPUL | 2026-03-18 | Flanges connected to foam line in Foam tank of 500 Ltrs are sub standard. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | These should be replaced with standard and approved fittings to ensure safe and reliable operation. | SOD | Marketing | NZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011128ACN-2026-03-4000125596 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125596 | 2026-09-05 | 44.7538 | 302 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125596 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125596 |  | AUD-2026-03-2000011128ACN-2026-03-4000125596 | 21 |  | 26 | 80 | 9 | 9 | 44
|  |  |  | Job under progress. | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125600 | Open | AGARWAL VIPUL | 2026-03-18 | Unused cable entry points in the junction boxes at the TT Gantry were found to be left open. | 4.0999999999999996 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1216 | BAHADURGARH TERMINAL | Unused cable entry points in the junction boxes should be properly blinded to prevent ingress of dust and moisture. | SOD | Marketing | NZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011128ACN-2026-03-4000125600 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125600 | 2026-09-05 | 44.7538 | 241 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125600 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125600 |  | AUD-2026-03-2000011128ACN-2026-03-4000125600 | 21 |  | 26 | 80 | 9 | 9 | 35
[5 empty] | SR MGMT INSPECTION 1216 BAHADURGARH TML | 2026-02-24 17:30 | AUD-2026-03-2000011128 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125602 | Open |  |  | All balance scrap to be disposed by 30.3.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1216 | BAHADURGARH TERMINAL | All balance scrap to be disposed by 30.3.2026 | SOD | Marketing | NZ | 2026-03-30 |  | 1 |  | S1 | F1 | 2026-03-30 | AUD-2026-03-2000011128ACN-2026-03-4000125602 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011128ACN-2026-03-4000125602 | 2026-09-05 | 44.7538 | 210 | >20 | AUD-2026-03-2000011128 - ACN-2026-03-4000125602 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011128ACN-2026-03-4000125602 |  | AUD-2026-03-2000011128ACN-2026-03-4000125602 | 21 |  | 26 | 80 | 9 | 9 | 30
[5 empty] | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125703 | Open |  |  | NPCB related points & other depot related action points reviewed | 1.4 | Earlier action points status checked | 1742 | BOKARO DEPOT | All NPCB projects to be completed by 30.6.2026 | SOD | Marketing | PZR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125703 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125703 | 2026-09-19 10:00 | 30.3372 | 302 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125703 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010870ACN-2026-03-4000125703 |  | AUD-2026-03-2000010870ACN-2026-03-4000125703 | 21 |  | 26 | 80 | 1 | 1 | 44
[5 empty] | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125719 | Open |  |  | pending Points : OISD - NIL SSA - 6 MDSA - 10 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1742 | BOKARO DEPOT | Advised to close all points | SOD | Marketing | PZR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010870ACN-2026-03-4000125719 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125719 | 2026-09-19 10:00 | 30.3372 | 241 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125719 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010870ACN-2026-03-4000125719 |  | AUD-2026-03-2000010870ACN-2026-03-4000125719 | 21 |  | 26 | 80 | 1 | 1 | 35
[5 empty] | SENIOR MANAGEMENT INSPECTION | 2026-01-29 | AUD-2026-03-2000010870 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125721 | Open |  |  | All NPCB projects reviewed . Major project of ethanol tank and MFM jobs are in progress , apart from some OISD compliances projects | 4.3 | Project progress reviewed | 1742 | BOKARO DEPOT | Location officers advised to complete all projects by 30.06.2026 | SOD | Marketing | PZR | 2026-06-30 |  | 8 |  | S2 | F4 | 2026-06-30 | AUD-2026-03-2000010870ACN-2026-03-4000125721 | JH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010870ACN-2026-03-4000125721 | 2026-09-19 10:00 | 30.3372 | 302 | >20 | AUD-2026-03-2000010870 - ACN-2026-03-4000125721 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010870ACN-2026-03-4000125721 |  | AUD-2026-03-2000010870ACN-2026-03-4000125721 | 21 |  | 26 | 80 | 1 | 1 | 44
|  |  |  | Power card issue and earthing relay issue has been rectified. Communication issue yet to be rectified. Taken up with TAS vendor | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125839 | Open | Sreelal P P | 2026-05-23 | K factor changed in bay No.2 due to power card issue. Bay is still kept offline due to earthing relay issue | 3.13 | K-factor changes reviewed (if any) | 1845 | IRUMPANAM TERMINAL | Bay:2 to be made functional at the earliest | SOD | Marketing | CZR | 2026-04-30 |  | 8 |  | S4 | F2 | 2026-04-30 | AUD-2026-03-2000011133ACN-2026-03-4000125839 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125839 | 2026-09-02 16:30 | 47.0663 | 241 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125839 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011133ACN-2026-03-4000125839 |  | AUD-2026-03-2000011133ACN-2026-03-4000125839 | 21 |  | 26 | 80 | 1 | -4 | 35
[5 empty] | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124859 | Open |  |  | Lux level checked and found low level at : 1. Tank 18/19 ROSOV /MOV area - only 10 2. Primary road near HSD tank - only 10 3. rear side of TT gantry - 28 4. Lube drum area - no light | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1723 | PATNA DEPOT | Location advised to take budget and improve lighting in these areas | SOD | Marketing | PZR | 2026-09-30 | FAILURE TO FOLLOW PROCEDURES | 15 | PROCESS SAFETY | S3 | F5 | 2026-09-30 | AUD-2026-03-2000011074ACN-2026-03-4000124859 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124859 | 2026-08-03 | 77.7538 | 394 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124859 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011074ACN-2026-03-4000124859 |  | AUD-2026-03-2000011074ACN-2026-03-4000124859 | 21 |  | 26 | 80 | 0 | 0 | 57
[5 empty] | SR. MANAGEMENT INSPECTION- PATNA NEW IRD | 2026-03-18 | AUD-2026-03-2000011074 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124872 | Open |  |  | VRU is found not working from last 8 months due to OEM refusal to mainatin without giving them AMC order for longer period at very high cost | 6.3 | VRU operations | 1723 | PATNA DEPOT | Urgently other vendors to be roped in with help of HQO | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-06-30 | AUD-2026-03-2000011074ACN-2026-03-4000124872 | BR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011074ACN-2026-03-4000124872 | 2026-08-03 | 77.7538 | 302 | >20 | AUD-2026-03-2000011074 - ACN-2026-03-4000124872 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011074ACN-2026-03-4000124872 |  | AUD-2026-03-2000011074ACN-2026-03-4000124872 | 21 |  | 26 | 80 | 0 | 0 | 44
|  |  |  | "1. GMB payment issue being resolved in coordination with GMB. Account reconcilliation in progress. 2. TK10 & TK14 issue resolved. 3. SSA & ESA complaince being done in time bound manner. 4. Surge Analysis in progress. Rupture Disk procurement in progress. 5.Manpower issue being taken up zone." | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125469 | Open | KUMAR NITISH | 2026-07-31 | Following pending issues were discussed with Location team- 1. The current GMB payment process being followed was discussed in detail and advised location to take immediate action for clearance of pending payments on priority for ensuring smooth vessel berthing operations at Mundra. Also, location has been advised to take approvals in line with EAM for increased mandatory deposit with GMB keeping cushion for 5-6 vessels at all times. 2. Detailed discussion happened on the process of product handling of TK10 & TK14 in line with HQO discussion for ensuring that tanks will be further utilized for MS/HSD. 3. Current compliance status of SSA and ESA hasbeen discussed with Mundra team with action plan for ensuring time bound closure of recommendations. It was advised to location to prepare and share the tank outage schedule and action plan for installation of RRD on pending tanks and tanks requiring major repairs. 4. Existing surge relieve mechanism has been discussed and further action to be taken for handling surge during vessel backloading operations. 5. During discussion with location, location has expressed the constraints faced wrt available manpower for ensuringvessel unloading and other major ongoing activities. Zone is currently arranging the manpower from other locations’ within zone as per requirement. | 1.3 | Pending issues reviewed | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-03-2000010720ACN-2026-03-4000125469 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125469 | 2026-09-18 | 31.7538 | 302 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125469 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010720ACN-2026-03-4000125469 |  | AUD-2026-03-2000010720ACN-2026-03-4000125469 | 21 |  | 26 | 80 | 5 | 5 | 44
|  |  |  | SSA & ESA complaince being done in time bound manner. | SENIOR MANAGEMENT INSPECTION MUNDRA TERM | 2026-02-04 | AUD-2026-03-2000010720 | 2026-02-03 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125476 | Open | KUMAR NITISH | 2026-07-31 | Current compliance status of SSA and ESA has been discussed with Mundra team with action plan for ensuring time bound closure of recommendations. It was advised to location to prepare and share the tank outage schedule and action plan for installation of RRD on pending tanks and tanks requiring major repairs. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1546 | Mundra Terminal-MDPL | Location to take corrective action | SOD | Marketing | NWR | 2026-12-30 |  | 4 |  | S2 | F2 | 2027-03-31 | AUD-2026-03-2000010720ACN-2026-03-4000125476 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010720ACN-2026-03-4000125476 | 2026-09-18 | 31.7538 | 485 | >20 | AUD-2026-03-2000010720 - ACN-2026-03-4000125476 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010720ACN-2026-03-4000125476 |  | AUD-2026-03-2000010720ACN-2026-03-4000125476 | 21 |  | 26 | 80 | 5 | 5 | 70
|  |  |  | in process | ZONAL VISIT REPORTSHOLAPUR 14&16.03.2026 | 2026-03-16 | AUD-2026-03-2000011316 | 2026-03-14 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125607 | Open | RANA PULKIT | 2026-08-08 | Location is under process to scrap misc. items | 3.9 | Abnormal variations / unused assets reviewed | 1509 | SHOLAPUR TERMINAL | scrap disposal to be completed by 30.04.2026 | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-03-2000011316ACN-2026-03-4000125607 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011316ACN-2026-03-4000125607 | 2026-09-19 | 30.7538 | 241 | >20 | AUD-2026-03-2000011316 - ACN-2026-03-4000125607 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011316ACN-2026-03-4000125607 |  | AUD-2026-03-2000011316ACN-2026-03-4000125607 | 21 |  | 26 | 80 | 0 | 0 | 35
KAUSHIK ANIL | 2026-03-23 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-03-23 | Training to Security guards given on handling emergencies during offshift on 24.02.2026 and 11.03.2026. Hence Complied. | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124090 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-03-23 | Off Shift mock drill conducted on 16.02.2026 at 6 pm. All teams as per offshift plan have actively particpated in the drill. Awareness about Role clarity among Security personnel during off shift hours to be improved | 2.1 | Fire drill conducted in last 6 months (surprise) | 1895 | MANGALORE TERMINAL | Training to Security staff on handling emergency during offshift to be given | SOD | Marketing | SWZ | 2026-03-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-03-2000011174ACN-2026-03-4000124090 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124090 | 2026-07-29 17:00 | 82.0455 | 203 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124090 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011174ACN-2026-03-4000124090 | AUD-2026-03-2000011174ACN-2026-03-4000124090 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 29
KAUSHIK ANIL | 2026-03-23 | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-03-23 | Training to security guards given on TT checks procedure at in/out gates on 24.02.2026 and 11.03.2026. Hence Complied. | SENIOR MANAGEMENT INSPN MANAGLORE TML | 2026-02-16 | AUD-2026-03-2000011174 | 2026-02-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124092 | Closed | PALLIVILLA MANOHAR RAVI NARAYANA | 2026-03-23 | Security entry registers at Vistor gate and hazardous gate checked. Found okay CCTV recoridngs of Security frisking at vistir gateand TT checks before parking area entry checked randomly. Found okay, however scope for improvement found | 2.8 | Access control systems checked | 1895 | MANGALORE TERMINAL | Training to Security staff to be given and ensure proper checks of TT's and Persons at respective gates to be improved. Monitoring to be done. | SOD | Marketing | SWZ | 2026-03-10 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-10 | AUD-2026-03-2000011174ACN-2026-03-4000124092 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011174ACN-2026-03-4000124092 | 2026-07-29 17:00 | 82.0455 | 203 | >20 | AUD-2026-03-2000011174 - ACN-2026-03-4000124092 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011174ACN-2026-03-4000124092 | AUD-2026-03-2000011174ACN-2026-03-4000124092 | 21 | 21 | 26 | 80 | 2 | 2 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Regular self monitoring of Safe 100, samridhhi, cost rationalisation initiative, compliance to circulars and guidelines, expense monitoring & booking, VTS, EM locking and SOPs is being done. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122064 | Closed | KUMAR NITISH | 2026-03-23 | Safe 100, samridhhi, cost rationalisation initiative, compliance to circulars and guidelines, expense monitoring & booking, VTS, EMlocking and SOPs were discussed. | 1.6 | Expectations clearly communicated to officers | 1128 | MATHURA TERMINAL | Regular self monitoring shall be ensured. | SOD | Marketing | NUZ | 2026-03-02 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122064 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122064 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122064 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122064 | AUD-2026-02-2000010909ACN-2026-02-4000122064 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Regular self monitoring ofStock loss in LDO, opex, cycle time, project closure, solar generation, RFDs is being done. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000122065 | Closed | KUMAR NITISH | 2026-03-23 | Stock loss in LDO, opex, cycle time, project closure, solar generation, RFDs to be monitored. | 1.8 | Improvement plans discussed | 1128 | MATHURA TERMINAL | Regular self monitoring shall be ensured. | SOD | Marketing | NUZ | 2026-03-02 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122065 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122065 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122065 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122065 | AUD-2026-02-2000010909ACN-2026-02-4000122065 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Mobile equipment - MEFG, foam pourer has been tested on 23.03.2026 .Necessary repairs done.(Permit no-10000077050) | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122066 | Closed | KUMAR NITISH | 2026-03-23 | Drill conducted in TK24 manifold area and ETP. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1128 | MATHURA TERMINAL | Mobile equipment - MEFG, foam pourer shall be periodically tested to ensure desired performance. | SOD | Marketing | NUZ | 2026-03-02 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122066 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122066 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122066 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122066 | AUD-2026-02-2000010909ACN-2026-02-4000122066 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.A high nos of sprinkler nozzles of Tk24 found choked have been cleaned and servicing done vide permit no.100000747050. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122072 | Closed | KUMAR NITISH | 2026-03-23 | HCD of dyke containing TK24 was check and found functional. HVLR of Tank no 24 was operated by Security and also by officer. Both could operate it properly. A high nos of sprinkler nozzles of Tk24 found choked. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-02 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122072 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122072 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122072 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122072 | AUD-2026-02-2000010909ACN-2026-02-4000122072 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied. Foam pourers of TK 7 has been cleaned and servicing done. Foam is being generated properly .Refer Permit no. 100000747050. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122092 | Closed | KUMAR NITISH | 2026-03-23 | None of the foam pourers generated adequate foam while testing TK7 | 6.4 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122092 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122092 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122092 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122092 | AUD-2026-02-2000010909ACN-2026-02-4000122092 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | MOHAMMAD MAZHARUDDIN | 2026-03-23 | Regular self monitoring is being done and sample pics attached for reference | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122725 | Closed | MOHAMMAD MAZHARUDDIN | 2026-03-23 | Safe 100, samridhhi, cost rationalisation initiative, compliance to circulars and guidelines, expense monitoring & booking, VTS, EMlocking and SOPs were discussed. | 1.6 | Expectations clearly communicated to officers | 1146 | MEERUT DEPOT | Regular self monitoring shall be ensured. | SOD | Marketing | NUZ | 2026-03-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122725 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122725 | 2026-09-25 19:00 | 23.9622 | 203 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122725 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122725 | AUD-2026-03-2000011218ACN-2026-03-4000122725 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 29
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | MOHAMMAD MAZHARUDDIN | 2026-03-23 | Eye sight and CB are checked through TPA. TPA carried out for 100% of TT crew, contract workmen and security guards. Record available at location for each memeber including other medical reports | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122730 | Closed | SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | Facility not available. | 2.16 | Eyesight / colour-blindness awareness checked | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011218ACN-2026-03-4000122730 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122730 | 2026-09-25 19:00 | 23.9622 | 203 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122730 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122730 | AUD-2026-03-2000011218ACN-2026-03-4000122730 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 29
SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | MOHAMMAD MAZHARUDDIN | 2026-03-23 | All valid MOCs are verified and closed as on 23/03/26. | SR MANAGEMENT INSPECTION MRT Q4 25-26 | 2026-03-09 | AUD-2026-03-2000011218 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122736 | Closed | SARANG MEHULKUMAR BHUPENDRABHAI | 2026-03-23 | Total MOC: 23, Open 2 nos. Over due 1 nos. | 3.17 | MOC status reviewed | 1146 | MEERUT DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-25 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000011218ACN-2026-03-4000122736 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011218ACN-2026-03-4000122736 | 2026-09-25 19:00 | 23.9622 | 203 | >20 | AUD-2026-03-2000011218 - ACN-2026-03-4000122736 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011218ACN-2026-03-4000122736 | AUD-2026-03-2000011218ACN-2026-03-4000122736 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied. Location maintains supporting document related to SOP deviation in VA alerts.Refer attachment. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122070 | Closed | KUMAR NITISH | 2026-03-23 | . PPE noncompliance TAS_1128_SOP043_170226_000170 closed with comments Person had been counselled to wear PPE when he enter in license area. 2. TT Crew non availability (TT unloading) TAS_1128_SOP045_200226_000154 closed with comment TT crew was there but not captured in this alert image found valid. | 2.7 | VA alerts checked / analysed | 1128 | MATHURA TERMINAL | Location to maintain supporting document related to SOP deviation in VA alerts. | SOD | Marketing | NUZ | 2026-03-02 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122070 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122070 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122070 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122070 | AUD-2026-02-2000010909ACN-2026-02-4000122070 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Work has been completed. Pumpable water volume is 8354 Kl as against 8280 Kl(OISD 117 requirement).MOC 3100001297 & 3100001455 have been closed. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122071 | Closed | KUMAR NITISH | 2026-03-23 | One of the water storage tank is in under height increase. Work is in stage of completion. Post work completion, adequate water storage will be available at location. | 2.10 | Fire water levels verified | 1128 | MATHURA TERMINAL | Location to complete and recommission the water tank. | SOD | Marketing | NUZ | 2026-02-28 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010909ACN-2026-02-4000122071 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122071 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122071 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122071 | AUD-2026-02-2000010909ACN-2026-02-4000122071 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied. Oil Leaks observed in Fire engine 1, 2 and 3 have been fixed by the vendor in AMC visit. refer attached Service report. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122073 | Closed | KUMAR NITISH | 2026-03-23 | Demonstration of fire monitor, MEFG & foam pourer is done by officer. Location has developed system of checking working of alarms of abnormal temperature, pressure, etc. of lube oils of fire engines, without taking the engines off service Oil Leaks observed in Fire engine 1, 2 and 3. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1128 | MATHURA TERMINAL | Leaks shall be arrested. | SOD | Marketing | NUZ | 2026-03-05 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010909ACN-2026-02-4000122073 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122073 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122073 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122073 | AUD-2026-02-2000010909ACN-2026-02-4000122073 | 21 | 21 | 26 | 80 | 14 | 13 | 27 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Earthpit no 223 of transformer yard fencing had improper clamp and connection (single bolt).The same has been fixed .Double bolting done vide permit no-100000741531. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122083 | Closed | KUMAR NITISH | 2026-03-23 | Earthpits 220 and 221 were checked. Resistance found as 0.4 and 0.6 Ohms, respectively, in grid, against last checked data of 0.43 and 0.82 respectively, measured in Sept 25. Earthpit no 223 of transformer yard fencing had improper clamp and connection (single bolt). | 3.16 | Earth pits / boundary / vegetation control checked | 1128 | MATHURA TERMINAL | Corrective action to be taken. | SOD | Marketing | NUZ | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122083 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122083 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122083 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122083 | AUD-2026-02-2000010909ACN-2026-02-4000122083 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Railing of Crossover between Tk07 and Tk24 fire wall had no middle level flat.Same has been repaired. vide permit no-100000741049. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122094 | Closed | KUMAR NITISH | 2026-03-23 | Railing of Crossover between Tk07 and Tk24 fire wall has no middle level flat. | 6.6 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122094 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122094 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122094 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122094 | AUD-2026-02-2000010909ACN-2026-02-4000122094 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied. For the LDO line touching fire water line near crossing wooden wedge has been placed and separation ensured. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | ADDITIONAL OBSERVATION | ACN-2026-02-4000122096 | Closed | KUMAR NITISH | 2026-03-23 | LDO line was found touching fire water line near crossing. | 6.8 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122096 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122096 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122096 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122096 | AUD-2026-02-2000010909ACN-2026-02-4000122096 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
ARYA VIPIN KUMAR | 2026-03-23 | DAS DARSHAN | 2026-03-23 | Cross over provided near collection pit 1 of OWS in siding area | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122677 | Closed | DAS DARSHAN | 2026-03-23 | Cross over to be provided near collection pit 1. | 6.10 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122677 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122677 | 2026-09-03 | 46.7538 | 203 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122677 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122677 | AUD-2026-03-2000011009ACN-2026-03-4000122677 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.TT No. UP85FT8477 & UP86T7480 found with excess dip at TT Gantry were reverified at calibration tower on 25.02.26 & 13.03.26 respectively . Dip of both TTs were found within permissible limit | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122076 | Closed | KUMAR NITISH | 2026-03-23 | Excess dip observed in few TTs at gantry. Details attached as annexure 1. | 3.2 | Post-loading dip checks verified | 1128 | MATHURA TERMINAL | Bay verification and rechecking of TT calibration shall be carried out. | SOD | Marketing | NUZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010909ACN-2026-02-4000122076 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122076 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122076 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122076 | AUD-2026-02-2000010909ACN-2026-02-4000122076 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
ARYA VIPIN KUMAR | 2026-03-23 | DAS DARSHAN | 2026-03-23 | Settled paver in ethanol unloading TT gantry have been repaired | SR MANAGEMENT INSPECTION LKO Q4 25-26 | 2026-01-30 | AUD-2026-03-2000011009 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000122669 | Closed | DAS DARSHAN | 2026-03-23 | Location to arrange to repair of settled paver in ethanol unloading TT gantry. | 6.2 |  | 1292 | LUCKNOW DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011009ACN-2026-03-4000122669 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011009ACN-2026-03-4000122669 | 2026-09-03 | 46.7538 | 203 | >20 | AUD-2026-03-2000011009 - ACN-2026-03-4000122669 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011009ACN-2026-03-4000122669 | AUD-2026-03-2000011009ACN-2026-03-4000122669 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Smoke detector has been installed and commissioned and integrated with TAS Refer Permit no-100000738627 Dt 12.03.2026 | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-02-4000122088 | Closed | KUMAR NITISH | 2026-03-23 | Control room smoke detector not functioning | 5.2 | Functioning of all Hooters in control room | 1128 | MATHURA TERMINAL | Control room smoke detector functionality to be restored. | SOD | Marketing | NUZ | 2026-03-10 | INSTRUMENTATION OR ALARM FAILURES | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122088 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122088 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122088 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122088 | AUD-2026-02-2000010909ACN-2026-02-4000122088 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
JHA PANKAJ KUMAR | 2026-03-23 | KUMAR NITISH | 2026-03-23 | Complied.Cable has been laid and Emregency stop provided for HSD at Gantry 2 Refer permit no. 100000736992 Dt 12.0.2026. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122089 | Closed | KUMAR NITISH | 2026-03-23 | Emergency stop not available for HSD at Gantry 2. | 6.1 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | EMERGENCY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122089 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122089 | 2026-09-18 | 31.7538 | 203 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122089 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122089 | AUD-2026-02-2000010909ACN-2026-02-4000122089 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 29
MEPPARAMBIL UNNI PRAVEENKUMAR | 2026-03-23 | M.RAJKUMAR | 2026-03-23 | LIC has taken resposibility to ensure for gouding the new officers as well as for knowledge transfer. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122601 | Closed | M.RAJKUMAR | 2026-03-23 | Interacted openly with all Officers and found them motivated with interest to perfrom well | 1.1 | Interaction with all officers (1–1.5 hrs) | 1856 | COIMBATORE DEPOT | Considering that DPC list may be published shortly the Location In-Charge (LIC) and senior officers were directed to prioritize comprehensive knowledge sharing. This will ensure seamless operational continuity. | SOD | Marketing | SZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000010712ACN-2026-03-4000122601 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122601 | 2026-08-28 17:00 | 52.0455 | 203 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122601 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010712ACN-2026-03-4000122601 | AUD-2026-03-2000010712ACN-2026-03-4000122601 | 21 | 21 | 26 | 80 | 0 | 1 | 31 | 29
MEPPARAMBIL UNNI PRAVEENKUMAR | 2026-03-23 | M.RAJKUMAR | 2026-03-23 | GM SZ had taken review of the activites of each location on 17.03.2026 and the status of the all activites and KPI has been discussed in detail. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122602 | Closed | M.RAJKUMAR | 2026-03-23 | Reviewed perfromance of all Officers and officeres were found focussed on the Goals and Targets with emphasis on process/efficiencyimprovement | 1.2 | Performance review conducted | 1856 | COIMBATORE DEPOT | Team to focus on G&T for the year and come up with improvements proces and work efficency | SOD | Marketing | SZ | 2026-03-31 | POOR COMMUNICATION | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-03-2000010712ACN-2026-03-4000122602 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122602 | 2026-08-28 17:00 | 52.0455 | 203 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122602 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010712ACN-2026-03-4000122602 | AUD-2026-03-2000010712ACN-2026-03-4000122602 | 21 | 21 | 26 | 80 | 0 | 1 | 31 | 29
MEPPARAMBIL UNNI PRAVEENKUMAR | 2026-03-23 | M.RAJKUMAR | 2026-03-23 | Location had put back the non functional cameras into operation. All cameras are in working condition. | COIMBATORE IRD VISIT REPORT UPLOADIN SAP | 2026-02-12 18:30 | AUD-2026-03-2000010712 | 2026-02-12 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122606 | Closed | M.RAJKUMAR | 2026-03-23 | CCTV Infrastructure: Out of 53 total cameras, 42 units are fully operational and monitored daily. Location is maintaining register for CCTV monitoring. 11 units are currently non-functional due to cable damage sustained during lube warehouse construction by LubesSBU. Cochin Lube RO has already placed the PO for cable replacement with an Estimated Date of Completion (EDC) of 20.02.2026. Spokewith RM of Cochin Lubes RO to expedite the work. CRM ensured that work will commence from 16.02.2025 and will be completed at the earliest. | 2.6 | CCTV functioning checked | 1856 | COIMBATORE DEPOT | Location to put back the non functional cameras into operation in coordination with Lubes SBU | SOD | Marketing | SZ | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S2 | F3 | 2026-02-28 | AUD-2026-03-2000010712ACN-2026-03-4000122606 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010712ACN-2026-03-4000122606 | 2026-08-28 17:00 | 52.0455 | 203 | >20 | AUD-2026-03-2000010712 - ACN-2026-03-4000122606 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010712ACN-2026-03-4000122606 | AUD-2026-03-2000010712ACN-2026-03-4000122606 | 21 | 21 | 26 | 80 | 0 | 1 | 26 | 29
SINGH SOURABH | 2026-03-25 | SINGH BHOPENDRA | 2026-03-25 | Location monitoring the VTS, MEB expense & booking and regulate the expense as per approved budget. Location reduced the 3 secuirtymanpower under samridhi cost saving initative. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124792 | Closed | SINGH BHOPENDRA | 2026-03-25 | Safe 100, samridhhi, cost rationalisation initiative, compliance to circulars and guidelines, expense monitoring & booking, VTS, EMlocking and SOPs were discussed. | 1.6 | Expectations clearly communicated to officers | 1157 | BAREILLY DEPOT | Regular self monitoring shall be ensured. | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124792 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124792 | 2026-07-16 | 95.7538 | 205 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124792 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124792 | AUD-2026-03-2000011014ACN-2026-03-4000124792 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 30
SINGH SOURABH | 2026-03-25 | SINGH BHOPENDRA | 2026-03-25 | 1. Traning provided to operation for operation of DCP and other fire figting facility at location. 2. Field traning provided to secuirty for movement of TT in case of emergency & ensured fire clock direction. 3. location call the mutual aid member they recahed the site during fire drill conduted at location at T4S audit on 23.03.2026 reached the site on time. 4. location verified the sequence of event & these are as per SOP. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124794 | Closed | SINGH BHOPENDRA | 2026-03-25 | 1. Date 10.03.2026 2. Area of drill conducted: Inside depot premises 3. Scenario covered: Fire in UG tank farm pit (Ethanol leakage) 4. Double/single Contingency: Single contingency 5. Observations : Communications by team to Fire chief to be improved Training shall be conducted on operation of DCP. Difficulty faced by user in operating HVLR valves. Location to review and conduct more training and session with security/TT crew for evacuation from gantry. Location shall call mutual aid member during mock drill tocheck response time and preparedness. Location to check and verify the sequence of events and shutdown of depot premises. Location to check and verify the cause and effect in field. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124794 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124794 | 2026-07-16 | 95.7538 | 205 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124794 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124794 | AUD-2026-03-2000011014ACN-2026-03-4000124794 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 30
SINGH SOURABH | 2026-03-25 | SINGH BHOPENDRA | 2026-03-25 | Location is monitoring the stock loss, project expense & sharing the details to zone. Location disposed off the 10 MT mis. MS scrap, 200 Nos foam drums, 20 lts foam drums & old VFD. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124793 | Closed | SINGH BHOPENDRA | 2026-03-25 | Stock loss, opex, cycle time, project closure, solar generation, RFDs to be monitored. | 1.8 | Improvement plans discussed | 1157 | BAREILLY DEPOT | Regular self monitoring shall be ensured. | SOD | Marketing | NUZ | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011014ACN-2026-03-4000124793 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124793 | 2026-07-16 | 95.7538 | 205 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124793 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124793 | AUD-2026-03-2000011014ACN-2026-03-4000124793 | 21 | 21 | 26 | 80 | 3 | 3 | 31 | 30
SINGH SOURABH | 2026-03-25 | SINGH BHOPENDRA | 2026-03-25 | All Fire Engine has been working fine as of now, leakage observed from cooling pipe same has been repalced and no lekage observed. | SR MANAGEMENT INSPECTION BRL Q4 25-26 | 2026-03-10 | AUD-2026-03-2000011014 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124799 | Closed | SINGH BHOPENDRA | 2026-03-25 | HVLR 4 of TK4 was operated by Ku Sakshi Gond properly. FE no 01 found be having issue of leaking. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1157 | BAREILLY DEPOT | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-15 | FATIGUE AND STRESS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011014ACN-2026-03-4000124799 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011014ACN-2026-03-4000124799 | 2026-07-16 | 95.7538 | 205 | >20 | AUD-2026-03-2000011014 - ACN-2026-03-4000124799 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011014ACN-2026-03-4000124799 | AUD-2026-03-2000011014ACN-2026-03-4000124799 | 21 | 21 | 26 | 80 | 3 | 3 | 28 | 30
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127129 | Open |  |  | VRU PESO approval, night loading approval, Budgets approval for Hydrant valves | 1.3 | Pending issues reviewed | 1585 | MAHUL TERMINAL | Location to take up with PESO for aprovals and HQO for funds | SOD | Marketing | WZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127129 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127129 | 2026-10-17 | 2.7538 | 241 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127129 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127129 |  | AUD-2026-03-2000010975ACN-2026-03-4000127129 | 21 |  | 26 | 80 | 28 | 28 | 35
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127132 | Open |  |  | Pumps in surplues | 3.9 | Abnormal variations / unused assets reviewed | 1585 | MAHUL TERMINAL | Communication to be sent to HQO on idlig assets | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127132 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127132 | 2026-10-17 | 2.7538 | 241 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127132 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127132 |  | AUD-2026-03-2000010975ACN-2026-03-4000127132 | 21 |  | 26 | 80 | 28 | 28 | 35
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127134 | Open |  |  | Vegetation seen almost all areas. Earth pit stickers outdated | 3.16 | Earth pits / boundary / vegetation control checked | 1585 | MAHUL TERMINAL | Housekeeping to done, Earth pit stickers to be changed | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127134 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127134 | 2026-10-17 | 2.7538 | 241 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127134 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127134 |  | AUD-2026-03-2000010975ACN-2026-03-4000127134 | 21 |  | 26 | 80 | 28 | 28 | 35
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127135 | Open |  |  | Yes, CCTV storage back up MOC, Close looping of hydrant line and valves for hydrant line | 3.17 | MOC status reviewed | 1585 | MAHUL TERMINAL | To be taken up with HQO for funds , spares | SOD | Marketing | WZ | 2026-09-30 |  | 4 |  | S1 | F4 | 2026-09-30 | AUD-2026-03-2000010975ACN-2026-03-4000127135 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127135 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127135 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127135 |  | AUD-2026-03-2000010975ACN-2026-03-4000127135 | 21 |  | 26 | 80 | 28 | 28 | 57
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127136 | Open |  |  | YES, painting overdue, structures rusted, scrap scattered, lot spare pumps available | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1585 | MAHUL TERMINAL | Painting over due, struct | SOD | Marketing | WZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-03-2000010975ACN-2026-03-4000127136 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127136 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127136 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127136 |  | AUD-2026-03-2000010975ACN-2026-03-4000127136 | 21 |  | 26 | 80 | 28 | 28 | 57
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127137 | Open |  |  | YES, leakages seen, lot of rusting. Structural damages, pumps to repaired | 4.2 | Maintenance activities reviewed | 1585 | MAHUL TERMINAL | M&R activity to be streamlines. Dedciated officer for M&R | SOD | Marketing | WZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-03-2000010975ACN-2026-03-4000127137 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127137 | 2026-10-17 | 2.7538 | 394 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127137 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127137 |  | AUD-2026-03-2000010975ACN-2026-03-4000127137 | 21 |  | 26 | 80 | 28 | 28 | 57
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127138 | Open |  |  | Scrap lying at various places | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1585 | MAHUL TERMINAL | Segreagation shall be done, lots to be made and disposal to be done immediately | SOD | Marketing | WZ | 2026-04-30 |  | 4 |  | S1 | F4 | 2026-04-30 | AUD-2026-03-2000010975ACN-2026-03-4000127138 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127138 | 2026-10-17 | 2.7538 | 241 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127138 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127138 |  | AUD-2026-03-2000010975ACN-2026-03-4000127138 | 21 |  | 26 | 80 | 28 | 28 | 35
[5 empty] | ZONE VISIT REPORT MAHUL 09.03.2026 | 2026-03-09 | AUD-2026-03-2000010975 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-03-4000127139 | Open |  |  | All are workinhg except Dyke drain | 5.2 | Functioning of all Hooters in control room | 1585 | MAHUL TERMINAL | Dyke drains hooters to be made functional | SOD | Marketing | WZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010975ACN-2026-03-4000127139 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010975ACN-2026-03-4000127139 | 2026-10-17 | 2.7538 | 302 | >20 | AUD-2026-03-2000010975 - ACN-2026-03-4000127139 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010975ACN-2026-03-4000127139 |  | AUD-2026-03-2000010975ACN-2026-03-4000127139 | 21 |  | 26 | 80 | 28 | 28 | 44
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Continuous monitering is done by TAS officer and is reriewed by LIC | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121366 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlier VC's with all Location TAS officer. | 1.8 | Improvement plans discussed | 1334 | HPCL REWARI IRD | Daily monitoring of TT exit time and LPM for improvement. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011004ACN-2026-02-4000121366 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121366 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121366 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121366 | AUD-2026-02-2000011004ACN-2026-02-4000121366 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Continuous monitering is done by TAS officer and is reriewed by LIC and record is being maintained | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000121658 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | 1. TAS officer to focus on improvement of TT exit time and LPM for the location as per the advice given by Zone through earlier VC's with all Location TAS officer. 2. Live VTS monitoring to be done and record maintained as per circular. 3. EM locking check to be done as per circular and record as per Annexure I of circular to be maintained | 1.8 | Improvement plans discussed | 1334 | HPCL REWARI IRD | 1. Daily monitoring of TT exit time and LPM for improvement. 2. Live VTS monitoring to be done and record maintained as per circular. 3. EM locking check to be done as per circular and record as per Annexure I of circular to be maintained | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121658 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121658 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121658 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121658 | AUD-2026-03-2000011158ACN-2026-03-4000121658 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | a) Fire Axe has been made available at the emergency trolly b) Electrical hand Gloves have been kept on in the emergency trolly | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121659 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Last Fire mock drill conducted on 29/01/2026 @ 1610 hours at Rewari IRD considering scenerio on Electrical Fire in MCC room due to short circuit. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1334 | HPCL REWARI IRD | a) Fire Axe to be made available at the site b) Electrical hand Gloves to be kept on standby | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121659 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121659 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121659 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121659 | AUD-2026-03-2000011158ACN-2026-03-4000121659 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | a) Fire Axe has been made available at the emergency trolly b) Electrical hand Gloves have been kept on in the emergency trolly | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121367 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Last Fire mock drill conducted on 29/01/2026 @ 1610 hours at Rewari IRD considering scenerio on Electrical Fire in MCC room due to short circuit. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1334 | HPCL REWARI IRD | a) Fire Axe to be made available at the site b) Electrical hand Gloves to be kept on standby | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121367 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121367 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121367 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121367 | AUD-2026-02-2000011004ACN-2026-02-4000121367 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | cleaning of both the tanks has been completed ias per approved MoC. | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121663 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | The minimum fire water requirement for the location is 3600 KL. At present, the location has 2712 KL of fire water available in thefire water tanks. Two tanks are under outage for cleaning, as per MoC No. 3100001505 dated 29/12/2025. The location has also informed its Mutual Aid partners (IOC, BPC, etc.) regarding the same vide letter no. HPCL/Fact/RT/01 dated 05/01/2026. | 2.10 | Fire water levels verified | 1334 | HPCL REWARI IRD | Cleaning of both the tanks to be completed in time bound manner as per approved MoC. Closure of MocC to be ensured after work is over. | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011158ACN-2026-03-4000121663 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121663 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121663 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121663 | AUD-2026-03-2000011158ACN-2026-03-4000121663 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | cleaning of both the tanks has been completed ias per approved MoC. | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121371 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | The minimum fire water requirement for the location is 3600 KL. At present, the location has 2712 KL of fire water available in thefire water tanks. Two tanks are under outage for cleaning, as per MoC No. 3100001505 dated 29/12/2025. The location has also informed its Mutual Aid partners (IOC, BPC, etc.) regarding the same vide letter no. HPCL/Fact/RT/01 dated 05/01/2026. | 2.10 | Fire water levels verified | 1334 | HPCL REWARI IRD | Cleaning of both the tanks to be completed in time bound manner as per approved MoC. Closure of MocC to be ensured after work is over. | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011004ACN-2026-02-4000121371 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121371 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121371 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121371 | AUD-2026-02-2000011004ACN-2026-02-4000121371 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Front LED Light of TK-03, TK-05 have been made functional. HMT-2 - LED lights is working now | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121368 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Lux Level checked during night inspection on 10th Feb 2026 at Various points in locations a) TT Gantry - 120 Lux b) Fire pump house - 92 lux c) DG Set Area - 30 lux d) Security Guard room - 355 Lux e) MCC Room - 231 Lux f) Pump House - 250 lux g) TK-03 near ROSOV - 189 lux h) Scrap yard - 13 Lux i) TK-13 near ROSOV - 161 Lux j) Admin Building - 300 Lux k) Roads - 26 Lux l) Front LED Light of TK-03, TK-05 are not working along with HMT-2 lights are blinking. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1334 | HPCL REWARI IRD | l) Front LED Light of TK-03, TK-05 to be made functional. HMT-2 - LED lights to be checked for its proper functioning | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121368 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121368 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121368 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121368 | AUD-2026-02-2000011004ACN-2026-02-4000121368 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Front LED Light of TK-03, TK-05 have been made functional. HMT-2 - LED lights is working now | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121660 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Lux Level checked during night inspection on 10th Feb 2026 at Various points in locations a) TT Gantry - 120 Lux b) Fire pump house - 92 lux c) DG Set Area - 30 lux d) Security Guard room - 355 Lux e) MCC Room - 231 Lux f) Pump House - 250 lux g) TK-03 near ROSOV - 189 lux h) Scrap yard - 13 Lux i) TK-13 near ROSOV - 161 Lux j) Admin Building - 300 Lux k) Roads - 26 Lux l) Front LED Light of TK-03, TK-05 are not working along with HMT-2 lights are blinking. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1334 | HPCL REWARI IRD | l) Front LED Light of TK-03, TK-05 to be made functional. HMT-2 - LED lights to be checked for its proper functioning | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121660 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121660 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121660 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121660 | AUD-2026-03-2000011158ACN-2026-03-4000121660 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Location is maintaining record of surperise night Inspection along with entrie in Gate register about visits done | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121661 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Surprise visit was done at terminal around 23:39 hours and fould all security guards in alert position. Security shift was headed by Sup Anup Singh along with Guards Mahipal, Karanveer & Satyanand. Further, location is not maintaining records of Surprise night inspection done. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1334 | HPCL REWARI IRD | Location to maintain record of surperise night Inspection along with entried in Gate register about visits done | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121661 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121661 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121661 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121661 | AUD-2026-03-2000011158ACN-2026-03-4000121661 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Location is maintaining record of surperise night Inspection along with entrie in Gate register about visits done | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121369 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Surprise visit was done at terminal around 23:39 hours and fould all security guards in alert position. Security shift was headed by Sup Anup Singh along with Guards Mahipal, Karanveer & Satyanand. Further, location is not maintaining records of Surprise night inspection done. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1334 | HPCL REWARI IRD | Location to maintain record of surperise night Inspection along with entried in Gate register about visits done | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000011004ACN-2026-02-4000121369 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121369 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121369 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121369 | AUD-2026-02-2000011004ACN-2026-02-4000121369 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Correction made | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000121662 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | On-Site Mock Fire Drill (Single contingency) as well as Off-Shift Hour Mock Fire Drill was carried out on 11th Feb 2026 and 12th Feb 2026 resp. Positives during both the drills were timely & efficient operation of all safety equipment including sprinklers and foam pourers, HVLRs and response time by all members of fire drill. (Detailed Fire Drill Reports Annexed along with this report). | 2.5 | Emergency response preparedness reviewed | 1334 | HPCL REWARI IRD | Leakage od Foam pick up line of FM-16 is to be arrested. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121662 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121662 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121662 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121662 | AUD-2026-03-2000011158ACN-2026-03-4000121662 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Correction made | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121370 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | On-Site Mock Fire Drill (Single contingency) as well as Off-Shift Hour Mock Fire Drill was carried out on 11th Feb 2026 and 12th Feb 2026 resp. Positives during both the drills were timely & efficient operation of all safety equipment including sprinklers and foam pourers, HVLRs and response time by all members of fire drill. (Detailed Fire Drill Reports Annexed along with this report). | 2.5 | Emergency response preparedness reviewed | 1334 | HPCL REWARI IRD | Leakage od Foam pick up line of FM-16 is to be arrested. | SOD | Marketing | NZ | 2026-03-12 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-12 | AUD-2026-02-2000011004ACN-2026-02-4000121370 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121370 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121370 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121370 | AUD-2026-02-2000011004ACN-2026-02-4000121370 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | TT inspections to being carried out as per circular. | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121666 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Thorough checking TT No HR47D6424 was done along with LIC and concerned officer to sensitize the need for proper inspection of TTs in line with the extant circular. Fire extinguisher of TT No. HR55AK8669 operated by the TT Driver and was found satisfactory | 3.1 | TT fittings & discipline checked | 1334 | HPCL REWARI IRD | Compliance of the observation made w.r.t. TT inspected to ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-03-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-03-2000011158ACN-2026-03-4000121666 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121666 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121666 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121666 | AUD-2026-03-2000011158ACN-2026-03-4000121666 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | TT inspections to being carried out as per circular. | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121374 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Thorough checking TT No HR47D6424 was done along with LIC and concerned officer to sensitize the need for proper inspection of TTs in line with the extant circular. Fire extinguisher of TT No. HR55AK8669 operated by the TT Driver and was found satisfactory | 3.1 | TT fittings & discipline checked | 1334 | HPCL REWARI IRD | Compliance of the observation made w.r.t. TT inspected to ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121374 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121374 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121374 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121374 | AUD-2026-02-2000011004ACN-2026-02-4000121374 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | PO placed for 3 month extension of CAMC on M/s Advanced Systek , also process initiated for 1 year AMC on M/s Advanced Systek | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121380 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Avg. TFMS-SAP reconciliation % for the period Oct'25 to Jan'26 is 96%. The existing CAMC contract of the location is valid only till 22nd March 2026 and location has not originated any LPR so far, for renewal of CAMC contract / placement of new AMC contract. | 3.10 | TFMS/SAP reconciliation checked | 1334 | HPCL REWARI IRD | b) Location to initiate process for finalization of CAMC / AMC contract for TAS | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121380 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121380 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121380 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121380 | AUD-2026-02-2000011004ACN-2026-02-4000121380 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | PO placed for 3 month extension of CAMC on M/s Advanced Systek , also process initiated for 1 year AMC on M/s Advanced Systek | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121672 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Avg. TFMS-SAP reconciliation % for the period Oct'25 to Jan'26 is 96%. The existing CAMC contract of the location is valid only till 22nd March 2026 and location has not originated any LPR so far, for renewal of CAMC contract / placement of new AMC contract. | 3.10 | TFMS/SAP reconciliation checked | 1334 | HPCL REWARI IRD | b) Location to initiate process for finalization of CAMC / AMC contract for TAS | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121672 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121672 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121672 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121672 | AUD-2026-03-2000011158ACN-2026-03-4000121672 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Taken up with pipeline | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121381 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Verified last 3 months TAS alerts in NOVEX portal on 11.02.2026 @ 16:41 hrs. and only 1 critical open alerts of Tank Leakage Alarmswere found which are related to tank no. TK16 which is slop tank in the custody of Pipelines Group. | 3.12 | Critical alarms checked & corrective actions reviewed | 1334 | HPCL REWARI IRD | Location has been advised to take up with pipelines officials to put the tanks under dormant mode after completion of PLTs after giving minimum 45’ product settling time to avoid such false “Tank Leakage Alarms”. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121381 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121381 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121381 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121381 | AUD-2026-02-2000011004ACN-2026-02-4000121381 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Taken up with pipeline | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121673 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Verified last 3 months TAS alerts in NOVEX portal on 11.02.2026 @ 16:41 hrs. and only 1 critical open alerts of Tank Leakage Alarmswere found which are related to tank no. TK16 which is slop tank in the custody of Pipelines Group. | 3.12 | Critical alarms checked & corrective actions reviewed | 1334 | HPCL REWARI IRD | Location has been advised to take up with pipelines officials to put the tanks under dormant mode after completion of PLTs after giving minimum 45’ product settling time to avoid such false “Tank Leakage Alarms”. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121673 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121673 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121673 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121673 | AUD-2026-03-2000011158ACN-2026-03-4000121673 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Complied | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121382 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Housekeeping - Housekeeping of the location is found to be Satisfactory with some areas requireing minor upkeep which were discussed during field round with location team.. PPE - During visit it was observed that all Contract workers along with Officers are adhering to guidelines of PPE usage and adequate no of PPE's available at the location. List of PPE available at location is enclosed. | 3.15 | Housekeeping & PPE usage checked | 1334 | HPCL REWARI IRD | a) Immediate | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121382 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121382 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121382 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121382 | AUD-2026-02-2000011004ACN-2026-02-4000121382 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Complied | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121674 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Housekeeping - Housekeeping of the location is found to be Satisfactory with some areas requireing minor upkeep which were discussed during field round with location team.. PPE - During visit it was observed that all Contract workers along with Officers are adhering to guidelines of PPE usage and adequate no of PPE's available at the location. List of PPE available at location is enclosed. | 3.15 | Housekeeping & PPE usage checked | 1334 | HPCL REWARI IRD | a) Immediate | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121674 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121674 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121674 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121674 | AUD-2026-03-2000011158ACN-2026-03-4000121674 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | concertina coil near pipeline area has been repaired | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121383 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Earth Pits - Total 207 Nos Earth pits are there at the location. Earth Pit No 137 & 27 Checked and Found Individual and Grid Reading as mentioned Individual Reading of EP 137 - 1.05 Ω Grid Reading of EP-137 - 0.45 Ω Individual Reading of EP 27 - 1.84 Ω Grid Reading of EP-27 - 0.42 Ω Boundary Wall - The condition of the boundary wall has been found satisfactory, and the concertina coilplaced along the periphery is intact except one spot which is near pipeline area. Needs rectification. However, provision of brokenglass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. Vegetation Control -No Encroaching/Overgrown vegetation observed. Vegetaion is under control at the location | 3.16 | Earth pits / boundary / vegetation control checked | 1334 | HPCL REWARI IRD | a) concertina coil near pipeline area to be repaired | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121383 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121383 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121383 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121383 | AUD-2026-02-2000011004ACN-2026-02-4000121383 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | concertina coil near pipeline area has been repaired | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121675 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Earth Pits - Total 207 Nos Earth pits are there at the location. Earth Pit No 137 & 27 Checked and Found Individual and Grid Reading as mentioned Individual Reading of EP 137 - 1.05 Ω Grid Reading of EP-137 - 0.45 Ω Individual Reading of EP 27 - 1.84 Ω Grid Reading of EP-27 - 0.42 Ω Boundary Wall - The condition of the boundary wall has been found satisfactory, and the concertina coilplaced along the periphery is intact except one spot which is near pipeline area. Needs rectification. However, provision of brokenglass topping on the boundary wall is proposed as an additional security measure to deter unauthorized entry. Vegetation Control -No Encroaching/Overgrown vegetation observed. Vegetaion is under control at the location | 3.16 | Earth pits / boundary / vegetation control checked | 1334 | HPCL REWARI IRD | a) concertina coil near pipeline area to be repaired | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121675 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121675 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121675 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121675 | AUD-2026-03-2000011158ACN-2026-03-4000121675 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Timely intiation and closure of MOC will be being taken care | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121384 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | During FY 2025-26, Total 41 Nos of MoC's were raised and 39 MoC's were approved. Only One MoC of Fire alarm Panel installation is in open state and One is having technical issue. One MoC is in open condition due to system error. ITSM issue has been logged by the location vide Ref No: 8000082337 & another MoC is under approval stage. | 3.17 | MOC status reviewed | 1334 | HPCL REWARI IRD | ITSM issue to be resolved and location to get MoC approval. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121384 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121384 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121384 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121384 | AUD-2026-02-2000011004ACN-2026-02-4000121384 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Timely intiation and closure of MOC will be being taken care | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121676 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | During FY 2025-26, Total 41 Nos of MoC's were raised and 39 MoC's were approved. Only One MoC of Fire alarm Panel installation is in open state and One is having technical issue. One MoC is in open condition due to system error. ITSM issue has been logged by the location vide Ref No: 8000082337 & another MoC is under approval stage. | 3.17 | MOC status reviewed | 1334 | HPCL REWARI IRD | ITSM issue to be resolved and location to get MoC approval. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121676 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121676 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121676 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121676 | AUD-2026-03-2000011158ACN-2026-03-4000121676 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | a) TE for PNGRB T4S Audit to be completed b) PO will be placed after CPBG submission of party | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121677 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | OISD Status - The OISD audit was conducted from 07th May 2025 to 09th May 2025, during which a total of 27 observations were raised. All observations have been complied with in a time-bound manner, and no observations are pending as of date. MDSA/Comprehensive Status - Comphrensive Audit was conducted from 19th Nov to 22nd Nov 2025 , during which 80 observations were raised. Out of 80 observations 48 observations were closed and 31 are pending. Self Safety Audit Status - Self safety Audit was conducted from 03 Sep to 8th Sep, during which 41 observations were raised. Out of 41 observations 40 observations were closed and 01 is pending. Also PNGRB T4S Audit Status - T4S is scheduled to be conducted in the month of march. Technical evaluation isunder progress. By 20th Feb PO will be placed post finalization of L1 Bidder. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1334 | HPCL REWARI IRD | a) TE for PNGRB T4S Audit to be completed b) PO placement to be done | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121677 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121677 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121677 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121677 | AUD-2026-03-2000011158ACN-2026-03-4000121677 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | a) TE for PNGRB T4S Audit to be completed b) PO will be placed after CPBG submission of party | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121385 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | OISD Status - The OISD audit was conducted from 07th May 2025 to 09th May 2025, during which a total of 27 observations were raised. All observations have been complied with in a time-bound manner, and no observations are pending as of date. MDSA/Comprehensive Status - Comphrensive Audit was conducted from 19th Nov to 22nd Nov 2025 , during which 80 observations were raised. Out of 80 observations 48 observations were closed and 31 are pending. Self Safety Audit Status - Self safety Audit was conducted from 03 Sep to 8th Sep, during which 41 observations were raised. Out of 41 observations 40 observations were closed and 01 is pending. Also PNGRB T4S Audit Status - T4S is scheduled to be conducted in the month of march. Technical evaluation isunder progress. By 20th Feb PO will be placed post finalization of L1 Bidder. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1334 | HPCL REWARI IRD | a) TE for PNGRB T4S Audit to be completed b) PO placement to be done | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121385 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121385 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121385 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121385 | AUD-2026-02-2000011004ACN-2026-02-4000121385 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | File note submitted | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121375 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Post loading dip checks were performed on HR55AC3202, HR55AC6133, HR47E5124, HR47D1002, HR55AB 3675 and found Ok. Location is currently carrying out 100% dip checks for all the TTs & will submitte proposal for 100% dip elimination on 23rd Feb 2026, in line with the circular. | 3.2 | Post-loading dip checks verified | 1334 | HPCL REWARI IRD | Proposal for Dip elemination to be submitted by the Location | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121375 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121375 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121375 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121375 | AUD-2026-02-2000011004ACN-2026-02-4000121375 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | File note submiited | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121667 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Post loading dip checks were performed on HR55AC3202, HR55AC6133, HR47E5124, HR47D1002, HR55AB 3675 and found Ok. Location is currently carrying out 100% dip checks for all the TTs & will submitte proposal for 100% dip elimination on 23rd Feb 2026, in line with the circular. | 3.2 | Post-loading dip checks verified | 1334 | HPCL REWARI IRD | Proposal for Dip elemination to be submitted by the Location | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121667 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121667 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121667 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121667 | AUD-2026-03-2000011158ACN-2026-03-4000121667 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Whatsapp group already created for sharing of information. | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121386 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | 1) Lack of Co-ordination : Dealers raised concern that at times they are not able to contact to depot officials to address their queries. To address this, it was suggested that field officers should make separate whatsapp group for their sales area with depot officials part of it and raising their concerns in that group to make it more streamline 2) Shortage in TT : Dealer enquired whether shortage in underground tank can be reported. GM O&D cleared their confusion by stating that only shortage of Tank truck can be booked. But if repeated shortage in underground tank is reported in case of same TT, TT calibration to be rechecked at Depot 3) VTS blocking of TT : DCT transporters enquired about issue of VTS blocking. GM O&D suggested them that TT if loaded does not follow approvedroute, it will get blocked. If transporters feel there is issue with approved route, they may get it changed from field officer with the help of terminal officials. 4) Late reporting of DCT : DCT Transporters were advised to get their TT reported by 3:30 Pm , sothat Terminal operation can be closed timely and night driving can be avoided. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1334 | HPCL REWARI IRD | 1. Whatsapp group to be created for sharing of information. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121386 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121386 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121386 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121386 | AUD-2026-02-2000011004ACN-2026-02-4000121386 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Noted and 20% blending is done and monitered on daily basis | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121376 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Blending of Ethanol is being done @ 19.8%- Location has been advised to achieve 20% as per guidelines | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1334 | HPCL REWARI IRD | Blending to be achieved @ 20% | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121376 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121376 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121376 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121376 | AUD-2026-02-2000011004ACN-2026-02-4000121376 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Whatsapp group already created for sharing of information. | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121678 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | 1) Lack of Co-ordination : Dealers raised concern that at times they are not able to contact to depot officials to address their queries. To address this, it was suggested that field officers should make separate whatsapp group for their sales area with depot officials part of it and raising their concerns in that group to make it more streamline 2) Shortage in TT : Dealer enquired whether shortage in underground tank can be reported. LIC clarified by stating that only shortage of Tank truck can be booked. But if repeated shortage in underground tank is reported in case of same TT, TT calibration to be rechecked at Depot 3) VTS blocking of TT : DCT transporters enquired about issue of VTS blocking. GM O&D suggested them that TT if loaded does not follow approved route, it will get blocked. If transporters feel there is issue with approved route, they may get it changed from field officer with the help of terminal officials. 4) Late reporting of DCT : DCT Transporters were advised to get their TT reported by 3:30 Pm , so that Terminal operation can be closed timely and night driving can be avoided. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1334 | HPCL REWARI IRD | 1. Whatsapp group to be created for sharing of information. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-03-2000011158ACN-2026-03-4000121678 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121678 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121678 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121678 | AUD-2026-03-2000011158ACN-2026-03-4000121678 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Noted and 20% blending is done and monitered on daily basis | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121668 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Blending of Ethanol is being done @ 19.8%- Location has been advised to achieve 20% as per guidelines | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1334 | HPCL REWARI IRD | Blending to be achieved @ 20% | SOD | Marketing | NZ | 2026-03-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-30 | AUD-2026-03-2000011158ACN-2026-03-4000121668 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121668 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121668 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121668 | AUD-2026-03-2000011158ACN-2026-03-4000121668 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Location has already reviewed and communicated reasons for abnormal variations on four occasions. One 400 KVA DG set is already shifted to Ajmer | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000121671 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Location has booked only 4 instances of abnormal gain/ loss during the period 1st Oct'25 to 10th Feb'26. Location has been advised to produce reasons for these abnormal variations on these four occasions. One 400 KVA DG set is lying as surplus which is to be shifted to Ajmer Terminal. Location to confirm shifting of the equipment by Feb’26 end. | 3.9 | Abnormal variations / unused assets reviewed | 1334 | HPCL REWARI IRD | Location to revert back with action taken. | SOD | Marketing | NZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-15 | AUD-2026-03-2000011158ACN-2026-03-4000121671 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121671 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121671 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121671 | AUD-2026-03-2000011158ACN-2026-03-4000121671 | 21 | 21 | 26 | 80 | 1 | 1 | 28 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | Location has already reviewed and communicated reasons for abnormal variations on four occasions. One 400 KVA DG set is already shifted to Ajmer | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121379 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Location has booked only 4 instances of abnormal gain/ loss during the period 1st Oct'25 to 10th Feb'26. Location has been advised to produce reasons for these abnormal variations on these four occasions. One 400 KVA DG set is lying as surplus which is to be shifted to Ajmer Terminal. Location to confirm shifting of the equipment by Feb’26 end. | 3.9 | Abnormal variations / unused assets reviewed | 1334 | HPCL REWARI IRD | Location to revert back with action taken. | SOD | Marketing | NZ | 2026-02-28 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000011004ACN-2026-02-4000121379 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121379 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121379 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121379 | AUD-2026-02-2000011004ACN-2026-02-4000121379 | 21 | 21 | 26 | 80 | 1 | 1 | 26 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | 1. Leakage has been arrested 2. Painting of Biodiesel line in progress 3. fixed Suitable compression glands at required places 4. Short bolting rectified 5. FLP junction box bolts tightened 6. Support for N2 cylinders have been provided 7. Distinct eartinghave been provided 8. Valve positioningto have been corrected 9. Earthing termination checked 10. Leakage to be arrested from oil cups 11. Locking pin placed in HOV 12. Lock has been ensured of VFD soft starter Panel 13. SOP board of VRU displayed 14. labour licence amendment already applied 15. Renewal of CGWA licence has been already applied | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121387 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | 1. Leakage has been observed from the swivel joints of the loading arms at TT Gantry Bay Nos. 7, 6, and 4. 2. The newly fabricatedbiodiesel line is to be painted after completion of the job. 3. An oversized double compression gland has been observed at the VRUactuator connections. 4. Short bolting has been observed in the VRU pump house area. 5. Bolts in the FLP junction box in the VRU area are not properly fastened. 6. An N₂ cylinder is placed in the VRU area without adequate support. Proper clamping or a bottom support arrangement should be provided to prevent it from falling. 7. Although double earthing has been provided for radar gauges, the terminations to the earthing strips are not distinct. Earthing should be connected through two separate and distinct earthing strips. 8. The inlet valve of TK-20 is positioned at the 2 o’clock direction, posing an operational hazard during emergencies. Replacement to the 12 o’clock position should be expedited. 9. At various locations, field equipment earthing connections have been found routed through insulators tightened onto cable trays. Earthing should not be connected to the cable tray, and the connections shouldbe clearly identifiable from the respective earthing strips for proper stray current drainage. 10. Leakage from the oil cups installed over product pumps has been observed at HSD Pump No. 4 and MS Pump No. 1. 11. The HOV on the discharge line of HSD-1 product pump has been found loose, and the locking pin is missing. 12. The door lock of the VFD soft-start panel in the MCC room needs to bereplaced. 13. SOP board placed in VRU area to be relocated as it is hindering Foam monitor operation 14. Amendment in Labour Licence required for change in Occupier 15. CGWA Licence Renewal is under progress. Needs to expedite. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1334 | HPCL REWARI IRD | 1. Leakage to be arrested 2. Painting of Biodiesel line to be done 3. Suitable compression glands to be used 4. Short bolting tobe rectified 5. FLP junction box bolts to be tightened 6. Support for N2 cylinders to be provided 7. Distinct earting to be provided 8. Valve positioningto be corrected 9. Earthing termination to be checked and made as per standard procedure 10. Leakage to be arrested from oil cups 11. Locking pin to be placved in HOV 12. Lock to be ensured of VFD soft starter Panel 13. SOP board of VRU to be reloacted 14. labour licence to be amended 15. CGWA licence to be renewed | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011004ACN-2026-02-4000121387 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121387 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121387 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121387 | AUD-2026-02-2000011004ACN-2026-02-4000121387 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | 1. Leakage has been arrested 2. Painting of Biodiesel line in progress 3. fixed Suitable compression glands at required places 4. Short bolting rectified 5. FLP junction box bolts tightened 6. Support for N2 cylinders have been provided 7. Distinct eartinghave been provided 8. Valve positioningto have been corrected 9. Earthing termination checked 10. Leakage to be arrested from oil cups 11. Locking pin placed in HOV 12. Lock has been ensured of VFD soft starter Panel 13. SOP board of VRU displayed 14. labour licence amendment already applied 15. Renewal of CGWA licence has been already applied | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000121679 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | 1. Leakage has been observed from the swivel joints of the loading arms at TT Gantry Bay Nos. 7, 6, and 4. 2. The newly fabricatedbiodiesel line is to be painted after completion of the job. 3. An oversized double compression gland has been observed at the VRUactuator connections. 4. Short bolting has been observed in the VRU pump house area. 5. Bolts in the FLP junction box in the VRU area are not properly fastened. 6. An N₂ cylinder is placed in the VRU area without adequate support. Proper clamping or a bottom support arrangement should be provided to prevent it from falling. 7. Although double earthing has been provided for radar gauges, the terminations to the earthing strips are not distinct. Earthing should be connected through two separate and distinct earthing strips. 8. The inlet valve of TK-20 is positioned at the 2 o’clock direction, posing an operational hazard during emergencies. Replacement to the 12 o’clock position should be expedited. 9. At various locations, field equipment earthing connections have been found routed through insulators tightened onto cable trays. Earthing should not be connected to the cable tray, and the connections shouldbe clearly identifiable from the respective earthing strips for proper stray current drainage. 10. Leakage from the oil cups installed over product pumps has been observed at HSD Pump No. 4 and MS Pump No. 1. 11. The HOV on the discharge line of HSD-1 product pump has been found loose, and the locking pin is missing. 12. The door lock of the VFD soft-start panel in the MCC room needs to bereplaced. 13. SOP board placed in VRU area to be relocated as it is hindering Foam monitor operation 14. Amendment in Labour Licence required for change in Occupier 15. CGWA Licence Renewal is under progress. Needs to expedite. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1334 | HPCL REWARI IRD | 1. Leakage to be arrested 2. Painting of Biodiesel line to be done 3. Suitable compression glands to be used 4. Short bolting tobe rectified 5. FLP junction box bolts to be tightened 6. Support for N2 cylinders to be provided 7. Distinct earting to be provided 8. Valve positioningto be corrected 9. Earthing termination to be checked and made as per standard procedure 10. Leakage to be arrested from oil cups 11. Locking pin to be placved in HOV 12. Lock to be ensured of VFD soft starter Panel 13. SOP board of VRU to be reloacted 14. labour licence to be amended 15. CGWA licence to be renewed | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011158ACN-2026-03-4000121679 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121679 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121679 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121679 | AUD-2026-03-2000011158ACN-2026-03-4000121679 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | All project closed except 4 , which will be closed by march , All invoices already punched after physical completion of work | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121389 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Project Progress reviewed, A total of 08 projects for FY 2025–26, along with one carry-over project from FY 2024–25, were taken up by the location. Out of the total 09 projects, two have been completed, and the remaining seven are likely to be completed by 31/03/2026. Details enclosed with this report. | 4.3 | Project progress reviewed | 1334 | HPCL REWARI IRD | Remaining 7 projects to be completed | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011004ACN-2026-02-4000121389 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121389 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121389 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121389 | AUD-2026-02-2000011004ACN-2026-02-4000121389 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | All project closed except 4 , which will be closed by march , All invoices already punched after physical completion of work | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000121681 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Project Progress reviewed, A total of 08 projects for FY 2025–26, along with one carry-over project from FY 2024–25, were taken up by the location. Out of the total 09 projects, two have been completed, and the remaining seven are likely to be completed by 31/03/2026. Details enclosed with this report. | 4.3 | Project progress reviewed | 1334 | HPCL REWARI IRD | Remaining 7 projects to be completed | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011158ACN-2026-03-4000121681 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121681 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121681 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121681 | AUD-2026-03-2000011158ACN-2026-03-4000121681 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | All balanced lot disposal/auction have been done successfully | SENIOR MANAGEMENT AUDIT BY NZ ZONAL TEAM | 2026-02-12 | AUD-2026-02-2000011004 | 2026-02-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121390 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Out of total estimated scrap realization value of Rs. 15.75 Lakhs, already realized Scrap value of Rs. 15.15 Lakhs thru successful auctioning of 5 out of total 6 lots. Disposal of balance lot is in progress. EDC of disposal of balance 2 lots is 15th Mar’26 and the location will be declared Scrap Free by 31st Mar’26 along with closure of AMDA as well | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1334 | HPCL REWARI IRD | Disposal of balance lot to be expedited | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000011004ACN-2026-02-4000121390 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011004ACN-2026-02-4000121390 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-02-2000011004 - ACN-2026-02-4000121390 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000011004ACN-2026-02-4000121390 | AUD-2026-02-2000011004ACN-2026-02-4000121390 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
TYAGI ATUL | 2026-03-25 | SINGH YUGAL KISHOR | 2026-03-25 | All balanced lot disposal/auction have been done successfully | SENIOR MANAGEMENT INSPECTION 1334 REWARI | 2026-02-12 16:00 | AUD-2026-03-2000011158 | 2026-02-10 14:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000121682 | Closed | SINGH YUGAL KISHOR | 2026-03-25 | Out of total estimated scrap realization value of Rs. 15.75 Lakhs, already realized Scrap value of Rs. 15.15 Lakhs thru successful auctioning of 5 out of total 6 lots. Disposal of balance lot is in progress. EDC of disposal of balance 2 lots is 15th Mar’26 and the location will be declared Scrap Free by 31st Mar’26 along with closure of AMDA as well | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1334 | HPCL REWARI IRD | Disposal of balance lot to be expedited | SOD | Marketing | NZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011158ACN-2026-03-4000121682 | HR | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011158ACN-2026-03-4000121682 | 2026-09-10 17:00 | 39.0455 | 205 | >20 | AUD-2026-03-2000011158 - ACN-2026-03-4000121682 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011158ACN-2026-03-4000121682 | AUD-2026-03-2000011158ACN-2026-03-4000121682 | 21 | 21 | 26 | 80 | 1 | 1 | 31 | 30
|  |  |  | Out of 76 Camera, Three are still down, Location summun to CCTV Vendor to complete User acceptance test and take corrective action | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127189 | Open | KAMLESH SAHU | 2026-05-07 | CCTV functioning found to be satisfactory. Total 79 cameras are there at New Depot, out of which 3 are down and not yet handed overby E&P to Operation Team. | 2.6 | CCTV functioning checked | 1528 | RAIPUR IRD-II | Following up with E&P for making Camera functional | SOD | Marketing | ECZ | 2026-04-30 |  | 6 |  | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127189 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127189 | 2026-08-28 18:00 | 52.0038 | 241 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127189 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011236ACN-2026-03-4000127189 |  | AUD-2026-03-2000011236ACN-2026-03-4000127189 | 21 |  | 26 | 80 | 3 | 3 | 35
|  |  |  | Location will float the tendor | LOCATION VISIT AT RAIPUR IRD | 2026-01-13 | AUD-2026-03-2000011236 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127190 | Open | KAMLESH SAHU | 2026-05-07 | VA system is not yet implemented at Raipur New IRD. | 2.7 | VA alerts checked / analysed | 1528 | RAIPUR IRD-II | Location is advised to float the tender and expedite installation of VA at location. | SOD | Marketing | ECZ | 2026-04-30 |  | 3 |  | S3 | F1 | 2026-04-30 | AUD-2026-03-2000011236ACN-2026-03-4000127190 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011236ACN-2026-03-4000127190 | 2026-08-28 18:00 | 52.0038 | 241 | >20 | AUD-2026-03-2000011236 - ACN-2026-03-4000127190 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011236ACN-2026-03-4000127190 |  | AUD-2026-03-2000011236ACN-2026-03-4000127190 | 21 |  | 26 | 80 | 3 | 3 | 35
|  |  |  | The three ongoing MOCs are related to the TAS revamping project. 1) Tank dip elimination 2) TFMS and SAP Stabilization 3) Bay revamping. Since as on date 31.08.2026, bay revamping is in progress, and both the other activities are under stabilization period of 90 days hence the MOCs will still remain functional and will be closed only after successful completion of stabilization period. Expected MOC closure by 30.12.2026. | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127198 | Open | SINGWAL DEEPAK | 2026-09-01 | Reviewed MOC at location, 7 are in closed status while 3 are ongoing. | 3.17 | MOC status reviewed | 1435 | GWALIOR DEPOT | Location to expedite closure of open MOC | SOD | Marketing | CEN | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-03-2000011237ACN-2026-03-4000127198 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127198 | 2026-08-22 19:00 | 57.9622 | 302 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127198 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011237ACN-2026-03-4000127198 |  | AUD-2026-03-2000011237ACN-2026-03-4000127198 | 21 |  | 26 | 80 | 2 | 2 | 44
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127199 | Open |  |  | 22 out of 24 observation in OISD, 62 out of 116 observations in MDSA & 63 out of 69 observations in SSA are found complied, for remaining work is in progress. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1435 | GWALIOR DEPOT | Location to expedite closure of open Audit observation point | SOD | Marketing | CEN | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-03-2000011237ACN-2026-03-4000127199 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127199 | 2026-08-22 19:00 | 57.9622 | 302 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127199 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011237ACN-2026-03-4000127199 |  | AUD-2026-03-2000011237ACN-2026-03-4000127199 | 21 |  | 26 | 80 | 2 | 2 | 44
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000011237 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127300 | Open |  |  | Reviewed the ongoing TAS revamp project and siding project. TAS project is lagging behind schedule. Location was advised to follow up with vendor for expediting completion. | 4.3 | Project progress reviewed | 1435 | GWALIOR DEPOT | Location is advised to expedite completion of TAS Revamp Project. | SOD | Marketing | CEN | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-03-2000011237ACN-2026-03-4000127300 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011237ACN-2026-03-4000127300 | 2026-08-22 19:00 | 57.9622 | 302 | >20 | AUD-2026-03-2000011237 - ACN-2026-03-4000127300 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011237ACN-2026-03-4000127300 |  | AUD-2026-03-2000011237ACN-2026-03-4000127300 | 21 |  | 26 | 80 | 2 | 2 | 44
|  |  |  | 2) 65% work completed for railway siding revamp, project completion due date extended upto 30.09.26 and efile note approved for same. Hydrant line ( approx 1550 m ) laid down, 10 No. of sprinkler segment fabricated and erected as per Railway SOD, all pedestal work completed for hydrant line ( 8 inch ) | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127303 | Open | PANWAR VIPIN SINGH | 2026-07-31 | 1. TAS officer to focus on expediting winding up of TAS Revamp Project. 2. Safety Officer to expedite and ensure timely completion of Railway siding Fire Hydrant Network work. | 1.8 | Improvement plans discussed | 1436 | SAGAR DEPOT | 1) Expediting completion of TAS project 2) Expediting completion of Railway siding Fire Hydrant Network work | SOD | Marketing | CEN | 2026-06-30 |  | 2 |  | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127303 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127303 | 2026-08-07 19:00 | 72.9622 | 302 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127303 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011238ACN-2026-03-4000127303 |  | AUD-2026-03-2000011238ACN-2026-03-4000127303 | 21 |  | 26 | 80 | 4 | 2 | 44
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-02-13 | AUD-2026-03-2000011238 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127319 | Open |  |  | OISD/MDSA/SSA compliance was reviewed. OISD points pertaining to Railway Siding are still pedning for complaince. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1436 | SAGAR DEPOT | Location to the compliance of pending audit points on priority with set target. | SOD | Marketing | CEN | 2026-06-30 |  | 12 |  | S4 | F3 | 2026-06-30 | AUD-2026-03-2000011238ACN-2026-03-4000127319 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011238ACN-2026-03-4000127319 | 2026-08-07 19:00 | 72.9622 | 302 | >20 | AUD-2026-03-2000011238 - ACN-2026-03-4000127319 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000011238ACN-2026-03-4000127319 |  | AUD-2026-03-2000011238ACN-2026-03-4000127319 | 21 |  | 26 | 80 | 4 | 2 | 44
|  |  |  | i) FO/ LDO- Necessary followups are going on with Zone and HQO for getting the necessary approval to liquidate the Off Spec FO/ LDO either to VR or MR. ii)MTO/ Hexane- MTO has been liquidated from the location.Regular followups are going with I&C,Kolkata for earliest liquidation of the Hexane. iii) LSHFHSD -Regular followups are going with I&C,Kolkata for earliest liquidation of the LSHFHSD . iv) TK210- Prior approval for the TK 210 conversion from SKO to ATF has been obtained. Tendering for the modification job is under progress.Fund will be released by facilities and Planning dept in April'26 followed by PO placement.The tank conversion activity will be started post PO placement and overall job will be completed including all statutory approval by 31.07.2026 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127094 | Open | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | Pending issues reviewed and corrective action recommended. | 1.3 | Pending issues reviewed | 1644 | KOLKATA-I TERMINAL | Off Spec FO/ LDO to be liquidated. MTO Hexane also to be liquidated. LSHFHSD to be supplied to DS customers in coordination DS RM. TK210 to be put in service after PESO approval. | SOD | Marketing | EZ | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-31 | AUD-2026-03-2000010730ACN-2026-03-4000127094 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127094 | 2026-09-18 | 31.7538 | 241 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127094 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127094 |  | AUD-2026-03-2000010730ACN-2026-03-4000127094 | 21 |  | 26 | 80 | 0 | -7 | 35
|  |  |  | i)PLC and LRC job will be start from 03.04.2026 and will be completed by 30.05.2026 ii)MTO proposal will be sent to HQO by 15.04.2026 for necessary release of fund from E&P dept. iii)Dip elimination filenote will be initiated by 30.04.2026 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127095 | Open | BUDHI VEERAIAH | 2026-05-16 | TAS revamping Job Completion - It was given to understand that all the gantry metering unit installed and commissioned. However, new PLC and LRC installation is pending. Proposal for MTO unloading at Kolkata - Pending TT Dip elimination file note - Pending | 1.4 | Earlier action points status checked | 1644 | KOLKATA-I TERMINAL | Location is advised to expedite the job | SOD | Marketing | EZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 4 | PROCESS SAFETY | S2 | F2 | 2026-05-30 | AUD-2026-03-2000010730ACN-2026-03-4000127095 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127095 | 2026-09-18 | 31.7538 | 241 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127095 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127095 |  | AUD-2026-03-2000010730ACN-2026-03-4000127095 | 21 |  | 26 | 80 | 0 | -7 | 35
|  |  |  | PO placed on the replacemnet for the Non functional CCTVs and the job will be completed by 30.06.2026 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127500 | Open | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | Location has total of 110 CCTV Camera and 95 found as functional | 2.6 | CCTV functioning checked | 1644 | KOLKATA-I TERMINAL | It was given understand that the non functional cameras are beyond repair and location is in process of procurement of new additional CCTV camera under NPCB | SOD | Marketing | EZ | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010730ACN-2026-03-4000127500 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127500 | 2026-09-18 | 31.7538 | 302 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127500 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127500 |  | AUD-2026-03-2000010730ACN-2026-03-4000127500 | 21 |  | 26 | 80 | 0 | -7 | 44
|  |  |  | Post Rake unloading, Location has been coordinating with the Loading location for the dip variations and observations on the seal conditions. Also location is tallying the product qunatity of TAS and SAP record on dailly basis including bay-wise variations,if any and taking corrective actions accordingly. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127506 | Open | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1644 | KOLKATA-I TERMINAL | MS losses to be brought under control | SOD | Marketing | EZ | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010730ACN-2026-03-4000127506 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127506 | 2026-09-18 | 31.7538 | 241 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127506 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127506 |  | AUD-2026-03-2000010730ACN-2026-03-4000127506 | 21 |  | 26 | 80 | 0 | -7 | 35
|  |  |  | Pending points will be completed with the timeline . | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127509 | Open | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | OISD - 4 pending point SSA - 3 Pending point MDSA - 20 pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1644 | KOLKATA-I TERMINAL | Location to close the open points at the earliest | SOD | Marketing | EZ | 2026-05-30 |  | 5 |  | S1 | F5 | 2026-05-30 | AUD-2026-03-2000010730ACN-2026-03-4000127509 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127509 | 2026-09-18 | 31.7538 | 271 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127509 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127509 |  | AUD-2026-03-2000010730ACN-2026-03-4000127509 | 21 |  | 26 | 80 | 0 | -7 | 39
|  |  |  | i) Process for disposal of new identifed lot will be started and the lot will be disposeed off by 30.09.2026 ii)Lighst will be repaired by 15.04.2026 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127510 | Open | BUDHI VEERAIAH | 2026-05-16 | Visit in TTG, TWG BB2 , TTPH, TWPH, Control room, Security room, Admin carried out. Housekeeping & SOP adherance found satisfactory | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1644 | KOLKATA-I TERMINAL | Scrap Disposal to be expedited. Unidentifed scrap [Fire Extingusher, Unloading hose] found in Kolkata Terminal-II. 3 of the lights found to be non functional in TW siding | SOD | Marketing | EZ | 2026-04-15 |  | 5 |  | S1 | F5 | 2026-09-30 | AUD-2026-03-2000010730ACN-2026-03-4000127510 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127510 | 2026-09-18 | 31.7538 | 226 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127510 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127510 |  | AUD-2026-03-2000010730ACN-2026-03-4000127510 | 21 |  | 26 | 80 | 0 | -7 | 33
|  |  |  | i) Process for disposal of new identifed lot will be started and the lot will be disposeed off by 30.06.2026 ii)Lighst will be repaired by 15.04.2026 | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127512 | Open | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | Scrap Dispoal to be expedited. Uniddentifed scrap [Fire Extingusher, Unloading hose] found in Kolkata Terminal-II. 3 of the lights found to be non functional in TW siding | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1644 | KOLKATA-I TERMINAL | LIC to ensure 100% physical disposal by 30th Mar'26 | SOD | Marketing | EZ | 2026-03-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-03-2000010730ACN-2026-03-4000127512 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127512 | 2026-09-18 | 31.7538 | 210 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127512 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010730ACN-2026-03-4000127512 |  | AUD-2026-03-2000010730ACN-2026-03-4000127512 | 21 |  | 26 | 80 | 0 | -7 | 30
[5 empty] | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122786 | Open |  |  | One experienced officer is required in location. TAS system was replaced 10 years before. | 1.5 | HQO / Zonal support required identified | 1800 | HUBLI DEPOT | Location to develop proposal for new TAS | SOD | Marketing | SWZ | 2026-06-30 |  | 3 |  | S3 | F1 | 2026-06-30 | AUD-2026-03-2000011030ACN-2026-03-4000122786 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122786 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122786 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122786 |  | AUD-2026-03-2000011030ACN-2026-03-4000122786 | 21 |  | 26 | 80 | 18 | 18 | 44
[5 empty] | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122789 | Open |  |  | Detailed analysis of lux level shall be carried out in all areas of the IRD | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1800 | HUBLI DEPOT | Lighting improvement to be completed by 30.09.2026 | SOD | Marketing | SWZ | 2026-09-30 |  | 2 |  | S2 | F1 | 2026-09-30 | AUD-2026-03-2000011030ACN-2026-03-4000122789 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122789 | 2026-09-11 19:30 | 37.9413 | 394 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122789 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122789 |  | AUD-2026-03-2000011030ACN-2026-03-4000122789 | 21 |  | 26 | 80 | 18 | 18 | 57
|  |  |  | 1 CCTV rectified and 1 PTZ camera again sent back for repair. | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122791 | Open | DEVA DHRUVA | 2026-07-31 | 2 CCTV are not working | 2.6 | CCTV functioning checked | 1800 | HUBLI DEPOT | To be rectified | SOD | Marketing | SWZ | 2026-04-30 |  | 2 |  | S2 | F1 | 2026-04-30 | AUD-2026-03-2000011030ACN-2026-03-4000122791 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122791 | 2026-09-11 19:30 | 37.9413 | 241 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122791 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122791 |  | AUD-2026-03-2000011030ACN-2026-03-4000122791 | 21 |  | 26 | 80 | 18 | 18 | 35
[5 empty] | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122792 | Open |  |  | Checked open patch HCD of TK-2 and point type HCD for Ethanol UG dyke, alarm triggered in Control room, main gate and local hooter also activated. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1800 | HUBLI DEPOT | Location to install point type HCD in pumphouse as per SSA | SOD | Marketing | SWZ | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011030ACN-2026-03-4000122792 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122792 | 2026-09-11 19:30 | 37.9413 | 241 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122792 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122792 |  | AUD-2026-03-2000011030ACN-2026-03-4000122792 | 21 |  | 26 | 80 | 18 | 18 | 35
[5 empty] | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122796 | Open |  |  | OISD audit 2025 total 38 points, 23 are complied. MDSA 2025, total 26 points, 4 complied. SSA 2025, total 56 points, 43 complied. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1800 | HUBLI DEPOT | To be complied at the earliest | SOD | Marketing | SWZ | 2026-06-30 |  | 2 |  | S2 | F1 | 2026-06-30 | AUD-2026-03-2000011030ACN-2026-03-4000122796 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122796 | 2026-09-11 19:30 | 37.9413 | 302 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122796 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122796 |  | AUD-2026-03-2000011030ACN-2026-03-4000122796 | 21 |  | 26 | 80 | 18 | 18 | 44
[5 empty] | SENIOR MANAGEMENT INSPECTION HUBLI IRD | 2026-03-25 19:00 | AUD-2026-03-2000011030 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122798 | Open |  |  | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | 4.3 | Fifteen projects to be completed for which works are under progress | 1800 | HUBLI DEPOT | Capitalization of physically completed projects is to be ensured, completion of projects by time line to be ensured. | SOD | Marketing | SWZ | 2026-04-05 |  | 4 |  | S2 | F2 | 2026-04-05 | AUD-2026-03-2000011030ACN-2026-03-4000122798 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011030ACN-2026-03-4000122798 | 2026-09-11 19:30 | 37.9413 | 216 | >20 | AUD-2026-03-2000011030 - ACN-2026-03-4000122798 | 532 | 8294 | 21 | 8294 | 197 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011030ACN-2026-03-4000122798 |  | AUD-2026-03-2000011030ACN-2026-03-4000122798 | 21 |  | 26 | 80 | 18 | 18 | 31
JHA PANKAJ KUMAR | 2026-03-28 | KUMAR NITISH | 2026-03-28 | Complied.Facility to check eye sight & Colour blindness has been developed. refer attachment. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122075 | Closed | KUMAR NITISH | 2026-03-28 | Facility not available | 2.16 | Eyesight / colour-blindness awareness checked | 1128 | MATHURA TERMINAL | facility shall be developed. | SOD | Marketing | NUZ | 2026-03-05 | THIRD PARTY ERRORS | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010909ACN-2026-02-4000122075 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122075 | 2026-09-18 | 31.7538 | 208 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122075 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122075 | AUD-2026-02-2000010909ACN-2026-02-4000122075 | 21 | 21 | 26 | 80 | 14 | 13 | 27 | 30
JHA PANKAJ KUMAR | 2026-03-28 | KUMAR NITISH | 2026-03-28 | Complied.TT crew of UP 86T7480 and UP80DT8234 have been counselled . PPE usage being checked without fail. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122082 | Closed | KUMAR NITISH | 2026-03-28 | Housekeeping of location is satisfactory. TT crew of UP 86T7480 and UP80DT8234 were not wearing safety harness. | 3.15 | Housekeeping & PPE usage checked | 1128 | MATHURA TERMINAL | Location to ensure PPE usage by TT crew. | SOD | Marketing | NUZ | 2026-03-02 | COMPLACENCY OR RISK NORMALIZATION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-03-02 | AUD-2026-02-2000010909ACN-2026-02-4000122082 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122082 | 2026-09-18 | 31.7538 | 208 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122082 | 532 | 8294 | 21 | 8294 | 231 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122082 | AUD-2026-02-2000010909ACN-2026-02-4000122082 | 21 | 21 | 26 | 80 | 14 | 13 | 26 | 30
JHA PANKAJ KUMAR | 2026-03-28 | KUMAR NITISH | 2026-03-28 | Complied. 3.In submerged pump house, all pumps' oil cups have been replaced and oil filled. vide permit no.100000748040 dt 24.03.2026. 4.raisers of white oil in TW Gantry have been blinded. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122085 | Closed | KUMAR NITISH | 2026-03-28 | 1. Full field round completed. 2. Electrical panels of MCC room found as being maintained properly. 3. In submerged pump house, all pumps having empty oil cups and most of them are open from top. 4. A number of raisers of white oil in TW Gantry found not blinded. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1128 | MATHURA TERMINAL | Corrective action to be taken. | SOD | Marketing | NUZ | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122085 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122085 | 2026-09-18 | 31.7538 | 208 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122085 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122085 | AUD-2026-02-2000010909ACN-2026-02-4000122085 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 30
JHA PANKAJ KUMAR | 2026-03-28 | KUMAR NITISH | 2026-03-28 | Complied. Balance MS scraps hae been disposed off vide permit no. 100000749042 dt 26.03.2026 | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122087 | Closed | KUMAR NITISH | 2026-03-28 | Scrap available at location. Disposal in progress. Auction completed for most of the items. Upliftment is pending and being followed up with scrap vendor. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1128 | MATHURA TERMINAL | For balance MS scrap, RFD to be generated. | SOD | Marketing | NUZ | 2026-03-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010909ACN-2026-02-4000122087 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122087 | 2026-09-18 | 31.7538 | 208 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122087 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122087 | AUD-2026-02-2000010909ACN-2026-02-4000122087 | 21 | 21 | 26 | 80 | 14 | 13 | 28 | 30
JHA PANKAJ KUMAR | 2026-03-28 | KUMAR NITISH | 2026-03-28 | Complied.Samples have been disposed off. As per Communication received from Mobile QC lab Samples from January 2026 onwards have been retained. | SR MANAGEMENT INSPECTION MATHRA Q4 25-26 | 2026-02-24 13:30 | AUD-2026-02-2000010909 | 2026-02-23 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122095 | Closed | KUMAR NITISH | 2026-03-28 | Sample which have to be kept till testing of related samples under MDG, were found to be kept in heaps and were not being disposed off regularly. | 6.7 |  | 1128 | MATHURA TERMINAL | Corrective action to be taken | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010909ACN-2026-02-4000122095 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010909ACN-2026-02-4000122095 | 2026-09-18 | 31.7538 | 208 | >20 | AUD-2026-02-2000010909 - ACN-2026-02-4000122095 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010909ACN-2026-02-4000122095 | AUD-2026-02-2000010909ACN-2026-02-4000122095 | 21 | 21 | 26 | 80 | 14 | 13 | 31 | 30
POTHALA VENKATA RAO | 2026-03-30 | PP AKHIL | 2026-03-17 | Stock loss performance improved. Feb/cummulative MS 0.37%/0.15% HSD 0.31%/ 0.33% Eth 0.4% / 0.45% Ola performance improved to95% in Februray 2026., | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123493 | Closed | PP AKHIL | 2026-03-17 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1937 | SURYAPET TERMINAL | Stock loss, OLA Performance to be improved. | SOD | Marketing | SCR | 2026-01-30 | INSTRUMENTATION OR ALARM FAILURES | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123493 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123493 | 2026-08-04 18:45 | 75.9726 | 210 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123493 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123493 | AUD-2026-03-2000011061ACN-2026-03-4000123493 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 30
POTHALA VENKATA RAO | 2026-03-30 | PP AKHIL | 2026-03-12 | New gland rope fixed and gland leak arrested for Fire pump 1 vide permit 100000736600.Video attached | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123496 | Closed | PP AKHIL | 2026-03-12 | The following firefighting facilities were checked and demonstrated: Sprinkler systems for Tank-1B, Tank-1C, and Tank-3B HVLR-1, HVLR-2, and HVLR-6 for Tank-1B and Tank-1C MEFG for Tank-3A HCDs at Tank-3A & Tank-3B (West side – Open Path) and Tank-01A (Right side – Open Path) Water-cum-foam monitor (FM-36) near Tank-1C Fire Engine FE-1: manual testing carried out for gland leakage and performance Fire engine sequencing and auto-start functionality checked by dropping system pressure | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1937 | SURYAPET TERMINAL | Slight Gland leakage observed in one of the fire pump | SOD | Marketing | SCR | 2026-01-30 | FAILURE TO FOLLOW PROCEDURES | 5 | ASSET INTEGRITY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123496 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123496 | 2026-08-04 18:45 | 75.9726 | 210 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123496 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123496 | AUD-2026-03-2000011061ACN-2026-03-4000123496 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 30
POTHALA VENKATA RAO | 2026-03-30 | PP AKHIL | 2026-03-10 | New set of electrical hand gloves purchased and placed in Fire emergency trolley. All the items are placed in designated shelvesas per OISD 244 is attached and the details of items. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123494 | Closed | POTHALA VENKATA RAO | 2026-03-30 | Reviewed emergency trolley equipment. Some of the items were found missing and not in the designated compartments. Interacted with officers & security personnel about their roles and resposibilities during emergencies | 2.5 | Emergency response preparedness reviewed | 1937 | SURYAPET TERMINAL | Missing electrical hand gloves purchased and kept in Fire emergency trolley. All the items are placed in designated shelves and the details of items as per OISD 244 is attached. | SOD | Marketing | SCR | 2026-01-30 | POOR EQUIPMENT MAINTENANCE | 5 | EMERGENCY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123494 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123494 | 2026-08-04 18:45 | 75.9726 | 210 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123494 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123494 | AUD-2026-03-2000011061ACN-2026-03-4000123494 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 30
POTHALA VENKATA RAO | 2026-03-30 | PP AKHIL | 2026-03-10 | 1-Camera angle adjusted for following cameras for better visibility -Perimerter camera near pipeline -Lube ware house(Camea screenshot attached). 2-Camera lens removed and cleaned for following cameras FLM-8 ,TK-1C and Camera near 2B is replaced and kept spare camera.(Camea screenshot attached). | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123495 | Closed | PP AKHIL | 2026-03-10 | • Total cameras installed: 43 (Digital: 42, Analogue: 1) • Cameras working: All 43 (one camera under maintenance was rectified during inspection) • Cameras integrated with VA: 25 | 2.6 | CCTV functioning checked | 1937 | SURYAPET TERMINAL | 1. Camera angles near the pipeline area and lube warehouse need adjustment for improved supervision and visibility. 2. Camera clarity near FLM-8, TK-2B, and TK-1C is inadequate; corrective action to be taken | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123495 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123495 | 2026-08-04 18:45 | 75.9726 | 210 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123495 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123495 | AUD-2026-03-2000011061ACN-2026-03-4000123495 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 30
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-03 | 1. Location organising weekly basis training to contract workmen, officers , TT crew and security staff for handling fire fightingscenrio , use of PPE, emergency evacuation. Records also maintained for same. Training provided to all Officers, CWs, security and TT crew as per OISD 244 modules and records maintained. 2. Location conducted Bomb threat mock drill on 08.01.26 and learnings from drill discussed with all teams and same discussed in safety committee meetings. Location also provided training to CW and security for emergency evaution and understading of their roles in mock drills. 3. ERDMP document modified as per advise. 4. All the relevant scenerio covered in FY 25-26 ( including tank farm pool fire, ows flash fire, tank on fire at gantry, leakage scenrio, drill in pump house, electric fire in mcc room, fire in parking area, off shift and off site mock drills, bomb threat mock drill, earthquake level III mock drill, fire in sample room etc. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121483 | Closed | PANWAR VIPIN SINGH | 2026-03-03 | A Bomb Threat drill was conducted on 08/01/2026 in the presence of the Bomb Squad, Fire Brigade, local police, District Medical Team, and Mutual Aid Partners. Observations: 1 Quick identification of suspicious item 2 Effective coordination between Depot personnel, mutual aid partners and district administration 3 Evacuation procedure was followed as per emergency plan ERDMP document was also checked for the emergency scenarios considered for the location and it was found that a scenario of tilting of floating roof was also considered in it whereas the location is having only UG product tanks. Further, all the relevant emergency scenarios have not been so far covered in mock drills conducted in this Financial Year. | 2.1 | Fire drill conducted in last 6 months (surprise) | 1308 | SITARGANJ DEPOT | 1 Need for Regular training to prevent panic is to be done 2 Before arrival of bomb Squad premises should be evacuated by the depot personnels 3. ERDMP to be modified with correct information. 4. All the relevant emergency scenarious covered in the ERDMP document to be covered during this FY. | SOD | Marketing | NUZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-06-30 | AUD-2026-02-2000010854ACN-2026-02-4000121483 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121483 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121483 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121483 | AUD-2026-02-2000010854ACN-2026-02-4000121483 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-25 | Compliance mentioned for TT no. UP25FT8460 done. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121488 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | TT fitting and safety check of TT No UP25FT8460 was done. Observations are as follows: 1. Double convex side mirror to be fixed for visibilty of blind spots. 2. Welding to be done on the ends of hinge pin to avoid removal. 3. Check the welding of the hinges laps are properly done for complete surface of the valve box. | 3.1 | TT fittings & discipline checked | 1308 | SITARGANJ DEPOT | Compliance of the observation made w.r.t. TT inspected to be ensured and TT inspections to be carried out as per circular. | SOD | Marketing | NUZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-02-2000010854ACN-2026-02-4000121488 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121488 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121488 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121488 | AUD-2026-02-2000010854ACN-2026-02-4000121488 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-25 | HCD repaired, calibrated by OEM Drager Safety and same installed and tested on 12.03.2026 | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121954 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | Open Path HCD is under maintenence as Calibration is required to be done hence it has been handed over to TAS vendor under AMC contrtact. | 4.2 | Maintenance activities reviewed | 1308 | SITARGANJ DEPOT | HCD to be installed post calibration and confirmation to be provided to Zone | SOD | Marketing | NUZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-15 | AUD-2026-02-2000010854ACN-2026-02-4000121954 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121954 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121954 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121954 | AUD-2026-02-2000010854ACN-2026-02-4000121954 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-31 | 1. TT parking area cleaned with water and same mentioned in housekeeping checklist on fortnightly basis. 2. Sealing of Gaps between window frames and walls completed. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121498 | Closed | PANWAR VIPIN SINGH | 2026-03-31 |  | 3.15 | Housekeeping & PPE usage checked | 1308 | SITARGANJ DEPOT | 1. Fortnightly cleaning of TT parking area with water, if felt necessary 2. Sealing of Gaps between window frames and walls | SOD | Marketing | NUZ | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121498 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121498 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121498 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121498 | AUD-2026-02-2000010854ACN-2026-02-4000121498 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-25 | MOC approved and closed. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121950 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | During FY 2025-26, Total 07 Nos of MoC's were raised and 06 MoC's were approved. Only One MoC related to TT Parking SOP is under process | 3.17 | MOC status reviewed | 1308 | SITARGANJ DEPOT | MOC to be approved and closer of the same in time bound manner | SOD | Marketing | NUZ | 2026-02-28 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121950 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121950 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121950 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121950 | AUD-2026-02-2000010854ACN-2026-02-4000121950 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 31
PURANAM PRAKASH | 2026-03-31 | G SADASIVAN | 2026-03-31 | Officers operatedFoam generation of MEFG of TK-102 & monitor-15 | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124083 | Closed | G SADASIVAN | 2026-03-31 | Officers operated MEFG, Monitor near TK-102 and MEFG near OWS | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1777 | Hassan Terminal | Officers operatedFoam generation of MEFG of TK-102 & monitor-15 | SOD | Marketing | SWZ | 2026-03-15 | INADEQUATE SAFETY CULTURE | 8 | EMERGENCY | S4 | F2 | 2026-03-15 | AUD-2026-03-2000011172ACN-2026-03-4000124083 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124083 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124083 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124083 | AUD-2026-03-2000011172ACN-2026-03-4000124083 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 31
PURANAM PRAKASH | 2026-03-31 | G SADASIVAN | 2026-03-31 | Gantry cleanliness maintained .Photos attached . | SENIOR MANAGEMENT INSPECTION HASSAN TML | 2026-01-28 | AUD-2026-03-2000011172 | 2026-01-28 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124088 | Closed | G SADASIVAN | 2026-03-31 | House keeping is good. | 3.15 | Housekeeping & PPE usage checked | 1777 | Hassan Terminal | Gantry cleanliness maintained | SOD | Marketing | SWZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 9 | CONTRACTOR SAFETY | S3 | F3 | 2026-03-15 | AUD-2026-03-2000011172ACN-2026-03-4000124088 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011172ACN-2026-03-4000124088 | 2026-09-22 17:00 | 27.0455 | 211 | >20 | AUD-2026-03-2000011172 - ACN-2026-03-4000124088 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011172ACN-2026-03-4000124088 | AUD-2026-03-2000011172ACN-2026-03-4000124088 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-16 | Level–II Mock Drill was conducted on 13.03.2026 at HPCL Sitarganj IRD. Prior to the drill, table-top discussion and planning session was carried out to brief all concerned personnel about the scenario, response strategy, and coordination required during the emergency. Proper training and briefing were provided to all team members and they were made clearly aware of their roles and responsibilities as per the Fire Organisation Chart. During the mock drill, all team members effectively performed their assigned duties and responsibilities. The drill was successfully executed with the active participation and support of Mutual Aid members, Fire Brigade, Medical Team, Police, and other emergency response agencies. The effectiveness of the mock drill was assessed based on response time, coordination among teams, communication effectiveness, and adherence to assigned roles and responsibilities, which demonstrated satisfactory preparedness and emergency response capability of the depot. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121485 | Closed | PANWAR VIPIN SINGH | 2026-03-16 | Emergency response preparedness was verified by conducting a mock drill based on a scenario in which a fire broke out at Bay No. 01after the driver moved the TT without removing the unloading hoses and earthing cleat. This resulted in the hoses being pulled out,causing product spillage and a static spark subsequently ignited the spilled product, leading to a fire. All equipment were tested and performed well. However, Delay observed in supplying Foam barrel to Fire Fighting team and effective operation of Foam monitor was not observed. Mock drills must be conducted in letter and spirit and all members should be clear with their roles and responsibilities. | 2.5 | Emergency response preparedness reviewed | 1308 | SITARGANJ DEPOT | Effectiveness of the mock drill must be ensured through proper training and clear communication of roles and responsibilities to all concerned personnel. | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121485 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121485 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121485 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121485 | AUD-2026-02-2000010854ACN-2026-02-4000121485 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-25 | 1. Open path HCD repaired by OEM Drager safety & TAS vendor Icon Control and same installed and tested on 12.03.2026. 2. Numbering over each ESD done. Number plate avaialbe at each ESD in location. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121487 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | 1. Total 2 Nos of HCD available at the location. Out of which 01 nos is Open path and 01 Nos is Point type HCD. Open Path HCD is under maintenence as Calibration is required to be done hence it has been handed over to TAS vendor under AMC contrtact. Point type HCD No: 01 Located at Pump House operated; and found to be operated at 39% LEL 2. Tot 13 No of ESD available at the location. The Functionality of ESD has been checked during Mock drill conducted on 17th Feb'26 and found satisfactory. ESD NO: 07 activated placedin Control room and TAS log generated 3. All tanks are underground therefore HVLR and RSFPS is not available at the location | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1308 | SITARGANJ DEPOT | 1. Expedite the maintenance of Open path HCD 2. Numbering over each ESD to be mentioned | SOD | Marketing | NUZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-15 | AUD-2026-02-2000010854ACN-2026-02-4000121487 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121487 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121487 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121487 | AUD-2026-02-2000010854ACN-2026-02-4000121487 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-03 | Gate in front of the store-room adjoining the Admin Building locked and regular monitoring done for same. Location ensuring that nobody will visit to licensed area from this gate and shall use CBAC entry only. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121486 | Closed | PANWAR VIPIN SINGH | 2026-03-03 | During the Visit Access control at main gate was checked and found that CBAC Systen was finctional alongwith Biomatric operational at Maingate, Entry to Licence area and Control room. | 2.8 | Access control systems checked | 1308 | SITARGANJ DEPOT | Gate in front of the store-room adjoining the Admin Building should be kept in locked condition and personnel should move only thruthe CBAC system. | SOD | Marketing | NUZ | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010854ACN-2026-02-4000121486 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121486 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121486 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121486 | AUD-2026-02-2000010854ACN-2026-02-4000121486 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-25 | 1. Proposal submitted to HQO and budget shifted after ED Sir approval. 2. Workability sent to NZ CPO and advised CPO for work order of housekeeping and handling services. PO awarded to new contractors M/S MS Jat Enterprises and Jai bajrang Construction co. New employment card and i card issued to contract workmen effective 24.03.2026. 3. BG received from CCTV vendor and invoice of amcalso released. 4. TAS related issues of TAS vendor. A VC was conducted by DGM Operations & Automation, NZ-OND on 16th Feb'26 along with the TAS officer & LIC Sitarganj in which all the pending issues were discussed with the TAS AMC vendor (M/s. ICON). | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-02-4000121480 | Closed | PANWAR VIPIN SINGH | 2026-03-25 | Following pending issues were discussed : 1. Budget shifting for GL code of calibration charges. 2. Finalisation of PO for Housekeeping and Handling services 3. BG related issues of TAS vendor and CCTV vendor. 4. TAS related issues of TAS vendor. A VC was conducted by DGM Operations & Automation, NZ-OND on 16th Feb'26 along with the TAS officer & LIC Sitarganj in which all the pending issues were discussed with the TAS AMC vendor (M/s. ICON). Time-lines for closure of all the pending TAS issues were agreed upon by the vendor and a detailed MOM was prepared for the meeting. | 1.3 | Pending issues reviewed | 1308 | SITARGANJ DEPOT | 1. Location to take up with HQO thru zone for allocation of budget for the CE 2. Location to obtain workability of rates from the contractor and submit to CPO-NZ. 3. Location to obtain request from the TAS-CAMC provider as discussed during the VC with the vendor. 4. Location to maintain follow-up with the vendor to ensure closure of the pending issues as per the agreed time-lines | SOD | Marketing | NUZ | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010854ACN-2026-02-4000121480 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121480 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121480 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121480 | AUD-2026-02-2000010854ACN-2026-02-4000121480 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-31 | Flameproof lights installed on bay no 6 and lux level meeting as per PNGRB norms. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121484 | Closed | PANWAR VIPIN SINGH | 2026-03-31 | On 16/02/2026 @ 20:00 hrs, Lux level chaecked a various locations including 1. TT Gantry Bay No - 01 - 115 Lux 2. Admin Building - 300 Lux 3. Product Pump House - 366 Lux 4. U/G Tank Farm Area - 56 Lux 5. TT Sealing/Locking bay - 260 Lux 6. Roads - 26 Lux 7. Lighs are required in newly extended Bany no-06 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1308 | SITARGANJ DEPOT | 7. Lighting arangement to be provided in Bay No-06 | SOD | Marketing | NUZ | 2026-03-31 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121484 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121484 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121484 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121484 | AUD-2026-02-2000010854ACN-2026-02-4000121484 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
SINGH RAJ KUMAR | 2026-03-31 | PANWAR VIPIN SINGH | 2026-03-31 | 1. The room cleaned thoroughly, and measures taken to prevent the ingress of dust, housekeeping checklist maintained. point complied. 2. Fabrication work done and complied. 3. Paver blocks locked properly and PCC done in adjoint surface near soak pit. Pointcomplied. 4. New flower and composte were poured on flower pots in vertical garden. Point complied 5. One housekeeping staff dedicately deployed for gantry cleaning activity and advised for regular cleaning of gantry to ensure no oil stans. Point complied. 6. Foam Barel Shed fabricated point complied. 7. Hydrotesting of CO2 cylinder of 75Kg DCP done by Industrial Solution and certificate also provided for same. Point complied. 9. Correct size of Double compression glan used. Point complied. 10. Leakage arrested for FE2, and for FE 1, amc done. complied. 11. Overhead light in Bay No 6 installed. point complied. 12. Numbering of Smoke detectors done. point complied. 13. TT Branding under progress. | SENIOR MANAGEMENT INSPECTION SITARGANJ | 2026-02-18 13:00 | AUD-2026-02-2000010854 | 2026-02-16 15:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121953 | Closed | PANWAR VIPIN SINGH | 2026-03-31 | 1. Cleaning of TT Crew waiting room is required 2. Arrangement to be made to protect Fire water Hydrant Line at TT Parking area. Parked TT may cause damage to the facility 3. Paver block to be properly locked near Soal Pit in TT parking area 4. Vertical garden to be maintained properly 5. Presence of Oil is found in the recovery Tray placed near Bay no: 04 / 05 / 06 6. Proper covering arrangement to be provised for Foam Barrel placed in field. 7. 75 Kg DCP cylinder has been hydrotested 01/03/2025, however it cant be ascertained that external CO2 cylinder hydrotesting was done or not. Last testing date 12/10/2020 8. Double compression gland of Motor placed in Calibration shed was found to be over size 9. Sand buckets found to be partially filled with Sand in entire premises and also lumps found. 10. Leakage observed in both the Fire Engine and both Jockey pumps from Motor/Engine coupling point. 11. Lighting arrangement is to provided at Bay no-06 12. Numbering of Smoke Detectors (both False sealing & False flooring) to be done in Control room building 13. Some TTs have been observed without proper branding as per the transportation tender’s requirement. Location to take-up with the respective transporters to ensure proper branding by Feb’26 end. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1308 | SITARGANJ DEPOT | 1. The room must be cleaned thoroughly, and measures should be taken to prevent the ingress of dust. 2. Fabrication work for hydrant line guard is under progress 3. Paver blocks locked properly and PCC done in adjoint surface near soak pit. 4. Virtical garden 5. Mechanism to be emplied to avoid any oil presence 6. Foam Barel Shed to be provised 7. Hydrotesting of CO2 cylinder is to be done 9. Correct size of Double compression glan to be used 10. Leakage to be arrested in Fire Engines and Jockey pumps. 11. Overhead light in Bay No06 to be installed 12. Numbering of Smoke detectors to be done for visual identification. 13. TT Branding tobe ensured and 100% compliance to be ensured | SOD | Marketing | NUZ | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-02-2000010854ACN-2026-02-4000121953 | UK | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010854ACN-2026-02-4000121953 | 2026-08-26 17:00 | 54.0455 | 211 | >20 | AUD-2026-02-2000010854 - ACN-2026-02-4000121953 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010854ACN-2026-02-4000121953 | AUD-2026-02-2000010854ACN-2026-02-4000121953 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126435 | Open |  |  | Performance review done. The two NPCB projects for SSA compliance PO are delayed | 1.2 | Performance review conducted | 3693 | KAKINADA TML | The two NPCB projects to be completed within time by close followup with vendor. | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126435 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126435 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126435 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126435 |  | AUD-2026-04-2000011081ACN-2026-04-4000126435 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126436 | Open |  |  | Pending Issues reviewed . PESO initial approval received for conversion of Class A to Class C for 4 tanks. To apply for final approval | 1.3 | Pending issues reviewed | 3693 | KAKINADA TML | To obtain final approval for conversion of 4 tanks Class A to Class C | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126436 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126436 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126436 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126436 |  | AUD-2026-04-2000011081ACN-2026-04-4000126436 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126437 | Open |  |  | Expectations clearly communicated to officers regarding following of SOPs in Terminal Operations , Taking regular field rounds for safety inside Terminal , external pipeline monitoring, CCTV monitoring | 1.6 | Expectations clearly communicated to officers | 3693 | KAKINADA TML | CCTV monitoring on daily basis and records to be maintained. | SOD | Marketing | SCR | 2026-03-25 |  | 5 |  | S1 | F5 | 2026-03-25 | AUD-2026-04-2000011081ACN-2026-04-4000126437 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126437 | 2026-09-16 16:00 | 33.0872 | 205 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126437 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126437 |  | AUD-2026-04-2000011081ACN-2026-04-4000126437 | 21 |  | 26 | 80 | 0 | 0 | 30
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126439 | Open |  |  | Double contingency scenario not applicable for Kakinada Tml. Single contingency drill conducted. Mock Drill Observations for improvement i) Role clarity to be improved ii) Rescue team with stretcher took more time to reach iii) SCABA person without fire proximitysuit iv) Auxiliary team has not brought the emergency trolley to site. v) The rope tied to Person with SCABA for checking LEL is entangled due to which rope length is less , vi) Fire engines not run at full RPM vii) delay in operating Siren viii)Tank 4 not getting covered from two foam monitors | 2.2 | Double contingency scenario simulated; observations recorded | 3693 | KAKINADA TML | Short comings observed in the fire drill to be improved in next mock drills | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000126439 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126439 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126439 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126439 |  | AUD-2026-04-2000011081ACN-2026-04-4000126439 | 21 |  | 26 | 80 | 0 | 0 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126442 | Open |  |  | CCTV functioning checked . 14 out 15 cameras are working . CCTV camera coverage not available along the boundary wall. CCTV monitornot available in Security cabin | 2.6 | CCTV functioning checked | 3693 | KAKINADA TML | Non working camera to be rectified and AMC to be placed . Additional CCTV cameras to be procured for covering the boundar wall area. CCTV monitor to be provided in security cabin. | SOD | Marketing | SCR | 2026-04-10 |  | 5 |  | S1 | F5 | 2026-04-10 | AUD-2026-04-2000011081ACN-2026-04-4000126442 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126442 | 2026-09-16 16:00 | 33.0872 | 221 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126442 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126442 |  | AUD-2026-04-2000011081ACN-2026-04-4000126442 | 21 |  | 26 | 80 | 0 | 0 | 32
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126443 | Open |  |  | Not available | 2.8 | Access control systems checked | 3693 | KAKINADA TML | Access control system to be provided , proposal to be submitted | SOD | Marketing | SCR | 2026-04-15 |  | 5 |  | S1 | F5 | 2026-04-15 | AUD-2026-04-2000011081ACN-2026-04-4000126443 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126443 | 2026-09-16 16:00 | 33.0872 | 226 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126443 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126443 |  | AUD-2026-04-2000011081ACN-2026-04-4000126443 | 21 |  | 26 | 80 | 0 | 0 | 33
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126446 | Open |  |  | MDSA Pending Points28 and SSA one pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 3693 | KAKINADA TML | Compliance of Pending MDSA and SSA points to be expedited | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000126446 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126446 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126446 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126446 |  | AUD-2026-04-2000011081ACN-2026-04-4000126446 | 21 |  | 26 | 80 | 0 | 0 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000126447 | Open |  |  | Full field round completed (gantry/tank farm/jetty/product pump house/Fire Pump House/ security/admin).Tanks TK 2 and TK4 roof plates rusting observed ,painting to be done, rain water to be removed to avoid further corrosion. 300 M of 20 pipeline from exchange pit to Jetty is heavily corroded , the pipeline is not in use, Pressure guages in product pump house calibration is due, Fire extinguishers servicing date not painted, Fire buckets sand is not full, MCC room Electrical gloves due for testing, ON/OFF Knobs missing for lighting panel. Concertina Coil at some places not proper. Security : Lady Security guard not available and separate cabin for checking /frisking of female workers/ visitors is not available. Signage board of No Drone Zone not available. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 3693 | KAKINADA TML | 1)Tanks TK 2 and TK4 roof painting to be done, rain water to be removed to avoid further corrosion. 2)Pressure guages in product pump house to be calibrated, Fire extinguishers servicing date to be painted, Fire buckets sand to be replenished, MCC room Electricalgloves due to be replaced, ON/OFF Knobs to be provided for lighting panel. 3) To provide lady security guard and separate cabin forchecking/frisking of female workers /visitors.4) No Drone zone signage board to be provided 5) Concertina Coil at some places needsto be rectified. | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126447 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126447 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126447 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126447 |  | AUD-2026-04-2000011081ACN-2026-04-4000126447 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000126448 | Open |  |  | Lux level improvement NPCB project is delayed | 4.3 | Project progress reviewed | 3693 | KAKINADA TML | to be completed by 30.04.2026 | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126448 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126448 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126448 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126448 |  | AUD-2026-04-2000011081ACN-2026-04-4000126448 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000126449 | Open |  |  | 25 KG DCP FE hoses damaged , painting faded. Terminal internal pipelines rusting observed at few places, work permits not made for DCP FE Servicing | 4.4 | Quality of PM compliance reviewed | 3693 | KAKINADA TML | 25 KG DCP FE hoses to be replaced , printing to be done,. Terminal internal pipelines rusting observed at few places painting to beto be done at rusted areas, work permits to be made for DCP FE Servicing and all the maintenance works . | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000126449 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126449 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126449 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126449 |  | AUD-2026-04-2000011081ACN-2026-04-4000126449 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127850 | Open |  |  | Scrap worth Rs. 5.0 Lakhs disposed and one more RFD for scrap worth Rs. 1.5 Lakhs auction done | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 3693 | KAKINADA TML | Old hose pipes , misc iron scrap RFD to be made again. Old hose pipes lying adjacent to boundary wall to be shifted to scrap yard. | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000127850 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000127850 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000127850 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000127850 |  | AUD-2026-04-2000011081ACN-2026-04-4000127850 | 21 |  | 26 | 80 | 0 | 0 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127851 | Open |  |  | 3 nos 5 KVA UPS received from Suryapet Terminal are idling | 6.1 |  | 3693 | KAKINADA TML | To coordinate and send to any needy location | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000127851 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000127851 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000127851 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000127851 |  | AUD-2026-04-2000011081ACN-2026-04-4000127851 | 21 |  | 26 | 80 | 0 | 0 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127852 | Open |  |  | Two SOP Boards lying in Calibration shed | 6.2 |  | 3693 | KAKINADA TML | Two SOP Boards lying in Calibration shed TO BE PUT TO USE | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000127852 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000127852 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000127852 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000127852 |  | AUD-2026-04-2000011081ACN-2026-04-4000127852 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127853 | Open |  |  | Boundary Wall cracks observed on either side of emergency exit gate | 6.3 |  | 3693 | KAKINADA TML | Boundary wall cracks to be repaired | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011081ACN-2026-04-4000127853 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000127853 | 2026-09-16 16:00 | 33.0872 | 241 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000127853 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000127853 |  | AUD-2026-04-2000011081ACN-2026-04-4000127853 | 21 |  | 26 | 80 | 0 | 0 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127854 | Open |  |  | Only two VHF sets available and balance are beyond repair | 6.4 |  | 3693 | KAKINADA TML | New VHF sets to be procured. | SOD | Marketing | SCR | 2026-05-31 |  | 5 |  | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011081ACN-2026-04-4000127854 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000127854 | 2026-09-16 16:00 | 33.0872 | 272 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000127854 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000127854 |  | AUD-2026-04-2000011081ACN-2026-04-4000127854 | 21 |  | 26 | 80 | 0 | 0 | 39
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127858 | Open |  |  | Improvement Plans discussed. | 1.8 | Improvement plans discussed | 1953 | RAJAHMUNDRY TERMINAL | Tank Repairs to be completed for TK2A and TK 3B and put back in operation | SOD | Marketing | SCR | 2026-06-30 |  | 5 |  | S1 | F5 | 2026-06-30 | AUD-2026-04-2000011082ACN-2026-04-4000127858 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127858 | 2026-07-22 18:30 | 88.983 | 302 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127858 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127858 |  | AUD-2026-04-2000011082ACN-2026-04-4000127858 | 21 |  | 26 | 80 | 1 | 2 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127861 | Open |  |  | CCTV functioning checked . 43 out 45 cameras are active in VA. Out of the total 51 CCTV cameras , 3 cameras are not working. Two cameras sent for repair and one camera is beyond repair. UG tank camera angle to be adjusted, NR HVLR CP6 camera angle to be adjusted,Admin office front side camera not clear due to excess light reflection, Watch Tower 1 perimeter camera angle to be adjusted , Watch Tower 2 perimeter camera is not working | 2.6 | CCTV functioning checked | 1953 | RAJAHMUNDRY TERMINAL | CCTV cameras to be realigned for proper coverage . To follow up with vendor for repair of the two cameras , one new camera to be procured | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011082ACN-2026-04-4000127861 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127861 | 2026-07-22 18:30 | 88.983 | 241 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127861 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127861 |  | AUD-2026-04-2000011082ACN-2026-04-4000127861 | 21 |  | 26 | 80 | 1 | 2 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127863 | Open |  |  | HVLR/HCD/ESD functionality checked. Initially open path HCD near OMC Pump House found not working , after reset in Control room HCDfunctioned however the hooter sound is low. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1953 | RAJAHMUNDRY TERMINAL | HCDs Functioning to be checked regularly and records to be maintained. Additional Hooters to be placed at Product pump house and atOMC pump House | SOD | Marketing | SCR | 2026-04-30 |  | 5 |  | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011082ACN-2026-04-4000127863 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127863 | 2026-07-22 18:30 | 88.983 | 241 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127863 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127863 |  | AUD-2026-04-2000011082ACN-2026-04-4000127863 | 21 |  | 26 | 80 | 1 | 2 | 35
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127869 | Open |  |  | MDSA Pending Points are nil , ESA two points pending and SSA two points pending | 3.18 | OISD/MDSA/SSA compliance reviewed | 1953 | RAJAHMUNDRY TERMINAL | Pending ESA and SSA point to be completed as per the given target dates | SOD | Marketing | SCR | 2026-05-31 |  | 5 |  | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011082ACN-2026-04-4000127869 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127869 | 2026-07-22 18:30 | 88.983 | 272 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127869 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127869 |  | AUD-2026-04-2000011082ACN-2026-04-4000127869 | 21 |  | 26 | 80 | 1 | 2 | 39
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127873 | Open |  |  | Scrap worth Rs.10.0 Lakhs disposed. Scrap items like old drums , wooden boxes, iron cut pieces , old cables , valves RFD pending | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1953 | RAJAHMUNDRY TERMINAL | RFD for remaining scrap items to be made and chain link fencing to be provided for scrap yard. | SOD | Marketing | SCR | 2026-03-30 |  | 5 |  | S1 | F5 | 2026-03-30 | AUD-2026-04-2000011082ACN-2026-04-4000127873 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127873 | 2026-07-22 18:30 | 88.983 | 210 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127873 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127873 |  | AUD-2026-04-2000011082ACN-2026-04-4000127873 | 21 |  | 26 | 80 | 1 | 2 | 30
[5 empty] | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-04-4000127874 | Open |  |  | MFM based accounting being done for OMC(IOC) PLTs. | 5.1 | MFM based accounting at Pipeline and OMC location | 1953 | RAJAHMUNDRY TERMINAL | VVSPL receipts accounting thru MFM to be commenced after stabilisation study of MFM qty vs Physical dip qty in co-ordination with VVSPL_RBS | SOD | Marketing | SCR | 2026-04-05 |  | 5 |  | S1 | F5 | 2026-04-05 | AUD-2026-04-2000011082ACN-2026-04-4000127874 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127874 | 2026-07-22 18:30 | 88.983 | 216 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127874 | 532 | 8294 | 21 | 8294 | 197 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011082ACN-2026-04-4000127874 |  | AUD-2026-04-2000011082ACN-2026-04-4000127874 | 21 |  | 26 | 80 | 1 | 2 | 31
TILKAN RAVINDRA KUMAR | 2026-04-01 |  |  | All Monitors in Plant are Checked by third party .Necessary servicing is done Now all monitors are in good owrking condition | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125852 | Closed | TILKAN RAVINDRA KUMAR | 2026-04-01 | Officer operated Monitor near TK-302 and checked for smoothness of operation, needs improvement. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1833 | COCHIN BLACK TERMINAL | Corrective action to be taken for smooth operation of monitor | SOD | Marketing | CZR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125852 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125852 | 2026-09-08 16:00 | 41.0872 | 212 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125852 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125852 | AUD-2026-03-2000011134ACN-2026-03-4000125852 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 31
TILKAN RAVINDRA KUMAR | 2026-04-01 |  |  | MRF Kottayam route correction is done.No zero violations in this route | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125855 | Closed | TILKAN RAVINDRA KUMAR | 2026-04-01 | VTS deviations are being monitored by locations. Issues on generations of route violations at kottayam routes are identified and corrective actions taken by timely invoicing. | 3.3 | VTS deviations reviewed | 1833 | COCHIN BLACK TERMINAL | Route corrections to be done in kottayam area at the earliest | SOD | Marketing | CZR | 2026-03-31 | NATURAL DISASTERS OR UNFORESEEN EVENTS | 8 | PROCESS SAFETY | S4 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125855 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125855 | 2026-09-08 16:00 | 41.0872 | 212 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125855 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125855 | AUD-2026-03-2000011134ACN-2026-03-4000125855 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 31
BANOTHU KRISHNA | 2026-04-01 | Sreelal P P | 2026-04-01 | Location has shared Manpower details including retiring officer details with zone vide mail dt 05.03.2026 | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125834 | Closed | Sreelal P P | 2026-04-01 | Interacted with Officers. Concerns regarding manpower faced by officers was discussed. Location needs E0 Officers in place of retiring employees. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1845 | IRUMPANAM TERMINAL | Manpower details including retiring officer details to be shared with zone | SOD | Marketing | CZR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 2 | EMERGENCY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125834 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125834 | 2026-09-02 16:30 | 47.0663 | 212 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125834 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011133ACN-2026-03-4000125834 | AUD-2026-03-2000011133ACN-2026-03-4000125834 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 31
BANOTHU KRISHNA | 2026-04-01 | Sreelal P P | 2026-04-01 | Location has received 8.3KL ARAFFF foam under the HQO contract. Materials received on 17.03.2026. Gate pass attached for reference.GRN approved vide 5001188269 and 5001188267 respectively for expense booking | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125837 | Closed | Sreelal P P | 2026-04-01 | Foam Inventory is adequate as per OISD STD 244 and 117. AFFF Requirement - 8.08 AFFF Available - 10KL ARAFFF Requirement - 8.88KL ARAFFF Available - 13KL Location has released callup order for additional 8.3KL of ARAFFF foam under central contract. Expecteddate of delivery 20.03.2026 | 2.9 | Foam inventory verified | 1845 | IRUMPANAM TERMINAL | Location to follow up for getting the foam in time. Expense booking to be completed | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ASSET INTEGRITY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125837 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125837 | 2026-09-02 16:30 | 47.0663 | 212 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125837 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125837 | AUD-2026-03-2000011133ACN-2026-03-4000125837 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Tank farm valve manifold lux level improved by proper lighting placement. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122045 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Lux requirement/ Lux achieved: 1. Road: 10/21 2. Transformer arae: 100/152 3. ETP area: 60/122 4. Tank farm valve manifold area: 60/42 5. TT gantry platform area: 60/102 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1278 | JODHPUR TERMINAL | Lux reading was lesser than requirement at valve manifold area of TK12. Pls check. Same needs to be checked for other HSD tanks. | SOD | Marketing | NWF | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 5 | ENVIRONMENTAL | S1 | F5 | 2026-03-15 | AUD-2026-02-2000010963ACN-2026-02-4000122045 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122045 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122045 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122045 | AUD-2026-02-2000010963ACN-2026-02-4000122045 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Letter issued to the security agency to ensure that the frisking is being done properly and utmost care is ensured in security of the premises. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122046 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Check for three different periods: 1. 31.12.2025, 17.00 hr to 17.30 hr (TT gantry area) 2. 30.12.2025, 08.15 hr to 09.00 hr (Security gate frisking area) 3. 25.11.2025 (seurity gate frisking area) 1. TT crews were wearing PPE. Fire ext. were kept at required place. 2. Though Security was frisking incomers, however, frisking was only for name sake. It was not being done properly. Location to give training and take it strictly with security contractor. Letter to be issued to security contractor. 3. It was checked to ascertain whether location is keeping 92 days back up or not. It is okay | 2.6 | CCTV functioning checked | 1278 | JODHPUR TERMINAL | 2. Training to be enhanced | SOD | Marketing | NWF | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 4 | ENVIRONMENTAL | S1 | F4 | 2026-03-15 | AUD-2026-02-2000010963ACN-2026-02-4000122046 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122046 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122046 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122046 | AUD-2026-02-2000010963ACN-2026-02-4000122046 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | VA exceptions are corrected after taking up with the HQO. any lapses are being reported in portal and training is being imparted accordingly. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122047 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | VA system alerts were checked for last three months: Non-compliance towards PPE: 4 cases Non-compliance towards Fire ext: 2 Non-compliance towards wheel choke: 6 Perimeter intrusion in non-working hr: 7 cases Emergency gate opening cases: 2 No. of cases which were declared as false in last 3 months: Non-compliance towards PPE: 0 Non-compliance towards Fire ext: 2 Non-compliance towards wheel choke: 6 Perimeter intrusion in non-working hr: 6 cases Emergency gate opening cases: 1 | 2.7 | VA alerts checked / analysed | 1278 | JODHPUR TERMINAL | Location is required to keep close watch on VA alert | SOD | Marketing | NWF | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122047 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122047 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122047 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122047 | AUD-2026-02-2000010963ACN-2026-02-4000122047 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Foam calcuation is shared with the zone for review. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122048 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | 1. 8.5 Kl x 2 tanks were having only 985 litre x 2 = 1.97 KL foam. Foam was thick and level indicator was not showing foam inside horizontal tank. Foam level was measured by using dip rod. 2. One more 5 Kl foam bladde tank was found fully top up. 3. Foam requirement is 16 KL as per MOU with MARG members 4. Location informed that each of the 49 WCFM is having 200 litre foam barrel. Total foam quantity is approx 19 Kl inside Terminal | 2.9 | Foam inventory verified | 1278 | JODHPUR TERMINAL | 1. Both 8.5 KL capacity foam tanks are almost empty. 2. Whether all 49 WCFM is having 200 litre foam barrels and all barrels are topped up, this needs to be checked by location. 3. Location to check 1 KL daughter tank connected with all 7 HVLRs. Pls check if itis topped up? As 8.5 KL x 2 tanks are not having foam, how location will replenish foam in HVLR daughter tanks? | SOD | Marketing | NWF | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 3 | ASSET INTEGRITY | S1 | F3 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122048 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122048 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122048 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122048 | AUD-2026-02-2000010963ACN-2026-02-4000122048 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | same will be corrected in next TAS vendor person visit. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.10 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122049 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Fire water required is 2840 KL. Water level is more than requirement. However, water required is not correctly populated in TAS screen. This needs to be rectified | 2.10 | Fire water levels verified | 1278 | JODHPUR TERMINAL | Pls correct water storage required in TAS | SOD | Marketing | NWF | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122049 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122049 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122049 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122049 | AUD-2026-02-2000010963ACN-2026-02-4000122049 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Security personnels are the main gate are trained and advised to ensure to pass on the information if anything unusual or any alarmis generated by the system. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122350 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | A. HVLR checked (two nos.). 1. One HVLR was operated. However, Fire engine didn't start. It didn't make required pressure. HVLR water was not reaching to tank. 2. 2nd HVLR operated. It worked fine. B. RSFPS cheked: 1. RSFPS was operfated from control room in test mode for TK5 (slop tank). It worked fine. 2. RSFPS was operated from push button (on ground area) for TK6 (slop tank). It worked fine. C. ESD was checked. It worked well. D. HCD -9 was tested for working. Local hooter sounded. It also gave signal at control room. However, there was no response from security personnel. If any unhealthy signal omes, it reflects at panel displayed at security room. they should inform to officer for any unhealthy signal. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1278 | JODHPUR TERMINAL | A. On further checking, it was observed that Fire engine no. 2 is not cranking properly. It starts after two /three cranks. It is also causing damage to teeth of self starter gear. There is also gasket leakage from the body of fire engine. This engine has to be taken under maintenance. As location is having only 1 +1 fire engine, a time bound action plan with MOC approval is required. B. Okay C. Okay D. Training to be given to security | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 3 | ENVIRONMENTAL | S1 | F3 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122350 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122350 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122350 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122350 | AUD-2026-02-2000010963ACN-2026-02-4000122350 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Training are imparted in quarterly basis, records are being maintained. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122351 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | New Officer operated one 25 kg DCP and two nos. of HVLR. They operated well. However, following observations were made: 1. officerjoined one year back does not have knowledge of LEL, HCD, Dyke Valve Position indicator, HVLR etc. She was trained one year back. After that no training to her. 2. Contract enginners do not have knowledge of all these fire fighting facilities, though he is a part of Fire Auxiliarry team. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1278 | JODHPUR TERMINAL | Training to be enhanced to new joinees and contract engineers. | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122351 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122351 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122351 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122351 | AUD-2026-02-2000010963ACN-2026-02-4000122351 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Daily morning meetings are being conducted with the TT crew for synergy. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000122352 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Meeting was called with TT crew of Jodhpur Tml on 25.02.2026. One hr interaction was carried out with them. Emergency preparedness checked. It require further training. | 2.15 | TT crew roadside emergency procedures checked | 1278 | JODHPUR TERMINAL | Zone has shared SOP in Hindi for actions to be taken by TT crew in case of emergency (both inside terminal as well as outside termnal. It needs to be displayed at prominent place and training to be given to all TT crew | SOD | Marketing | NWF | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122352 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122352 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122352 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122352 | AUD-2026-02-2000010963ACN-2026-02-4000122352 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Similar actions are being taken fro other TTs also. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122353 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Checked for following three TTs: 1. RJ19GJ5979 2. RJ22GB6345 3. RJ07GG0742 Fittings were okay. Driver is keeping master switch in off condition. Hand break is ON | 3.1 | TT fittings & discipline checked | 1278 | JODHPUR TERMINAL | Branding of TT no. RJ22GB6345 & RJ22GB0745 was not good. To be done. Location needs to ensure 100% branding in all TTs. Location isalso requested to share fortnightly data of TT branding. | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 3 | EMERGENCY | S1 | F3 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122353 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122353 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122353 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122353 | AUD-2026-02-2000010963ACN-2026-02-4000122353 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Dip checked are being ensured as per dip elimination file note. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122354 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Checked for 5 TTs. Following variations observed compartment wise: 1. RJ19GT5979: +3 mm/+2 mm/+1 mm/+1 mm 2. RJ22GB6345: +2 mm/+1mm/+1 mm 3. RJ07GG0742: +1 mm/+3 mm/ok 4. RJ54GA1442: -1 mm/+2 mm/+1 mm/+1 mm/+4 mm 5. RJ19GF1914: ok/ok/+1 mm/+1 mm | 3.2 | Post-loading dip checks verified | 1278 | JODHPUR TERMINAL | Variation observed in two trasnport Tts. Three DCT Tts performed well. It was advised during my last visit to Jodhpur Tml (15th and16th Dec, 2025) to check dip of all transport Tts and share the result. If any transport TT is consistently showing variation equalto or greater than +3 mm, pls go for recalibration of that TT. | SOD | Marketing | NWF | 2026-03-31 | OUTDATED OR COMPLEX SOPS | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122354 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122354 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122354 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122354 | AUD-2026-02-2000010963ACN-2026-02-4000122354 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | corrective actions are the SOP is being taken, letters being issued and reply being sought from the transporters. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122355 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | List of VTS deviations for the period 05.01.2026 to 22.02.2026 shared with locations by Zone. There are cases where route corrections may be required. Multiple loaded Tts are stopping at one place. Location is required to take explanation from transporter. If explanation is not satisfactory, location needs to take up with Administration, including SP. If concerned DCT or transporter is not giving reply of our letter and their TT is still stopping at that place, then TT loading has to be stopped. It is also observed that location is keeping separate file for letter issued and letter replied. Pls keep letter issued and replied together in one file only | 3.3 | VTS deviations reviewed | 1278 | JODHPUR TERMINAL | Location to take corrective action and revert. | SOD | Marketing | NWF | 2026-03-07 | LACK OF TRAINING OR COMPETENCY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-07 | AUD-2026-02-2000010963ACN-2026-02-4000122355 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122355 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122355 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122355 | AUD-2026-02-2000010963ACN-2026-02-4000122355 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | calibrations done within time, same shalll be ensured next time. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122356 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Calibration of 4 prover tanks are due on 11.03.2026. Location was advised to make payment by 28th Feb | 3.13 | K-factor changes reviewed (if any) | 1278 | JODHPUR TERMINAL | Payment to be made and timely renewal of calibration of prover tanks (both mobile and fixed0 to be done. | SOD | Marketing | NWF | 2026-03-11 | LACK OF TRAINING OR COMPETENCY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-11 | AUD-2026-02-2000010963ACN-2026-02-4000122356 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122356 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122356 | 532 | 8294 | 21 | 8294 | 222 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122356 | AUD-2026-02-2000010963ACN-2026-02-4000122356 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | housekeeping being ensured, leakages being corrected as and when required. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122357 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Housekeeping needs to be improved. Drain surrounding the gantry not clean. TF PC area not clean. There were old layers of dirt/dustunderneath pipeline in tank farm area, Pumps (Foam) were not clean. There was leakage in the gantry in few bays. Leakage needs to be arrested. Floating roof of TK5 and TK6 were very dirty. It is not being cleaned regularly. | 3.15 | Housekeeping & PPE usage checked | 1278 | JODHPUR TERMINAL | Location informed that due to recent cleaning of sprinkler line in some of the tanks, TF PCC area was not clean. Drains were full of water. This is noted. However, it is already informed that we need to make housekeeping schedule of all jobs with frequency of cleaning. Contractor should be made responsible for cleaning the shed/equipment/pipeline/drain etc. Our housekeeping po is manpower based. Contractor will not have any stake to get the job done thru contract labour. There should be one control register which shows job done with date and sign of contractor/officer. | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 4 | ENVIRONMENTAL | S1 | F4 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122357 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122357 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122357 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122357 | AUD-2026-02-2000010963ACN-2026-02-4000122357 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | MOC for fire engine maintenance raised in portal and approval taken. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122359 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | MOC not taken for overriding Gantry Permissive byepass. Whenever, main fire engine is operated in local, system is defined for stopping gantry loading. It was byepassed during the period when one fire engine was under breakdown. MOC not taken. | 3.17 | MOC status reviewed | 1278 | JODHPUR TERMINAL | Location to follow all SOPs | SOD | Marketing | NWF | 2026-03-05 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122359 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122359 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122359 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122359 | AUD-2026-02-2000010963ACN-2026-02-4000122359 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | total 3 points pending as of now for CSA, which are being complied. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000122360 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Comprehensive Audit (Nov 25): 14 points pending out of 66, t4S audit: Nil point pending, Sr. Mgmt Audit: all points complied | 3.18 | OISD/MDSA/SSA compliance reviewed | 1278 | JODHPUR TERMINAL | All points to be complied by 31.03.2026. Weekly status to be shared | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122360 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122360 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122360 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122360 | AUD-2026-02-2000010963ACN-2026-02-4000122360 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | All projects competed as of now. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122361 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Only three pending projects. All will be closed by 31st March 2026 | 4.3 | Project progress reviewed | 1278 | JODHPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122361 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122361 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122361 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122361 | AUD-2026-02-2000010963ACN-2026-02-4000122361 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | All RFDs uploaded and approved. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122362 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Only one RFD is pending to be uploaded. Balance all RFD uploaded. Last date of make location scrap free is 31.03.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1278 | JODHPUR TERMINAL | Pls upload all RFds in portal. Ensure that location becomes scrap free by 31.03.2026 | SOD | Marketing | NWF | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122362 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122362 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122362 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122362 | AUD-2026-02-2000010963ACN-2026-02-4000122362 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Study being done in order to ensure MFM based booking, follow up being done with the ASPL. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-02-4000122363 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | MFM based accounting is not being done. Location to make study and share fortnightly report as per format shared | 5.1 | MFM based accounting at Pipeline and OMC location | 1278 | JODHPUR TERMINAL | Pls ensure MFM based accounting in PLT | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-02-2000010963ACN-2026-02-4000122363 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122363 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122363 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122363 | AUD-2026-02-2000010963ACN-2026-02-4000122363 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | All bio diesel procured. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122367 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | All allocated quantity of Bio diesel to be procured from vendor and to be consumed | 6.4 | Consumption of Bio Diesel quantity | 1278 | JODHPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122367 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122367 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122367 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122367 | AUD-2026-02-2000010963ACN-2026-02-4000122367 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | clamps prepared for all types of pipes. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122368 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | To handle sudden leakage from product pipeline, location should have safety kit. | 6.5 | Handling emergency | 1278 | JODHPUR TERMINAL | Pls make clamp and nipple arrangement for taking care of any leak in product pipeline. Make different sizes of clamps. | SOD | Marketing | NWF | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | ENVIRONMENTAL | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010963ACN-2026-02-4000122368 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122368 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122368 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122368 | AUD-2026-02-2000010963ACN-2026-02-4000122368 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Monitoring being done and a register is being maintained for the same. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.9 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122372 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Monthly monitoring of inventory of additive stock (Petrol plus, diesel plus, Corrosion Inhibitor etc) to be done. | 6.9 | Additive stock monitoring | 1278 | JODHPUR TERMINAL | Pls ensure record of physical vs book stock on monthly basis | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122372 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122372 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122372 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122372 | AUD-2026-02-2000010963ACN-2026-02-4000122372 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | RTGP being recorded as per the advise. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122371 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Pending RTGP record (month wise) to be parepared on RTGP register itself. List of open RTGP as per security vs list of open RTGP asper online gate pass portal | 6.8 | RTGP monitoring | 1278 | JODHPUR TERMINAL | Monthly monitoring of RTGP by security to be done | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122371 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122371 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122371 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122371 | AUD-2026-02-2000010963ACN-2026-02-4000122371 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | All log books are being signed by the respective responsible officer. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122370 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Log books are required to be signed by officers | 6.7 | Log Book | 1278 | JODHPUR TERMINAL | Pls ensure | SOD | Marketing | NWF | 2026-03-05 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-05 | AUD-2026-02-2000010963ACN-2026-02-4000122370 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122370 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122370 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122370 | AUD-2026-02-2000010963ACN-2026-02-4000122370 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Being implemented with follow up with the transporters. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122373 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Discounted toll to be implemented | 6.10 | Discounted toll | 1278 | JODHPUR TERMINAL | There is Gazette notification. Email shared with location on discounted toll concept. Pls implement | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122373 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122373 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122373 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122373 | AUD-2026-02-2000010963ACN-2026-02-4000122373 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | all old lubes are cleared with help of lube SBU. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122374 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Old Lubes are required to be liquidated | 6.11 | Liquidation of slow moving Lube | 1278 | JODHPUR TERMINAL | Pls coordinate with Lube Department. Visit of Technical officer is already done by Mr. darpan. Pls ensure liquidation of all old lubes | SOD | Marketing | NWF | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 1 | ENVIRONMENTAL | S1 | F1 | 2026-04-30 | AUD-2026-02-2000010963ACN-2026-02-4000122374 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122374 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122374 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122374 | AUD-2026-02-2000010963ACN-2026-02-4000122374 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 31
MEENA HIMANSHU | 2026-04-02 | SAINI JASVINDER SINGH | 2026-04-01 | Locks being checked by the LIC key. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.12 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122375 | Closed | SAINI JASVINDER SINGH | 2026-04-01 | Intelligent Key was used to check EM lock conditions of Tts. Two transport Tt and three DCT Tts were checked and found okay. LIC also checked from his own key. | 6.12 | Checking of lock by Intelligent key | 1278 | JODHPUR TERMINAL | LIC should give request letter to M/s Sterna for new locks. Pls check locks by using Intelligent key on weekly basis. 5 Tts per week. Revert with result. | SOD | Marketing | NWF | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122375 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122375 | 2026-09-25 20:45 | 23.8893 | 213 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122375 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122375 | AUD-2026-02-2000010963ACN-2026-02-4000122375 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 31
KAPIL DEV | 2026-04-03 | SINGH KUNAL | 2026-04-03 | Vadodara Terminal is dispatching sufficient bio diesel blending in TT dispatches as per the available indents. Vendor has been intimated to supply biodiesel. | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124917 | Closed | KAPIL DEV | 2026-04-03 | It was observed that location is not ensuring sufficient bio diesel blending in TT dispatches. Advised location to follow up and ensure improved performance. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000010974ACN-2026-03-4000124917 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124917 | 2026-09-10 21:00 | 38.8788 | 214 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124917 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124917 | AUD-2026-03-2000010974ACN-2026-03-4000124917 | 21 | 21 | 26 | 80 | 0 | -26 | 30 | 31
KAPIL DEV | 2026-04-03 | SINGH KUNAL | 2026-04-03 | 100% indent execution is being carried out for valid indents | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124918 | Closed | SINGH KUNAL | 2026-04-03 | The efficacy of present available transport TT fleet was discussed in detail and advised location for ensuring 100% indent execution at all times. | 1.8 | Improvement plans discussed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124918 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124918 | 2026-09-10 21:00 | 38.8788 | 214 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124918 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124918 | AUD-2026-03-2000010974ACN-2026-03-4000124918 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 31
KAPIL DEV | 2026-04-03 | SINGH KUNAL | 2026-04-03 | Issue has been taken up with the VA vendor and vendor has confirmed that they are working on this false alerts | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000124919 | Closed | SINGH KUNAL | 2026-04-03 | Yes done. Mainly related to Fire extinguisher at TTG false alert. Location to take corrective action with vendor | 2.7 | VA alerts checked / analysed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000010974ACN-2026-03-4000124919 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124919 | 2026-09-10 21:00 | 38.8788 | 214 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124919 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124919 | AUD-2026-03-2000010974ACN-2026-03-4000124919 | 21 | 21 | 26 | 80 | 0 | -26 | 35 | 31
KAPIL DEV | 2026-04-03 | SINGH KUNAL | 2026-04-03 | Projects has been closed as per the EDC without time extension | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124925 | Closed | SINGH KUNAL | 2026-04-03 | Yes reviewed and observed that projects due for closure in Mar'26 are well on track. | 4.3 | Project progress reviewed | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000010974ACN-2026-03-4000124925 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124925 | 2026-09-10 21:00 | 38.8788 | 214 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124925 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124925 | AUD-2026-03-2000010974ACN-2026-03-4000124925 | 21 | 21 | 26 | 80 | 0 | -26 | 30 | 31
KAPIL DEV | 2026-04-03 | SINGH KUNAL | 2026-04-03 | Disposal is completed | SENIOR MANAGEMENT INSPECTION VADODARA TE | 2026-03-17 | AUD-2026-03-2000010974 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124926 | Closed | SINGH KUNAL | 2026-04-03 | Yes done. 1 RFD is under disposal stage. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1410 | VADODARA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S2 | F1 | 2026-03-31 | AUD-2026-03-2000010974ACN-2026-03-4000124926 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010974ACN-2026-03-4000124926 | 2026-09-10 21:00 | 38.8788 | 214 | >20 | AUD-2026-03-2000010974 - ACN-2026-03-4000124926 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010974ACN-2026-03-4000124926 | AUD-2026-03-2000010974ACN-2026-03-4000124926 | 21 | 21 | 26 | 80 | 0 | -26 | 31 | 31
[5 empty] | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127444 | Open |  |  | Location to dispose of Iron scrap available, DG, Panels etc. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-30 |  | 1 |  | S1 | F1 | 2026-04-30 | AUD-2026-04-2000011243ACN-2026-04-4000127444 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127444 | 2026-08-26 17:00 | 54.0455 | 241 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127444 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011243ACN-2026-04-4000127444 |  | AUD-2026-04-2000011243ACN-2026-04-4000127444 | 21 |  | 26 | 80 | 4 | 4 | 35
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | i) Daily dip checking has been ensured by officers. They have started dip checking and dips are updated in SAP on daily basis. ii) LIC has ensured to carryout the surprise checks of loaded TTs. iii)Location has started providing require handson training to improve the operational knowledge of the safety critical equipment. iv)All officers has been advised to timley report - NMs,UCs,UAs in SAP and the same is being followed. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127092 | Closed | MAJUMDER BIRAJ | 2026-04-03 | Day-to-day operational activities were reviewed. Officers were advised to get engaged in field for TT dip checking / TT fittings checking. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1644 | KOLKATA-I TERMINAL | Location to improve DIP checking by officers at TT gantry for 100% of TTs loaded and maintain records. LIC to carry out surprise check of loaded TTs. TTs. All safety fittings of TTs to be checked thoroughly. All the officers were advised to have hands on training and operational knowledge of all the safety critical equipment. All officers to start reporting of Near misses, UCs, UAs in SAP | SOD | Marketing | EZ | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127092 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127092 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127092 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127092 | AUD-2026-03-2000010730ACN-2026-03-4000127092 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | Siphon Breaker has been installed in all operating MS tanks | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127093 | Closed | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | Performance review of officer carried out and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1644 | KOLKATA-I TERMINAL | Siphon Breaker job in the MS tanks to be expedited so as to close the open ESA recommendation. | SOD | Marketing | EZ | 2026-03-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 2 | ASSET INTEGRITY | S2 | F1 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127093 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127093 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127093 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127093 | AUD-2026-03-2000010730ACN-2026-03-4000127093 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | i). Location has been updating the TT dip checking data in SAP on DAILY basis. ii) EBMS SOP is made available at TTG . iii) Planning officers are checking Daily EBMS and records are maintained. iv) Necesaary training have been started for all planning officers on the applicable SOPs at TT gantry including the QC checks. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127096 | Closed | MAJUMDER BIRAJ | 2026-04-03 | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1644 | KOLKATA-I TERMINAL | Location to upload the 100%TT dip checking data in SAP. EBMS SOP not available at TTG - to be provided. Daily EBMS checks to be carried out by planning officers and records to be maintained. All planning officers to be conversant with all the applicable SOPs at gantry including the QC checks. | SOD | Marketing | EZ | 2026-03-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127096 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127096 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127096 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127096 | AUD-2026-03-2000010730ACN-2026-03-4000127096 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | Record for the compliance/action taken on the VA alerts is developed and the same is maintained. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127501 | Closed | MAJUMDER BIRAJ | 2026-04-03 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. However, it was observed that the supporting document in line with alert closure not available with location e.g. records of counselling the TT crew for wheel choke noncompliance/ PPE non compliance | 2.7 | VA alerts checked / analysed | 1644 | KOLKATA-I TERMINAL | It was advised to have written record for such complaince advice to the TT crew and to take their acknowledgement | SOD | Marketing | EZ | 2026-03-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127501 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127501 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127501 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127501 | AUD-2026-03-2000010730ACN-2026-03-4000127501 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-02 | Necessary Trainings have been provided on handling of safety critical equipment- SCABA, Fire extinguishers,Fire engines, HVLRs etc. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127503 | Closed | MAJUMDER BIRAJ | 2026-04-03 | Officers demonstrated the operation of 75 KG DCP | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1644 | KOLKATA-I TERMINAL | Officer need to be more conversant with Fire Engine operation and to operate all the safety critical equipment. Usage of SCABA to be practiced by all officers. | SOD | Marketing | EZ | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 3 | PROCESS SAFETY | S1 | F3 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127503 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127503 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127503 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127503 | AUD-2026-03-2000010730ACN-2026-03-4000127503 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | Location has been carrying out EBP checks and record is maintained. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127504 | Closed | MAJUMDER BIRAJ | 2026-04-03 | Random chekcing of EBP done from the all level sample of TT no. WB351652 and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1644 | KOLKATA-I TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-03-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127504 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127504 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127504 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127504 | AUD-2026-03-2000010730ACN-2026-03-4000127504 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
MAJUMDER BIRAJ | 2026-04-03 | CHOUDHURY DEBADIP NARAYAN | 2026-04-03 | Necessary trainings have been provided to officers on Ethanol/Bio Diesel receipt SOPs and record is maintained for each unloaded TT. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.6 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127505 | Closed | MAJUMDER BIRAJ | 2026-04-03 | Same is being ensured at location. | 3.6 | Ethanol TT dip before & after unloading verified (where applicable) | 1644 | KOLKATA-I TERMINAL | Ethanol/Bio Diesel receipt SOPs to be strictly adhered to and concerned Officers to be well conversant of same. Necessary records to be maintained for each TTs unloaded for assessing the receipt quantity. | SOD | Marketing | EZ | 2026-03-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010730ACN-2026-03-4000127505 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127505 | 2026-09-18 | 31.7538 | 214 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127505 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127505 | AUD-2026-03-2000010730ACN-2026-03-4000127505 | 21 | 21 | 26 | 80 | 0 | -7 | 30 | 31
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken and complied during the ERDMP and Monthly mock drill in front of PNGRB empanelled auditors and discussed during regular safety trainings | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121335 | Closed | SHIVESH TRIPATHI | 2026-04-07 | 1. Date 09.02.2026 & Time: 16:25 AM 2. Area of drill conducted: TT parking 3. Scenario covered: Fire in TT cabin 4. Double/single Contingency: Single contingency 5. Observation: Location to review TT evacuation in TT parking area and ensure clear visibilityto firefighting area Officers to participate in drill by operating firefighting equipment Delay is operation of DCP by first responder Effective communication between to teams to be ensured. Equipment performed satisfactorily. Location to conduct session of laying of fire hose in the field | 2.1 | Fire drill conducted in last 6 months (surprise) | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121335 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121335 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121335 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121335 | AUD-2026-02-2000010710ACN-2026-02-4000121335 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken and checked during ERDMP and comprehensive audit of location, further training imparted to ensure sustenance of the process safety as per corportation guidelines | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121339 | Closed | SHIVESH TRIPATHI | 2026-04-07 | 1.Testing carried of foam pourer of tank no 5,4 and TK2: performed satisfactorily 2. Sprinklers of Tk6 and Tk7 were operated. All sprinkler nozzles operated perfectly for Tk6. Sprinkler nozzles L6, U1, U4 and U9 found choked partially. 3. Foam pourers of Tk16 was operated. One foam pourer did not give proper discharge. 4. Dyke valve indicator of this tank farm was also operated, which worked properly. 5. Firewall valves of Tk6, Tk7 and Tk16 were checked. Found to have desired integrity. 6. Fire engine 2 was showing alarm in the security control room. Security found unaware of same. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121339 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121339 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121339 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121339 | AUD-2026-02-2000010710ACN-2026-02-4000121339 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | The same has been identified and communicated to the concerned security guards and roles and responsibility of the same has been updated | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121340 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Location is identifying security person who can drive the TT in case of emergency. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121340 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121340 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121340 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121340 | AUD-2026-02-2000010710ACN-2026-02-4000121340 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | HEALTH CAMPS ORGANISED TO COVER ALL OFFICER, CONTRACT WORKMAN, TT CREW covering extensive medical tests and same is being ensured | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121341 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Facility not available | 2.16 | Eyesight / colour-blindness awareness checked | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121341 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121341 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121341 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121341 | AUD-2026-02-2000010710ACN-2026-02-4000121341 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken and same checked during MDSA AUDIT AND ERDMP AUDIT. Some lights were kept off to electricity saving as per project Samriddhi, now Lux level is being ensured and periodically checked by M&I officer | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121336 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Lux level checked and found exceeding and low at few places. Location to review light deployment to lower the electricity consumption and to ensure LUX level as per OISD. Annexure 1 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121336 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121336 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121336 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121336 | AUD-2026-02-2000010710ACN-2026-02-4000121336 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken, DFMD rectified during the visit itself and training imparted to security guards | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121337 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Security found awake and alert. Security personnel is aware of fire engine operation. However location to impart refresher training to all security personnel including alarms showing in TAS screen. Register found updated. DFMD not working and kept in power offcondition. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121337 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121337 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121337 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121337 | AUD-2026-02-2000010710ACN-2026-02-4000121337 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken, Permit work is being verified at random periodic basis | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-02-4000121338 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Total Depot Camera- 60 Total Active Camera- 56 (Camera vendor has confirmed visit on 14.02.2026. Location has received 2 cameras for replacement) Last recording available for- 93 Days CCTV verification done for physical verification of maintenance active. Samecould not be verified against records. | 2.6 | CCTV functioning checked | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | THIRD PARTY ERRORS | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121338 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121338 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121338 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121338 | AUD-2026-02-2000010710ACN-2026-02-4000121338 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Corrective action taken, training imparted to CWs, SGs for proper following of SOP and rules and being checked on regular basis | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121345 | Closed | SHIVESH TRIPATHI | 2026-04-07 | House keeping practice is found satisfactory. Safety harness was not properly worn by TT crew of UP67AT1155. Housekeeping staff found not wearing safety harness during cleaning by standing over TT at calibration tower on date 23.01.2026. | 3.15 | Housekeeping & PPE usage checked | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121345 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121345 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121345 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121345 | AUD-2026-02-2000010710ACN-2026-02-4000121345 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | corrective action taken, proper connection and housekeeping ensured for proper fucntioning of earthpits | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121346 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Shoes, helmet found inside one earth pit (102) Infront of Admin Building. Connections inside Earth pit no 101, found improper Threeearth pits of Transformer yard, found with improper size pipe electrode. Two earth pits found having pipe coming out of earth pit cover. Single side earth pit clamp, improperly welded clamp with pipe electrode found in Transformer yard and near administrative building. Multiple earthing wire connection from single hole found near pole no 25. Such connections found in other places and in one earth pit of Transformer yard also. | 3.16 | Earth pits / boundary / vegetation control checked | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121346 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121346 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121346 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121346 | AUD-2026-02-2000010710ACN-2026-02-4000121346 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | MOCs are being reviewed regularly and Training imparted to officers to ensure non recurrence of such events | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121347 | Closed | SHIVESH TRIPATHI | 2026-04-07 | MOC not available for CCTV removed from TWDPH. | 3.17 | MOC status reviewed | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-07 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-07 | AUD-2026-02-2000010710ACN-2026-02-4000121347 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121347 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121347 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121347 | AUD-2026-02-2000010710ACN-2026-02-4000121347 | 21 | 21 | 26 | 80 | 1 | 2 | 27 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Open points being complied on timely basis as per the timeline set and monitored by Zone | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121348 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Compliance is being done. Status as of Jan'26: SAFE100 Self Safety Audit 2025: Total points: 35, Open points: 9, EDC: 31.03.2028 OISD ESA 2025-26: Total points: 26, Open points: 10, EDC: 31.03.2027 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1319 | MUGHALSARAI DEPOT | Location to close points scheduled for closure in current FY | SOD | Marketing | NCR | 2026-03-31 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010710ACN-2026-02-4000121348 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121348 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121348 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121348 | AUD-2026-02-2000010710ACN-2026-02-4000121348 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Since no abnormal observation was found, we have trained personnel and operations team carry out opns as per SOP to ensure sustenance of the same | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121342 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Randomly checked TT, which are coming inside are found to be in locked condition how ever few of them found to be with pre OTP. EMlock SOP compliance verified at field and found to be being followed. TT no UP64BT7077, UP50DT8167 & UP62T7351 checked with unauthorised Key and lock did not open. | 3.5 | EM Lock SOP compliance verified | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121342 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121342 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121342 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121342 | AUD-2026-02-2000010710ACN-2026-02-4000121342 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | corrective action taken by TAS Officer including recalibration of the tanks | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121343 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Tank dip reading: Tk16: Obs ref height 1249.4 cm. As per calibration chart, it is 1249.8 cm. Dip observed was 711.6cm. No difference with TAS dip Tk02: Obs ref height 1226.8 cm. As per calibration chart, it is 1227 cm. Dip observed was 842.3 CM. TAS dip 842.8. Water found was 0.6 cm. Need to check TAS data | 3.7 | Inventory physical dip of minimum two tanks taken | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121343 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121343 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121343 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121343 | AUD-2026-02-2000010710ACN-2026-02-4000121343 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | corrective action taken, RFDs prepared by M&I team for scrap disposal and regular preventive maintenance being insured | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-02-4000121344 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Asset verification completed by location and no open discrepancy. Location to identify the working/non working assets (Pumps, motors etc) and initiate action accordingly. | 3.9 | Abnormal variations / unused assets reviewed | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121344 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121344 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121344 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121344 | AUD-2026-02-2000010710ACN-2026-02-4000121344 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | corrective action taken, retractable ladders repaired and DFMD rectified, Preventive maintenance being carried out | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000121349 | Closed | SHIVESH TRIPATHI | 2026-04-07 | 1. Gantry: Lux level found satisfactory. Retractable ladder needs maintenance. Leakage observed from bottom loading coupler. Loading arm are not parked at designated place post loading. 2. Security & Admin Blocks: DFMD found not working. 3. Tank Farm: 4.PMCC room: None of the four smoke detectors found functional in Sample room 5. Siding: Drain free from oil. Gratings available over drain. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000121349 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000121349 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000121349 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000121349 | AUD-2026-02-2000010710ACN-2026-02-4000121349 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | corrective action taken, random verifcation of Work carried out by work permit system being done and record maintained | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122300 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Discrepancy observed in work permit system, actual testing in field and date mentioned in records upon review of CCTV footage. | 4.4 | Quality of PM compliance reviewed | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122300 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122300 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122300 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122300 | AUD-2026-02-2000010710ACN-2026-02-4000122300 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | RFDs have been prepared for all applicable items by M&I team, corrective action taken | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-02-4000122301 | Closed | SHIVESH TRIPATHI | 2026-04-07 | location to identify and segregate scrap available location. Scrap like defective valves, cables, pipes, IT assets, lights etc are available for disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122301 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122301 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122301 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122301 | AUD-2026-02-2000010710ACN-2026-02-4000122301 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, hooters have been replaced and being chekced on regular basis | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-02-4000122302 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Smoke detector 02 tested and found to be generating alarm however audio & visual siren not triggered. | 5.2 | Functioning of all Hooters in control room | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122302 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122302 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122302 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122302 | AUD-2026-02-2000010710ACN-2026-02-4000122302 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, Training imparted to Officer and CWs about handling of ethanol and additives | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122303 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Planning officer Not aware of Ethanol checking SOP. | 6.1 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122303 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122303 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122303 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122303 | AUD-2026-02-2000010710ACN-2026-02-4000122303 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN by M&I officer, end flange earthing provided | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122312 | Closed | SHIVESH TRIPATHI | 2026-04-07 | End flange earthing missing in TLF PH. | 6.10 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-02-28 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-02-28 | AUD-2026-02-2000010710ACN-2026-02-4000122312 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122312 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122312 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122312 | AUD-2026-02-2000010710ACN-2026-02-4000122312 | 21 | 21 | 26 | 80 | 1 | 2 | 26 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, maintenance work carried out in all pumps to ensure functioning properly | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.11 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122313 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Lube leakage observed from pump number HSD1 and MS 7. | 6.11 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122313 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122313 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122313 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122313 | AUD-2026-02-2000010710ACN-2026-02-4000122313 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Dg fuel line is installed at elevated level and strainer /mechanical seal and expansion drain line are installed at below ground level. As product movement is governed by gravity, the existing arrangement does not permit reverse flow or cross contamination. Additionally, the product collection barrel is located in close proximity to the HSD pumps, further minimizing any risk. To further strengthen the system and eliminate any possibility of cross contamination, a 2-inch gate valve has been installed between the DG fuel line and the strainer drain, mechanical seal, and expansion drain lines (Permit No. 110000140025). This corrective action ensures complete isolation and confirms nil cross contamination. | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.13 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122315 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Closed loop air out system not available in TLF and TWDPH. | 6.13 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122315 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122315 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122315 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122315 | AUD-2026-02-2000010710ACN-2026-02-4000122315 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, Civil work carried out to repair damaged section | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.14 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122316 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Bitumen Road found damaged in front of sample room and tank farm. | 6.14 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122316 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122316 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122316 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122316 | AUD-2026-02-2000010710ACN-2026-02-4000122316 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, Valve has been replaced and integrity rechecked | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.15 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122317 | Closed | SHIVESH TRIPATHI | 2026-04-07 | TK 17 sprinkler valve found passing. | 6.15 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122317 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122317 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122317 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122317 | AUD-2026-02-2000010710ACN-2026-02-4000122317 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, Emergency contact number has marked on the Tank trucks plying in contract with Depot | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.16 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122318 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Emergency contact number is not mentioned over few TT's tank body. | 6.16 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122318 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122318 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122318 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122318 | AUD-2026-02-2000010710ACN-2026-02-4000122318 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, Work permit training imparted to officer, CWs, and security, surprise inspection being carried out | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.17 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122319 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Work permit checked 110000679870 dated 08.01.2026 & 110000686399. Permits found to be closed in physical copy. TBT not singed by safety officer. Work permit number 100000689395 dated 19.01.2026 found to be not signed by contract supervisor, No TBT record available. | 6.17 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122319 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122319 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122319 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122319 | AUD-2026-02-2000010710ACN-2026-02-4000122319 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, verification of records further enforced by concerned officers | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.18 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122320 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Various check list were found filled by electrician unsigned, without testing date and without equipment number. | 6.18 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122320 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122320 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122320 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122320 | AUD-2026-02-2000010710ACN-2026-02-4000122320 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN foe improvement of Power factor of the location and minimisation of losses | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.19 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122321 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Power factor of location is observed 0.94 for last 3 months. | 6.19 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122321 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122321 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122321 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122321 | AUD-2026-02-2000010710ACN-2026-02-4000122321 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Housekeepng done by electricians and regular preventive maintenance being ensured by M&I team | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122304 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Floor of 250 KVA DG found oil soaked. Engine oil level found beyond maximum level. | 6.2 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122304 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122304 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122304 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122304 | AUD-2026-02-2000010710ACN-2026-02-4000122304 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, date of testing has been marked on Suitable place | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.20 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122322 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Last testing date not painted for WTI & OTI for siding transformer. | 6.20 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122322 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122322 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122322 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122322 | AUD-2026-02-2000010710ACN-2026-02-4000122322 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, SLD has been updated as per the current condition | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.21 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122323 | Closed | SHIVESH TRIPATHI | 2026-04-07 | SLD displayed outside siding MCC room not updated. | 6.21 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122323 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122323 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122323 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122323 | AUD-2026-02-2000010710ACN-2026-02-4000122323 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, DFMD rectification done and specification verifid | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.22 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122324 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Location to check DFMD specification installed at siding. | 6.22 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122324 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122324 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122324 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122324 | AUD-2026-02-2000010710ACN-2026-02-4000122324 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | CORRECTIVE ACTION TAKEN, 4 nut bolts tightened using non sparking tool by rake officer and sustenance being ensured | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.23 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122325 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Wagon unloading hose pipe connection found on 2 nut bolts. After unloading, hoses are kept on ground instead of stand. | 6.23 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122325 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122325 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122325 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122325 | AUD-2026-02-2000010710ACN-2026-02-4000122325 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | HPCL LOGO AND STICKER PASTED ON WAGON DECANTATION HOSE PIPE TO ENSURE DIFFERENTION BETWEEN HPCL AND BPCL rake | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.24 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122326 | Closed | SHIVESH TRIPATHI | 2026-04-07 | No clear identification between BPC and HPC unloading hoses. | 6.24 |  | 1319 | MUGHALSARAI DEPOT | HPCL LOGO AND STICKER PASTED ON WAGON DECANTATION HOSE PIPE TO ENSURE DIFFERENTION BETWEEN HPCL AND BPCL rake | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122326 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122326 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122326 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122326 | AUD-2026-02-2000010710ACN-2026-02-4000122326 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | HPCL LOGO AND STICKER PASTED ON WAGON DECANTATION HOSE PIPE TO ENSURE DIFFERENTION BETWEEN HPCL AND BPCL rake | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.25 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122327 | Closed | SHIVESH TRIPATHI | 2026-04-07 | As per records, strainer cleaning of fire engine was done on date 19.01.2026. Same could not verified in CCTV. | 6.25 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122327 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122327 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122327 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122327 | AUD-2026-02-2000010710ACN-2026-02-4000122327 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | regular monitoring of cctv camera is being ensured. | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.26 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122328 | Closed | SHIVESH TRIPATHI | 2026-04-07 | PTZ camera of RCT pump house was found misaligned since 24.12.2025. Upon review of CCTV footage of 24.12.2025 in control room, it is observed it was done by contract workmen and officer presence. Location reported issue of motor in camera, however, camera auto aligned itself on date 30.01.2026 after power failure. | 6.26 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122328 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122328 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122328 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122328 | AUD-2026-02-2000010710ACN-2026-02-4000122328 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | Location officers have been trained by LIC, field visits being ensured to enhance knowledge sharing | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.27 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122329 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Location officers are not aware of depot facilities and equipment available at location. Self-awareness and training session needs to be imparted to all officers. | 6.27 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | COST-CUTTING COMPROMISING SAFETY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122329 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122329 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122329 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122329 | AUD-2026-02-2000010710ACN-2026-02-4000122329 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
RAHA ROY SUBRAJYOTI | 2026-04-07 | SHIVESH TRIPATHI | 2026-04-07 | AG TANK SELF CLOSING TYPE DIP HATCH placed in tank by M&I officer | SR MANAGEMENT INSPECTION MGS Q4 25-26 | 2026-02-10 17:00 | AUD-2026-02-2000010710 | 2026-02-09 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122307 | Closed | SHIVESH TRIPATHI | 2026-04-07 | Tk16 gauge hatch found to be not self-closing type. | 6.5 |  | 1319 | MUGHALSARAI DEPOT | Corrective action to be taken | SOD | Marketing | NCR | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010710ACN-2026-02-4000122307 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010710ACN-2026-02-4000122307 | 2026-09-02 17:30 | 47.0247 | 218 | >20 | AUD-2026-02-2000010710 - ACN-2026-02-4000122307 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010710ACN-2026-02-4000122307 | AUD-2026-02-2000010710ACN-2026-02-4000122307 | 21 | 21 | 26 | 80 | 1 | 2 | 28 | 32
POTHALA VENKATA RAO | 2026-04-07 | PP AKHIL | 2026-04-07 | 10 applicable points of Suryapet.All complied(27 Points applicable for other locations not for suryapet) | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123490 | Closed | PP AKHIL | 2026-04-07 | pending issues and compliances, and the status of action points from the last BCM review | 1.3 | Pending issues reviewed | 1937 | SURYAPET TERMINAL | All pending points of previous BCM review to be complied immediately | SOD | Marketing | SCR | 2026-03-31 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123490 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123490 | 2026-08-04 18:45 | 75.9726 | 218 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123490 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123490 | AUD-2026-03-2000011061ACN-2026-03-4000123490 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 32
POTHALA VENKATA RAO | 2026-04-07 | PP AKHIL | 2026-04-07 | All critical alarms such as HCD, Dyke, ESD, and HHH are acknowledged only after analysing , in case of any alarms reported even during off‑shift hours by VVSPL. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123498 | Closed | PP AKHIL | 2026-04-07 | Critical alarms were reviewed for past one month | 3.12 | Critical alarms checked & corrective actions reviewed | 1937 | SURYAPET TERMINAL | Location advised to carefully monitor the alarms and not acknowledge them without going into detail of the reason for it | SOD | Marketing | SCR | 2026-01-30 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123498 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123498 | 2026-08-04 18:45 | 75.9726 | 218 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123498 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123498 | AUD-2026-03-2000011061ACN-2026-03-4000123498 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 32
POTHALA VENKATA RAO | 2026-04-07 | PP AKHIL | 2026-04-07 | Vide email dated 20.02.2026, mailed to AST & informed HQO with copy to SCZ vide email dated 10.03.2026. Erroneous data for Dec2025 has been deleted from events by AST. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123499 | Closed | PP AKHIL | 2026-04-07 | BCU K-factor was found populated erroneously for dates 11-12-2025 and 12-12-2025 | 3.13 | K-factor changes reviewed (if any) | 1937 | SURYAPET TERMINAL | Correspondence to be initiated with AST and zonal TAS for rectification and prevention of recurrence. | SOD | Marketing | SCR | 2026-01-30 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-30 | AUD-2026-03-2000011061ACN-2026-03-4000123499 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123499 | 2026-08-04 18:45 | 75.9726 | 218 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123499 | 532 | 8294 | 21 | 8294 | 262 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123499 | AUD-2026-03-2000011061ACN-2026-03-4000123499 | 21 | 21 | 26 | 80 | 0 | 0 | 22 | 32
POTHALA VENKATA RAO | 2026-04-07 | PP AKHIL | 2026-03-17 | COMPLETED | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123497 | Closed | PANDEY AKHIL | 2026-03-07 | Regular emails shared on OCC and combine alerts were reviewed | 3.3 | VTS deviations reviewed | 1937 | SURYAPET TERMINAL | OCC and Combined alerts are closed | SOD | Marketing | SCR | 2026-05-03 | INSTRUMENTATION OR ALARM FAILURES | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-05-03 | AUD-2026-03-2000011061ACN-2026-03-4000123497 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123497 | 2026-08-04 18:45 | 75.9726 | 218 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123497 | 532 | 8294 | 21 | 8294 | 169 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123497 | AUD-2026-03-2000011061ACN-2026-03-4000123497 | 21 | 21 | 26 | 80 | 0 | 0 | 35 | 32
POTHALA VENKATA RAO | 2026-04-07 | PP AKHIL | 2026-03-17 | loading of trucks has been started with bottom loading fittings. Conversion of trucks to bottom loading is in progress. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123655 | Closed | PP AKHIL | 2026-03-17 | Bottom loading conversion and conversion of trucks, Commissioning of new Solar plant | 6.1 |  | 1937 | SURYAPET TERMINAL | Location has been guided to initiate completion of bottom loading works in gantry and start loading , parallely advised for phase wise conversion of bottom loading trucks | SOD | Marketing | SCR | 2026-06-30 | FATIGUE AND STRESS | 5 | EMERGENCY | S1 | F5 | 2026-06-30 | AUD-2026-03-2000011061ACN-2026-03-4000123655 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123655 | 2026-08-04 18:45 | 75.9726 | 218 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123655 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123655 | AUD-2026-03-2000011061ACN-2026-03-4000123655 | 21 | 21 | 26 | 80 | 0 | 0 | 44 | 32
POTHALA VENKATA RAO | 2026-04-09 | PP AKHIL | 2026-04-09 | CEA approval received and the project was successfully commissioned on 24th March 2026 | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123653 | Closed | PP AKHIL | 2026-04-09 | ongoing Solar project status revived | 4.3 | Project progress reviewed | 1937 | SURYAPET TERMINAL | Advised location to expedite works / CEA visit and pre commission checks and start solar generation at the earliest | SOD | Marketing | SCR | 2026-02-25 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-25 | AUD-2026-03-2000011061ACN-2026-03-4000123653 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123653 | 2026-08-04 18:45 | 75.9726 | 220 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123653 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123653 | AUD-2026-03-2000011061ACN-2026-03-4000123653 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 32
POTHALA VENKATA RAO | 2026-04-09 | PP AKHIL | 2026-04-09 | Disposal of available completed. | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123654 | Closed | POTHALA VENKATA RAO | 2026-04-09 | visited Scrap yard and advised for immediated disposal of all available scrap | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1937 | SURYAPET TERMINAL | segregated scrap to be valuated and proceed for disosal | SOD | Marketing | SCR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011061ACN-2026-03-4000123654 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123654 | 2026-08-04 18:45 | 75.9726 | 220 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123654 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123654 | AUD-2026-03-2000011061ACN-2026-03-4000123654 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 32
POTHALA VENKATA RAO | 2026-04-09 | PP AKHIL | 2026-03-17 | All locks having wear and tear and causing E-Tag failure alerts are replaced and continuing the practice to avoid E-Tag alert | GM LOCATION VISIT TO SURYAPET TERMINAL | 2026-01-29 19:30 | AUD-2026-03-2000011061 | 2026-01-29 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123656 | Closed | POTHALA VENKATA RAO | 2026-04-09 | Checking of EM locks for E-TAG issues and replacement of the same to avoid alerts, | 6.3 |  | 1937 | SURYAPET TERMINAL | To check EM locks for replacement of locks having E Tag Issues | SOD | Marketing | SCR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011061ACN-2026-03-4000123656 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011061ACN-2026-03-4000123656 | 2026-08-04 18:45 | 75.9726 | 220 | >20 | AUD-2026-03-2000011061 - ACN-2026-03-4000123656 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011061ACN-2026-03-4000123656 | AUD-2026-03-2000011061ACN-2026-03-4000123656 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125485 | Closed |  |  | The efficacy of present available transport TT fleet was discussed in detail and advised location for ensuring 100% indent execution at all times. Observed that TT reporting in the starting of the office hours is very less. Advised location to follow up and ensure improved TT reporting. | 1.8 | Improvement plans discussed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125485 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125485 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125485 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125485 | AUD-2026-03-2000011072ACN-2026-03-4000125485 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125487 | Closed |  |  | Yes checked and observed that improvement/training needed. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | FATIGUE AND STRESS | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125487 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125487 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125487 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125487 | AUD-2026-03-2000011072ACN-2026-03-4000125487 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125488 | Closed |  |  | Availability of Foam (20 KL) was not in line with OISD requirement of 29.5 KL for which Release Order already placed on supplier and expected to receive foam by 28.02.2026. | 2.9 | Foam inventory verified | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125488 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125488 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125488 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125488 | AUD-2026-03-2000011072ACN-2026-03-4000125488 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125493 | Closed |  |  | Yes checked and found values are within permissible limit but due to ongoing project various material lying above the earthpits making testing difficult due to space limitation. Verified EP no-119 & EP no -120 and verified with values as:- o EP No-119 - grid - 0.25 Ohm & electrode - 1.21 Ohm o EP No-120 - grid – 0.45 Ohm & electrode – 1.32 Ohm | 3.16 | Earth pits / boundary / vegetation control checked | 1583 | KANDLA TERMINAL | Location to ensure witnessing of the earth pit testing activity in field and clearance of project material lying unsed in variou places. | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125493 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125493 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125493 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125493 | AUD-2026-03-2000011072ACN-2026-03-4000125493 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125491 | Closed |  |  | Reconciliation is being done basis the daily dayend Manual dips. Duly signed records are available at location. | 3.8 | Auto vs Manual reconciliation checked | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125491 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125491 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125491 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011072ACN-2026-03-4000125491 | AUD-2026-03-2000011072ACN-2026-03-4000125491 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125496 | Closed |  |  | Solar generation for a period Apr’25 to Jan’26 was reviewed and observed that frequent inverter tripping was happened due to which generation on those days were affected. Location has been advised to ensure close monitoring of solar generation for generation as per design basis. | 4.2 | Maintenance activities reviewed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125496 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125496 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125496 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125496 | AUD-2026-03-2000011072ACN-2026-03-4000125496 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125497 | Closed |  |  | Yes reviewed. Project works were going on in pump house, TT gantry area, tank farm area under land surrender project. 1. Roof Replacement and Allied Jobs TK302 and TK305 2. Roof Replacement and Allied Jobs TK304 3. Construction of Boundary wall 4. Construction of UG Tanks Pit and Installation of UG Tanks 5. Fabrication of Gantry Structure for extension of Gantry 6. Sand Blasting and Painting of Pipelines 7. ETP Sump Construction 8. Laying of underground Hume pipes for drainage and construction of open drain 9. Construction of Dyke Wall and Pipeline pedestals and culverts | 4.3 | Project progress reviewed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125497 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125497 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125497 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125497 | AUD-2026-03-2000011072ACN-2026-03-4000125497 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125499 | Closed |  |  | Location to ensure stock loss for HIGH FLASH DIESEL OIL, HP INDUSTRIAL DIESEL OIL, MS and LSHS to be within AOP Targets | 6.1 | Stockloss | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000011072ACN-2026-03-4000125499 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125499 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125499 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125499 | AUD-2026-03-2000011072ACN-2026-03-4000125499 | 21 | 21 | 26 | 80 | 2 | 2 | 30 | 32
TAK MITHLESH KUMAR | 2026-04-13 |  |  |  | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000126002 | Closed |  |  | 1. UG Tank Farm work is pending 2. Civil works are pending 3. Open drain slope to be ensured in line with drawing. 4. Extra manpower (security and CE) deployed for ongoing projects to be waithdarwn after project completion. | 6.4 | Other Project Review | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-03-2000011072ACN-2026-03-4000126002 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000126002 | 2026-08-16 | 64.7538 | 224 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000126002 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000126002 | AUD-2026-03-2000011072ACN-2026-03-4000126002 | 21 | 21 | 26 | 80 | 2 | 2 | 44 | 32
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | we are ensuring PPEs are used by workmen in field and empty TTs are checked by 2 officers. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127429 | Closed | NILABH | 2026-04-17 | Compliance is being done by location. How ever deviation observed for PERSONAL PROTECTIVE EQUIPMENT GUIDELINES (Usegae of safety harness at calibration tower) & Releasing of empty TT. | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127429 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127429 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127429 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127429 | AUD-2026-04-2000011243ACN-2026-04-4000127429 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Sri Mukesh Kumar operated HVLRs of Tk9 but not able to explain properly to GM Sir. We have give him training on HVLR and MEFG operations. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127434 | Closed | NILABH | 2026-04-17 | 1.Sri Mukesh Kumar was asked to operate one of the HVLRs of Tk9. He could operate the same properly & MEFG of Tk9 was also operatedproperly. 2. Module bearing sr no R14150081F1FM01 of rim seal fire protection system of Tk7 was operated. It worked properly. 3.Open path type HCD covering manifolds of Tk7 and Tk8 was checked. It was found functional properly. Point type HCD of Tk9 did not function 4. Testing of ESD: Operated ESD during mock drill. Fire siren not activated. TAS event report is not provided by the location. 5. Integrity of gate valve of fire wall bearing no GVC1, between Tk8 and Tk9 was checked. Found to be not passing. 6. Sprinklers system of Tk8 was operated. All nozzles found providing proper discharge. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1305 | KANPUR TERMINAL | Corrective action to be taken for point no 4 | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127434 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127434 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127434 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127434 | AUD-2026-04-2000011243ACN-2026-04-4000127434 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | We are covering use of panic button in Gate meetings and weekly TT crew training program at location. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127435 | Closed | NILABH | 2026-04-17 | Roadside emergency procedure awareness check carried out with TT crew of UP74AT0021. TT crew was found aware of emergency procedurehowever not aware of instances when Panic button to be presses given in TT cabin. | 2.15 | TT crew roadside emergency procedures checked | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127435 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127435 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127435 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127435 | AUD-2026-04-2000011243ACN-2026-04-4000127435 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Mock drill observations are noted and complied in further drills. In field training provided to electrician. VHF available at location for effective communication in field. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127430 | Closed | NILABH | 2026-04-17 | Observations: 1. Team leaders to ensure effective communication and reporting to fire chief during drills 2. fire siren was found not to be working. 3. Location to conduct training to electrician on fire fighting in electrical panel. 4. First CO2 type extinguisher did not perform satisfactorily. 5. Operation of DCP extinguisher was delayed by first responder at fisrt site. | 2.2 | Double contingency scenario simulated; observations recorded | 1305 | KANPUR TERMINAL | Corrective action shall be taken to improve in mock drills. | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127430 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127430 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127430 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127430 | AUD-2026-04-2000011243ACN-2026-04-4000127430 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Review of alert TT Crew non availability (TT unloading) TAS_1305_SOP045_180226_000001 dated 18.02.2026. Alert closed with comment INVALID. Reason for invalid alert is not covered in the comment as alert was found to be valid. As TT Crew was available so invalid comment was selected. All VA alerts are closed after due review. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127432 | Closed | NILABH | 2026-04-17 | 1.1 VA alerts are being closed by location in time. 1.2 Review of alert TT Crew non availability (TT unloading) TAS_1305_SOP045_180226_000001 dated 18.02.2026. Alert closed with comment INVALID. Reason for invalid alert is not covered in the comment as alert wasfound to be valid. | 2.7 | VA alerts checked / analysed | 1305 | KANPUR TERMINAL | Location to maintain supporting document related to SOP deviation in VA alerts. | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127432 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127432 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127432 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127432 | AUD-2026-04-2000011243ACN-2026-04-4000127432 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | location officer asked for using PPE during TT calibration. Councelling of officer done. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127440 | Closed | NILABH | 2026-04-17 | Housekeeping practice is found satisfactory. As found during random checking of CCTV footages, there are instances when location officer found not using PPE during TT calibration. | 3.15 | Housekeeping & PPE usage checked | 1305 | KANPUR TERMINAL | Location to ensure PPE usage by officers | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127440 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127440 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127440 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127440 | AUD-2026-04-2000011243ACN-2026-04-4000127440 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Regular practice. vegetation removed from top of boundary wall. Touch up painting being carried out. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127441 | Closed | NILABH | 2026-04-17 | Earth pit no 135 at TWPH was found to be having improper connection. Nearby earthpits 136 and 137 were having proper connections. Boundary wall TT gantry is having paint peel off. Near the future area boundary wall and front area of admin building, vegetation found on top of boundary wall. | 3.16 | Earth pits / boundary / vegetation control checked | 1305 | KANPUR TERMINAL | Corrective action to be taken. | SOD | Marketing | NCR | 2026-04-10 | POOR EQUIPMENT MAINTENANCE | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127441 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127441 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127441 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127441 | AUD-2026-04-2000011243ACN-2026-04-4000127441 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Noted, Open MOCs are closed after completion of job. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127442 | Closed | NILABH | 2026-04-17 | Total MOC: 76, Approved:19, Closed:18, In Preparation:4, Incomplete: 7,Rejected: 18, Submitted:10. | 3.17 | MOC status reviewed | 1305 | KANPUR TERMINAL | Location to review MOC availability and arrange to approval of MOC with status inpreparation, incomplete and submitted. | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127442 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127442 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127442 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127442 | AUD-2026-04-2000011243ACN-2026-04-4000127442 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | noted. Points are complied as per closure schedule. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127443 | Closed | NILABH | 2026-04-17 | Location is advised to close the compliance of priority basis scheduled in current FY. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1305 | KANPUR TERMINAL | Corrective action to be taken. | SOD | Marketing | NCR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-04-2000011243ACN-2026-04-4000127443 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127443 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127443 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127443 | AUD-2026-04-2000011243ACN-2026-04-4000127443 | 21 | 21 | 26 | 80 | 4 | 4 | 31 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | TT no UP78JN1455 was reverified and Check A and B was carried out. No abnormility was reported. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127436 | Closed | NILABH | 2026-04-17 | Post load dip checking was carried out at both gantry except bay no 15. All TTs were found in within limit except following Bay no9: UP78JN1455 (Ch 1: +8 mm, Ch 2: +4 mm, Ch 3: 5 mm) | 3.2 | Post-loading dip checks verified | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127436 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127436 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127436 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127436 | AUD-2026-04-2000011243ACN-2026-04-4000127436 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | TT no PB05AU1837 (Bay No 1) was checked by location officer for ethanol blending % and blending found 17.5%. With correction factorit will be 18.5% - 19%. We are checking ethanol blending regularly and no major variation is observed. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127437 | Closed | NILABH | 2026-04-17 | TT no PB05AU1837 (Bay No 1) was checked by location officer for ethanol blending % and blending found 17.5%. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1305 | KANPUR TERMINAL | Corrective action shall be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127437 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127437 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127437 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127437 | AUD-2026-04-2000011243ACN-2026-04-4000127437 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Density and temprature in within permisible limit. We are checing the same on regular basis. Same was checked with TAS vendor also. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127438 | Closed | NILABH | 2026-04-17 | Tk7: Reference height mentioned and observed: 1564 cm. Dip observed was 867.3 cm/ water nil. Density was 736 at 26 Deg cent. Product temperature was 25 deg cent. TAS records are : Product dip: 867.5 cm/Water dip: 0 cm, Temp: 23.83 C, density 736 Tk1: Reference height mentioned and observed: 1575 cm. Dip observed was 176.0 cm/1 mm. Density was 822 at 30.5 Deg cent. Product temperature was 28deg cent. TAS records are : Product dip: 175.8 cm/Water dip: 0.1 cm, Temp: 23.45 C, density 822. | 3.7 | Inventory physical dip of minimum two tanks taken | 1305 | KANPUR TERMINAL | Corrective action shall be taken on temp variation | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127438 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127438 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127438 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127438 | AUD-2026-04-2000011243ACN-2026-04-4000127438 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | unused status updated on surplus material portal. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127439 | Closed | NILABH | 2026-04-17 | List of unused/Surplus assets to be updated in surplus material portal (not in data mine). | 3.9 | Abnormal variations / unused assets reviewed | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127439 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127439 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127439 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127439 | AUD-2026-04-2000011243ACN-2026-04-4000127439 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | we are ensuring first 3 loads are checked by officer. LIC has instructed officers to ensure this. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127445 | Closed | NILABH | 2026-04-17 | On random checking (TT no UP90AT1905 for second load on 10.02.2026) it has been found, that there are instances, when post calibration, first 3 loads are not being checked by officer however records are available. | 6.1 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127445 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127445 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127445 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127445 | AUD-2026-04-2000011243ACN-2026-04-4000127445 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Sample register is signed and maintained. Instruction given to officer to ensure signing of sample register. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127446 | Closed | NILABH | 2026-04-17 | Sample register is not signed regularly and maintained since 22.02.2026 | 6.2 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127446 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127446 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127446 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127446 | AUD-2026-04-2000011243ACN-2026-04-4000127446 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | noted and rectified permits (100000719884 & 100000723984). | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127447 | Closed | NILABH | 2026-04-17 | On random checking of 4 permits, 2 permits (100000719884 & 100000723984) were not signed by issuer in closing work permit remark column. | 6.3 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127447 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127447 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127447 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127447 | AUD-2026-04-2000011243ACN-2026-04-4000127447 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | TT calibration record updated and blank checklist was kept for other TT inspection. Instruction givent to OIC for completely filling all coloums and headers. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127448 | Closed | NILABH | 2026-04-17 | TT calibration record is found with blank checklist having TT numbers and with signature of TT crew and HPCL officer. Calibration records are not maintained properly leaving few headers blank. | 6.4 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127448 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127448 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127448 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127448 | AUD-2026-04-2000011243ACN-2026-04-4000127448 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | Contract workmen are entring and leaving location and attendance timing is maintained in CLMS. Instruction given to security to ensure In and Out Time is maintained in gate register also. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127449 | Closed | NILABH | 2026-04-17 | Contract labour entry register is found without out time for few workers for date 02.03.2026, 25.03.2026, 22.03.2026. | 6.5 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000127449 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000127449 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000127449 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000127449 | AUD-2026-04-2000011243ACN-2026-04-4000127449 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
MANDAL PRATAPKUMAR | 2026-04-17 | NILABH | 2026-04-17 | We have review all registered releated to TT Gantry and TT calibration. All columns are properly filled now and same is maintaned. | SR MANAGEMENT INSPECTION KNP Q4 25-26 | 2026-03-28 15:00 | AUD-2026-04-2000011243 | 2026-03-27 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128000 | Closed | NILABH | 2026-04-17 | There are numbers of registers and records having number of columns some of which are being kept blank. Location to review requirement of so many records and maintain the same fully. | 6.6 |  | 1305 | KANPUR TERMINAL | Corrective action to be taken | SOD | Marketing | NCR | 2026-04-10 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-04-10 | AUD-2026-04-2000011243ACN-2026-04-4000128000 | UP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011243ACN-2026-04-4000128000 | 2026-08-26 17:00 | 54.0455 | 228 | >20 | AUD-2026-04-2000011243 - ACN-2026-04-4000128000 | 532 | 8294 | 21 | 8294 | 192 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011243ACN-2026-04-4000128000 | AUD-2026-04-2000011243ACN-2026-04-4000128000 | 21 | 21 | 26 | 80 | 4 | 4 | 32 | 33
SRIJIN S | 2026-04-21 |  |  | All the Light fittings jobs at Cochin terminal completed. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125850 | Closed | SRIJIN S | 2026-04-21 | LUX level improvement in progress near tank farm. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1833 | COCHIN BLACK TERMINAL | Lighting Imporvement to be completed by 31.03.2026 | SOD | Marketing | CZR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125850 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125850 | 2026-09-08 16:00 | 41.0872 | 232 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125850 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125850 | AUD-2026-03-2000011134ACN-2026-03-4000125850 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 34
[5 empty] | LOCATION VISIT-LEH_15-17.04.26 | 2026-04-17 | AUD-2026-04-2000010791 | 2026-04-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000125663 | Open |  |  | Disposal of old DG, few other operational issues advised. | 1.3 | Pending issues reviewed | 1265 | LEH DEPOT | RFD to be processed for DG | SOD | Marketing | NFZ | 2026-05-30 |  | 4 |  | S1 | F4 | 2026-05-30 | AUD-2026-04-2000010791ACN-2026-04-4000125663 | LK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000010791ACN-2026-04-4000125663 | 2026-10-07 09:00 | 12.3788 | 271 | >20 | AUD-2026-04-2000010791 - ACN-2026-04-4000125663 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-04-2000010791ACN-2026-04-4000125663 |  | AUD-2026-04-2000010791ACN-2026-04-4000125663 | 21 |  | 27 | 80 | 0 | 0 | 39
|  |  |  | Necessary notification for safety harness has been submitted by HMEL and the same has been approved. installation pending. | LOCATION VISIT-HMEL BITUMEN TML_09.03.26 | 2026-03-09 | AUD-2026-04-2000011402 | 2026-03-09 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128653 | Open | NEGI APARNA | 2026-06-11 | Yes, Use of idle sealing platform for emptiness check of TTs before sending TTs inside gantry. | 1.3 | Pending issues reviewed | 3129 | BATHINDA BIT HMEL | To ensure installation of Safety harness arrangement to be done by HMEL Team before commencement of platform. | SOD | Marketing | NFZ | 2026-04-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 2 | PROCESS SAFETY | S1 | F2 | 2026-06-30 | AUD-2026-04-2000011402ACN-2026-04-4000128653 | [12 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011402ACN-2026-04-4000128653 | 2026-09-29 17:00 | 20.0455 | 226 | >20 | AUD-2026-04-2000011402 - ACN-2026-04-4000128653 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011402ACN-2026-04-4000128653 |  | AUD-2026-04-2000011402ACN-2026-04-4000128653 | 21 |  | 26 | 80 | 0 | 0 | 33
[5 empty] | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126313 | Open |  |  | Conduted | 1.2 | Performance review conducted | 1554 | MR-II TERMINAL | Painting to be started, equipment maintance and structure maintenance to be streamlined | SOD | Marketing | WZ | 2026-09-30 |  | 2 |  | S1 | F2 | 2026-09-30 | AUD-2026-04-2000011147ACN-2026-04-4000126313 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126313 | 2026-10-16 | 3.7538 | 394 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126313 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011147ACN-2026-04-4000126313 |  | AUD-2026-04-2000011147ACN-2026-04-4000126313 | 21 |  | 26 | 80 | 6 | 5 | 57
[5 empty] | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126320 | Open |  |  | EM Locks SOP pending at zone for approval | 3.5 | EM Lock SOP compliance verified | 1554 | MR-II TERMINAL | Location to followup | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126320 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126320 | 2026-10-16 | 3.7538 | 241 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126320 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011147ACN-2026-04-4000126320 |  | AUD-2026-04-2000011147ACN-2026-04-4000126320 | 21 |  | 26 | 80 | 6 | 5 | 35
[5 empty] | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126321 | Open |  |  | Audi Alarm not availble for Dyke drains valves | 3.12 | Critical alarms checked & corrective actions reviewed | 1554 | MR-II TERMINAL | Location to develop Audio Visual alarms for Dyke drain sensors | SOD | Marketing | WZ | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-04-2000011147ACN-2026-04-4000126321 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126321 | 2026-10-16 | 3.7538 | 302 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126321 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011147ACN-2026-04-4000126321 |  | AUD-2026-04-2000011147ACN-2026-04-4000126321 | 21 |  | 26 | 80 | 6 | 5 | 44
[5 empty] | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126323 | Open |  |  | YES. VRU MOC pending approval | 3.17 | MOC status reviewed | 1554 | MR-II TERMINAL | Location to submit to Zone | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126323 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126323 | 2026-10-16 | 3.7538 | 241 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126323 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011147ACN-2026-04-4000126323 |  | AUD-2026-04-2000011147ACN-2026-04-4000126323 | 21 |  | 26 | 80 | 6 | 5 | 35
[5 empty] | ZONAL VISIT REPORT MR2 24.03.2026 | 2026-03-24 | AUD-2026-04-2000011147 | 2026-03-24 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000126325 | Open |  |  | Reviewed. FO 380 pump repairs to be expedited. Leaks seen in FO and RPO pumps | 4.2 | Maintenance activities reviewed | 1554 | MR-II TERMINAL | Location to do prompt repairs | SOD | Marketing | WZ | 2026-04-30 |  | 2 |  | S1 | F2 | 2026-04-30 | AUD-2026-04-2000011147ACN-2026-04-4000126325 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011147ACN-2026-04-4000126325 | 2026-10-16 | 3.7538 | 241 | >20 | AUD-2026-04-2000011147 - ACN-2026-04-4000126325 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011147ACN-2026-04-4000126325 |  | AUD-2026-04-2000011147ACN-2026-04-4000126325 | 21 |  | 26 | 80 | 6 | 5 | 35
[5 empty] | LOCATION VISIT-NALAGARH_05-07.03.26 | 2026-03-07 | AUD-2026-04-2000010748 | 2026-03-05 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128570 | Open |  |  | Location is having 40 CCTVs and out of which 38 are working. Checked records of CCTV being analysed by Security. | 2.6 | CCTV functioning checked | 1183 | NALGARH DEPOT | Repair of camera to be expedited. | SOD | Marketing | NFZ | 2026-04-30 |  | 8 |  | S2 | F4 | 2026-04-30 | AUD-2026-04-2000010748ACN-2026-04-4000128570 | HP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010748ACN-2026-04-4000128570 | 2026-08-27 | 53.7538 | 241 | >20 | AUD-2026-04-2000010748 - ACN-2026-04-4000128570 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-04-2000010748ACN-2026-04-4000128570 |  | AUD-2026-04-2000010748ACN-2026-04-4000128570 | 21 |  | 26 | 80 | 1 | 1 | 35
[5 empty] | LOCATION VISIT-NALAGARH_05-07.03.26 | 2026-03-07 | AUD-2026-04-2000010748 | 2026-03-05 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000128571 | Open |  |  | Scrap observed at Location, RFD of the same processed but disposal not done despite finalization of bidder in auction two times. Location is in process of getting the auction done again on the basis of lots to ensure disposal. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1183 | NALGARH DEPOT | Actual disposal to be expedited. | SOD | Marketing | NFZ | 2026-03-31 |  | 4 |  | S1 | F4 | 2026-03-31 | AUD-2026-04-2000010748ACN-2026-04-4000128571 | HP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000010748ACN-2026-04-4000128571 | 2026-08-27 | 53.7538 | 211 | >20 | AUD-2026-04-2000010748 - ACN-2026-04-4000128571 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000010748ACN-2026-04-4000128571 |  | AUD-2026-04-2000010748ACN-2026-04-4000128571 | 21 |  | 26 | 80 | 1 | 1 | 31
[5 empty] | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-04-4000128230 | Open |  |  | MFM based accounting not being done . VVSPL MFM to be calibrated due to erroenous reading of temp sensor/ denisty. Hence, PLT booking presenlty done thru manual tank dips. | 5.1 | MFM based accounting at Pipeline and OMC location | 1937 | SURYAPET TERMINAL | To take up with VVSPL for completion of calibration and commencing of MFM based accounting | SOD | Marketing | SCR | 2026-05-31 |  | 5 |  | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011400ACN-2026-04-4000128230 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128230 | 2026-08-04 18:45 | 75.9726 | 272 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128230 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-04-2000011400ACN-2026-04-4000128230 |  | AUD-2026-04-2000011400ACN-2026-04-4000128230 | 21 |  | 27 | 80 | 0 | 0 | 39
[5 empty] | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000128231 | Open |  |  | Live Fire Training not done for security guards | 6.1 |  | 1937 | SURYAPET TERMINAL | Live fire training to be conducted for all the security guards | SOD | Marketing | SCR | 2026-05-31 |  | 5 |  | S1 | F5 | 2026-05-31 | AUD-2026-04-2000011400ACN-2026-04-4000128231 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128231 | 2026-08-04 18:45 | 75.9726 | 272 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128231 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-04-2000011400ACN-2026-04-4000128231 |  | AUD-2026-04-2000011400ACN-2026-04-4000128231 | 21 |  | 27 | 80 | 0 | 0 | 39
|  | CHANGMAI RAHUL | 2026-04-23 | FRS is functional now. BSNL Intranet link was down for almost one month hence the punching was not done during that time. FRS andIntranet link is functional now. Reflected in system. Physical attendance register is maintained by security guard. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127070 | Completed | CHANGMAI RAHUL | 2026-04-23 | Yes, Interacted with LIC. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1708 | DIMAPUR DEPOT | Officer is advised for on time reporting to depot and use the FRS for attendance recording. If FRN is non- functional, same to be taken up with EZ HR immediately for rectification. Attendance reporting to be entered in security register. | SOD | Marketing | GZR | 2026-03-30 | INSTRUMENTATION OR ALARM FAILURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127070 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127070 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127070 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000010729ACN-2026-03-4000127070 |  | AUD-2026-03-2000010729ACN-2026-03-4000127070 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-04-23 | Appplied for all pending licenses. CTO Pollution renewal received. New Hazardous waste NOC license applied.Factory license applied and reviewed by factory officer and has called to factory office for few clarifications. All the pending Jobs as per Zonal visit 16-17 Oct25 is completed. Materials procurement process initiated as per the recommendation. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127071 | Completed | CHANGMAI RAHUL | 2026-04-23 | Yes, location performance review carried w.r.t infrastructure , safety equipment functioning, security and handling contractor engagement and statuary licenses. | 1.2 | Performance review conducted | 1708 | DIMAPUR DEPOT | Officer to proactively apply and follow-up for all licenses and approval pertaining to Dimapur depot. Also, the pending jobs w.r.t last zonal visit dated 16-17 Oct'25 to be complied at the earliest. | SOD | Marketing | GZR | 2026-04-05 |  | 8 |  | S2 | F4 | 2026-04-05 | AUD-2026-03-2000010729ACN-2026-03-4000127071 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127071 | 2026-09-12 | 37.7538 | 216 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127071 | 532 | 8294 | 21 | 8294 | 197 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127071 |  | AUD-2026-03-2000010729ACN-2026-03-4000127071 | 21 |  | 26 | 80 | 7 | 7 | 31
|  | CHANGMAI RAHUL | 2026-04-23 | 1. Night Inspection to be done quarterly as per SOP 2. Safety training with fire mockdrill given to the CW and SGs 3. Housekeepigimproved espcially the tank firm area which was having improperly dressed cablings. 4. Reco done in March end and also to be done every month end. 5. Material Gate pass system available for In gate pass with single approver.For out material single approver not allowed by system as per IS department. 6. Work Permit system is being taken for any activities in the Depot premises. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127074 | Completed | CHANGMAI RAHUL | 2026-04-23 | 1. Night Inspection Not done by LIC 2. Safety training to the CW and SGs not done 3. Housekeepig of the depot to be improved 4. Reco not bring done on every month end 5. Material Gate pass system not implemented 6. Work Permit system not implemented | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1708 | DIMAPUR DEPOT | Officer to take immediate needful corrective action on the points mentioned | SOD | Marketing | GZR | 2026-03-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-30 | AUD-2026-03-2000010729ACN-2026-03-4000127074 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127074 | 2026-09-12 | 37.7538 | 210 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127074 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127074 |  | AUD-2026-03-2000010729ACN-2026-03-4000127074 | 21 |  | 26 | 80 | 7 | 7 | 30
|  | CHANGMAI RAHUL | 2026-04-23 | Fire drill started monthly basis as per ERDMP.- Last Level 2 ERDMP done on 02/04/2026 | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127078 | Completed | CHANGMAI RAHUL | 2026-04-23 | During the fire drill it was checked | 2.5 | Emergency response preparedness reviewed | 1708 | DIMAPUR DEPOT | Depot has been advised to have a calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual | SOD | Marketing | GZR | 2026-04-15 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127078 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127078 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127078 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127078 |  | AUD-2026-03-2000010729ACN-2026-03-4000127078 | 21 |  | 26 | 80 | 7 | 7 | 33
|  | CHANGMAI RAHUL | 2026-04-23 | 26 CCTV rectified by CCTV Vendor as of 22/04/26 and 1 CCTV rectification process underway. | LOCATION VISIT - EZ | 2026-03-12 | AUD-2026-03-2000010729 | 2026-03-11 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127079 | Completed | CHANGMAI RAHUL | 2026-04-23 | All the 27 CCTV camera is down | 2.6 | CCTV functioning checked | 1708 | DIMAPUR DEPOT | Location to ensure to bring these camera back to operation ASAP in close coordination with vendor | SOD | Marketing | GZR | 2026-04-15 | INSTRUMENTATION OR ALARM FAILURES | 10 | CONTRACTOR SAFETY | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010729ACN-2026-03-4000127079 | NL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010729ACN-2026-03-4000127079 | 2026-09-12 | 37.7538 | 226 | >20 | AUD-2026-03-2000010729 - ACN-2026-03-4000127079 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM | AUD-2026-03-2000010729ACN-2026-03-4000127079 |  | AUD-2026-03-2000010729ACN-2026-03-4000127079 | 21 |  | 26 | 80 | 7 | 7 | 33
MEENA HIMANSHU | 2026-04-24 | SAINI JASVINDER SINGH | 2026-04-24 | MOVS repaired and parts changed. | AUDIT UPLOAD IN SAP | 2026-02-25 15:00 | AUD-2026-02-2000010963 | 2026-02-24 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-02-4000122366 | Closed | SAINI JASVINDER SINGH | 2026-04-24 | Order given to M/s Rotork for supply of mov spares. M/s Rotork is also providing AMC in Jodhpur Tml. Pls get all MOVs corrected | 6.3 | mov repair and communication | 1278 | JODHPUR TERMINAL | MOV to be repaired | SOD | Marketing | NWF | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 1 | ASSET INTEGRITY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010963ACN-2026-02-4000122366 | RJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010963ACN-2026-02-4000122366 | 2026-09-25 20:45 | 23.8893 | 235 | >20 | AUD-2026-02-2000010963 - ACN-2026-02-4000122366 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010963ACN-2026-02-4000122366 | AUD-2026-02-2000010963ACN-2026-02-4000122366 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 34
TAPAS RANJAN PANDA | 2026-04-29 | BHUYAN PRARTHANA | 2026-04-11 | Location acting on priority and in a timely manner on all the observations/ advices and noted the observation for future. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123971 | Closed | BHUYAN PRARTHANA | 2026-04-11 | Improvement vis-à-vis different parameters being shared time to time from zone | 1.8 | Improvement plans discussed | 1677 | GUWAHATI DEPOT | Location to act on priority and in a timely manner on all the observations/ advices | SOD | Marketing | GZR | 2026-03-10 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123971 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123971 | 2026-09-01 | 48.7538 | 240 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123971 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123971 | AUD-2026-03-2000011012ACN-2026-03-4000123971 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | 1. Megaphone being used now 2. Noted 3. SCABA being used now 4. Noted for future drills 5. Emergency gate is being opened | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123972 | Closed | BHUYAN PRARTHANA | 2026-04-11 | Single contingency is applicable to Guwahati and accordingly, simulated emergency scenario of pin-hole leakage between H and HH levels of MS Tank (TK-2). Gaps Observed : 1. Megaphone was not used 2. Miscommunication w.r.t scenerio to other stakeholders 3. SCABA not used 4. Product salvation not done and LEL clearance given after taking the reading 5. Emergency gate was not opened | 2.2 | Double contingency scenario simulated; observations recorded | 1677 | GUWAHATI DEPOT | More such drills to be conducted and all gaps identified to be plugged | SOD | Marketing | GZR | 2026-03-10 | LACK OF TRAINING OR COMPETENCY | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123972 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123972 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123972 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123972 | AUD-2026-03-2000011012ACN-2026-03-4000123972 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Location has developed a fire drill calendar & the same is in place. Monthly L1 drills are planned as per the calendar covering allthe scenarios as per ERDMP manual. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123973 | Closed | BHUYAN PRARTHANA | 2026-04-11 | During the fire drill it was checked | 2.5 | Emergency response preparedness reviewed | 1677 | GUWAHATI DEPOT | Depot has been advised to have a calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123973 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123973 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123973 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123973 | AUD-2026-03-2000011012ACN-2026-03-4000123973 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Noted and same is being monitored. Bifurcation of road from main entry to depot gate has been done with proper slotting & no trucksare allowed for parking in that stretch. Congestion in TT gantry is monitored by shifting some of the trucks (empty) in the lube godown area. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123974 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | All CCTV Camera were active | 2.6 | CCTV functioning checked | 1677 | GUWAHATI DEPOT | Random video recording of the CCTV were checked and it was advised to have more stringent control on TT movement inside depot. Depot should avoid congesion of TT inside the TTG. TT parking discpline to be maintained. No TTs should be parked at the entrance road from main road to depot. | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123974 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123974 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123974 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123974 | AUD-2026-03-2000011012ACN-2026-03-4000123974 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Noted and same is being done | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123975 | Closed | BHUYAN PRARTHANA | 2026-04-11 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. However, it was observed that the supporting document in line with alert closure not available with location e.g. records of counselling the TT crew for wearing safety harness belt/ wheel choke non compliance. | 2.7 | VA alerts checked / analysed | 1677 | GUWAHATI DEPOT | It was advised to have written record for such compliance advice to the TT crew and to take their acknowledgement | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 15 | PROCESS SAFETY | S3 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123975 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123975 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123975 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123975 | AUD-2026-03-2000011012ACN-2026-03-4000123975 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Noted and same is being done | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123977 | Closed | BHUYAN PRARTHANA | 2026-04-11 | New officers were not fully aware of the functioning / operation of the fire Engine & MEFG. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1677 | GUWAHATI DEPOT | It is advised to carry such hands on operation of safety critical equipment by all the officers | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123977 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123977 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123977 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123977 | AUD-2026-03-2000011012ACN-2026-03-4000123977 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Noted and same is being done through necessary training as per OISD STD 154 course module & various SST & gate meetings. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123978 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | Roadside emergency procedure awareness check carried out with TT crews. TT crews were found partial aware of emergency procedure. | 2.15 | TT crew roadside emergency procedures checked | 1677 | GUWAHATI DEPOT | DSO and LIC is advised to have proper dissemination of the information w.r.t action to be taken in such cases. | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123978 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123978 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123978 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123978 | AUD-2026-03-2000011012ACN-2026-03-4000123978 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Same is being followed and noted for future | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123981 | Closed | BHUYAN PRARTHANA | 2026-04-11 | It was given to understand that the reco is being done on Auto dips only except in case of exception like in Oct'25, UG tanks radars were under replacement. Conversion of TK-2 from MS to EBMS in Dec'25 and manual dip for quarter end closing and there was issue in radar for TK-7 in Jan'26 | 3.8 | Auto vs Manual reconciliation checked | 1677 | GUWAHATI DEPOT | LIC has been advised to ensure to take MOC approval in such cases where equipment is out of order and hence manual dip is to be put. | SOD | Marketing | GZR | 2026-03-10 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123981 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123981 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123981 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123981 | AUD-2026-03-2000011012ACN-2026-03-4000123981 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Same is being followed and noted for future. Except quarter end manual dip posting there are no instances of putting manual dip entry. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123982 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | It was given to understand that the reco is being done on Auto dips only except in case of exception like in Oct'25, UG tanks radars were under replacement. Conversion of TK-2 from MS to EBMS in Dec'25 and manual dip for quarter end closing and there was issue in radar for TK-7 in Jan'26 | 3.10 | TFMS/SAP reconciliation checked. | 1677 | GUWAHATI DEPOT | LIC has been advised to ensure to take MOC approval in such cases where equipment is out of order and hence manual dip is to be put. | SOD | Marketing | GZR | 2026-03-10 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123982 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123982 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123982 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123982 | AUD-2026-03-2000011012ACN-2026-03-4000123982 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Same is being followed and noted for future. All the necessary paintings of MS tanks TK-1 & TK-2 and TT gantry roof sheet completed. Arterial roads asphalting has been completed & dyke wall height has been increased. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123983 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | Housekeeping needs improvement. Tanks to be painted, dyke wall height to be increased. Road Asphalting to be done. Gantry Structure/ Gantry shed painting to done. | 3.15 | Housekeeping & PPE usage checked | 1677 | GUWAHATI DEPOT | In view of the OISD Audit scheduled from 21-23 Jan'26 and to maintain the hygiene of location, it was advised to take immediate corrective action to improve the housekeeping of the depot | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123983 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123983 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123983 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011012ACN-2026-03-4000123983 | AUD-2026-03-2000011012ACN-2026-03-4000123983 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Same is being followed and noted for future. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123984 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | MOC is being reviewed at zonal level on regular basis | 3.17 | MOC status reviewed | 1677 | GUWAHATI DEPOT | It is advised to close all the approved open where work is completed | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123984 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123984 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123984 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123984 | AUD-2026-03-2000011012ACN-2026-03-4000123984 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
TAPAS RANJAN PANDA | 2026-04-30 | BHUYAN PRARTHANA | 2026-04-11 | Noted & site clearance is taken care of. | LOCATION VISIT - EZ | 2026-01-17 | AUD-2026-03-2000011012 | 2026-01-15 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123986 | Closed | TAPAS RANJAN PANDA | 2026-04-30 | M&R Activity was going on in view of the upcoming ESA. Reviewed the work permit and JSA of the same | 4.2 | Maintenance activities reviewed | 1677 | GUWAHATI DEPOT | Location to ensure local site clearance w.r.t project material etc before completion of each project | SOD | Marketing | GZR | 2026-03-10 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011012ACN-2026-03-4000123986 | AS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011012ACN-2026-03-4000123986 | 2026-09-01 | 48.7538 | 241 | >20 | AUD-2026-03-2000011012 - ACN-2026-03-4000123986 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011012ACN-2026-03-4000123986 | AUD-2026-03-2000011012ACN-2026-03-4000123986 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 35
|  |  |  | RFD has been approved and auction is pending | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129954 | Open | DINESH KUMAR | 2026-07-07 | Location has approved RFDs for old CO TT and Miscellaneous scrap of 2MT | 3.9 | Abnormal variations / unused assets reviewed | 1254 | JALANDHAR DEPOT | scrap disposal to be completed by 30.06.2026 | SOD | Marketing | NFZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-07-31 | AUD-2026-05-2000011851ACN-2026-05-4000129954 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129954 | 2026-08-21 | 59.7538 | 302 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129954 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000011851ACN-2026-05-4000129954 |  | AUD-2026-05-2000011851ACN-2026-05-4000129954 | 21 |  | 27 | 80 | 0 | -21 | 44
|  |  |  | RFD approved , Auction pending | LOCATION VISIT-JALANDHAR_23-24.04.26 | 2026-04-24 | AUD-2026-05-2000011851 | 2026-04-23 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000129960 | Open | DINESH KUMAR | 2026-07-07 | Location has approved RFDs for old CO TT and Miscellaneous scrap of 2MT | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1254 | JALANDHAR DEPOT | location to dispose old Co. owned and misc. scrap identified | SOD | Marketing | NFZ | 2026-06-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-05-2000011851ACN-2026-05-4000129960 | PB | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000011851ACN-2026-05-4000129960 | 2026-08-21 | 59.7538 | 302 | >20 | AUD-2026-05-2000011851 - ACN-2026-05-4000129960 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000011851ACN-2026-05-4000129960 |  | AUD-2026-05-2000011851ACN-2026-05-4000129960 | 21 |  | 27 | 80 | 0 | -21 | 44
|  |  |  | For disposal of slow moving lube we have taken up the matter with retail and direct sales, we are in close follow up with them.For removal of FO line we need extra budget, we have asked extra budget from HQO, as soon as we will recieve budget this FO line removal task will be completed, we have taken quotation from vendors. After removal of FO lines , then after collecting all FO off spec product , disposal work will be initiated. | SENIOR MANAGEMENT INSPECTION | 2026-04-23 17:00 | AUD-2026-05-2000012001 | 2026-04-22 09:10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000129822 | Open | KUMAR ANIMESH | 2026-10-14 | all reviewed | 1.3 | Pending issues reviewed | 1636 | BALASORE DEPOT | disposal of slow moving lubes, removal of FO lines & disposal of offspec FO need to be focussed | SOD | Marketing | ECZ | 2026-09-30 | POOR PLANNING OR RISK ASSESSMENT | 12 | PROCESS SAFETY | S3 | F4 | 2026-09-30 | AUD-2026-05-2000012001ACN-2026-05-4000129822 | OR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012001ACN-2026-05-4000129822 | 2026-09-26 17:30 | 23.0247 | 394 | >20 | AUD-2026-05-2000012001 - ACN-2026-05-4000129822 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-05-2000012001ACN-2026-05-4000129822 |  | AUD-2026-05-2000012001ACN-2026-05-4000129822 | 21 |  | 27 | 80 | 12 | 12 | 57
[5 empty] | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000130101 | Open |  |  | 1st audit conducted by GM SWZ. Audit report no. AUD-2026-03-2000011134 | 1.4 | Earlier action points status checked | 1833 | COCHIN BLACK TERMINAL | "Pending observations 1. Manpower details including retiring officer details to be shared with zone - To expedite urgently 2. PESO permission for night operation - To be applied on priority 3. Civil consultant inspection for compound wall and Budget requirement to be submitted for repairs - To expedite health assessment urgently and undertake repair works needing immediate attention. Budegt requirement is to be submitted by May 2026 4. Location to close all NPCB projects within timelines - Action to be initiated urgently for both the open projects 5. Security to be trained with HVD/HZA endorsement - Review and take action 6. Location to close all NPCB projects within timelines - Action awaited. To handle on top most priroity. 7. Corrective action to be taken for smooth operation of monitor near TK-302 - completed. 8. Fit for road campaign to be conducted in March'26 and soft forms to be maintained for better monitoring - Job completed, soft forms to be maintained 9. Lighting Imporvement to be completed by 31.03.2026 - Completed. 10. Non working cameras to be made functional and MOC to be intaited - CCTVs are working 11. Location to follow up with TFMS vendor on continuous basis for stabilization - To complete by May 2026 12. Location to ensure PPEs for all workmen - compliance to be ensured for all workmen. 13. Grass cutting to be done - Job is in progress. 14. Compliance of MDSA 24-25, 25-26, Safe 100 : to be completed in a time bound manner. 15. Location to conduct monthly meetings with transporters 16. All projects to be completed in all aspects including capitalization, cloase out as per time lines 17. Company owned jeeps to be disposed off. Upiliftment to be completed" | SOD | Marketing | CZR | 2026-12-31 |  | 4 |  | S2 | F2 | 2026-12-31 | AUD-2026-05-2000012202ACN-2026-05-4000130101 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130101 | 2026-09-08 16:00 | 41.0872 | 486 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130101 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012202ACN-2026-05-4000130101 |  | AUD-2026-05-2000012202ACN-2026-05-4000130101 | 21 |  | 27 | 80 | 2 | 0 | 70
[5 empty] | GM-O&D INSPECTION AT COCHIN TERMINAL | 2026-05-12 | AUD-2026-05-2000012202 | 2026-05-11 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130112 | Open |  |  | No abnormal varioations reported | 3.9 | Abnormal variations / unused assets reviewed | 1833 | COCHIN BLACK TERMINAL | Tk 305 handling as per inspection recommendations Deletion of old asset of TK 303 & 307. | SOD | Marketing | CZR | 2026-06-30 |  | 2 |  | S1 | F2 | 2026-06-30 | AUD-2026-05-2000012202ACN-2026-05-4000130112 | KL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012202ACN-2026-05-4000130112 | 2026-09-08 16:00 | 41.0872 | 302 | >20 | AUD-2026-05-2000012202 - ACN-2026-05-4000130112 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012202ACN-2026-05-4000130112 |  | AUD-2026-05-2000012202ACN-2026-05-4000130112 | 21 |  | 27 | 80 | 2 | 0 | 44
[5 empty] | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000129558 | Open |  |  | Checked for TT Number : TS08UK4469 Found C2: + 3 Litres , For TT Number TS22UD5558 found C3 : +5 Litres , For TT Number TS08U 7790 found C1 : +20 Litres , C5 : +15 Litres , For TT Number TS22UD5558 found C3 : +5 Litres , For TT Numbers TS16UC3735 , TS08U1033 all Compartments found ok | 3.2 | Post-loading dip checks verified | 1919 | SECUNDERABAD TERMINAL | To re -check the calibration of TT no TS08U 7790 and also for TTs wherever excess product is observed. | SOD | Marketing | SCR | 2026-05-20 |  | 5 |  | S1 | F5 | 2026-05-20 | AUD-2026-05-2000012102ACN-2026-05-4000129558 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129558 | 2026-08-06 19:00 | 73.9622 | 261 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129558 | 532 | 8294 | 21 | 8294 | 152 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012102ACN-2026-05-4000129558 |  | AUD-2026-05-2000012102ACN-2026-05-4000129558 | 21 |  | 27 | 80 | 1 | -12 | 38
[5 empty] | AUDIT UPLOAD IN SAP | 2026-05-08 19:30 | AUD-2026-05-2000012102 | 2026-05-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 6.10 ADDITIONAL OBSERVATIONS | ACN-2026-05-4000129571 | Open |  |  | Lux Levels near the Tank manifold are not meeting requirements | 6.10 |  | 1919 | SECUNDERABAD TERMINAL | Lux Levels near the Tanks to be reviewed and to be improved | SOD | Marketing | SCR | 2026-08-31 |  | 5 |  | S1 | F5 | 2026-08-31 | AUD-2026-05-2000012102ACN-2026-05-4000129571 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012102ACN-2026-05-4000129571 | 2026-08-06 19:00 | 73.9622 | 364 | >20 | AUD-2026-05-2000012102 - ACN-2026-05-4000129571 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012102ACN-2026-05-4000129571 |  | AUD-2026-05-2000012102ACN-2026-05-4000129571 | 21 |  | 27 | 80 | 1 | -12 | 52
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | Briefing has been Done with the security guard . and Security agency has been informed to be more alert and vigilant. Thorough frisking has been done at Main Gate. Visitor pass is be issue to all visitor via Cbac and any Issue ingenerated the CBAC Gate pass is bening recored. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127624 | Closed | KUMAR MANISH | 2026-05-15 | Interaction was made with all the officers reviewing performance of each department in brief. Matters discussed were as follows: 1. Discussed malpractices cases which happened during the past in SOD locations and precautions to be taken by individuals. 2. Discussed safety related incidents which occurred at other locations and need for alertness & strict adherence to SOPs was emphasized. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1424 | JABALPUR DEPOT | Advised location to be alert and vigilant. Thorough frisking is to be carried out at Main Gate. Visitor pass to be issue to all visitor. The system placed at Main Gate to be used effectively. | SOD | Marketing | CEN | 2026-09-30 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127624 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127624 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127624 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127624 | AUD-2026-03-2000010981ACN-2026-03-4000127624 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | "TAS officer is dailing attending the issues and Calibration activities and if there is some Describanciy then Follow up is beingdone with the tas vendor. 2. LIC is carrying out EM locking checking and outcome to being recorded/maintained " | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127625 | Closed | KUMAR MANISH | 2026-05-15 | 1. TAS officer to focus on attending the issues on his own rather than everytime depending on TAS vendor. 2. Upon receipt of i-key, LIC to carryout EM locking checking and outcome to be recorded/maintained as per circular. | 1.8 | Improvement plans discussed | 1424 | JABALPUR DEPOT | 1. TAS officer to focus on attending the issues on his own rather than everytime depending on TAS vendor. 2. LIC to carryout EM locking checking and outcome to be recorded/maintained as per circular. | SOD | Marketing | CEN | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127625 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127625 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127625 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127625 | AUD-2026-03-2000010981ACN-2026-03-4000127625 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | During the safety Briefing the all the Teams of the Fire organisation Chart has been advised location to give more thrust on communication and proper coordination, work role assigned as per FOC. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127626 | Closed | KUMAR MANISH | 2026-05-15 | Fire drill are being conducted every month. Last drill was carried out by location on: 12/12/2025 | 2.1 | Fire drill conducted in last 6 months (surprise) | 1424 | JABALPUR DEPOT | Advised location to give more thrust on communication and proper coordination, assiging their work role during FF. | SOD | Marketing | CEN | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127626 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127626 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127626 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127626 | AUD-2026-03-2000010981ACN-2026-03-4000127626 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | During the safety Briefing the all the Teams of the Fire organisation Chart has been advised location to give more thrust on communication and proper coordination, work role assigned as per FOC. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127627 | Closed | KUMAR MANISH | 2026-05-15 | The safety and emergency preparedness was checked by carrying out surprised mock fire drill at MCC Room. The responses and shortcomings were discussed with all the participants team. The response was satisfactory. | 2.5 | Emergency response preparedness reviewed | 1424 | JABALPUR DEPOT | Advised location to give more thrust on communication and proper coordination, assiging their work role during FF. | SOD | Marketing | CEN | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 2 | PROCESS SAFETY | S1 | F2 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127627 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127627 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127627 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127627 | AUD-2026-03-2000010981ACN-2026-03-4000127627 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | Location has coordinated with the IOCL for expediting the Boundary wall work. Curently all Boaundary wall has been Completed. Only Plastering work is in progress. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127628 | Closed | KUMAR MANISH | 2026-05-15 | Earth pit observed in good condition. Boundary wall work between IOCL and HPCL is going on. IOCL is constructing the Boaundary wall. Vegetaion control is good. | 3.16 | Earth pits / boundary / vegetation control checked | 1424 | JABALPUR DEPOT | Advised location to coordinate with IOCL for expediting completion of Boundary wall | SOD | Marketing | CEN | 2026-09-30 | COST-CUTTING COMPROMISING SAFETY | 2 | PROCESS SAFETY | S2 | F1 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127628 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127628 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127628 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127628 | AUD-2026-03-2000010981ACN-2026-03-4000127628 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | All the Open points of the SSA has been Closed . And For the MDSA Targeted date is Dec 26 in SAP . | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127629 | Closed | KUMAR MANISH | 2026-05-15 | OISD/MDSA/SSA compliance has been reviewed. Nil pending OISD points. MDSA - (Dec`25 - 12 out 40 Points complied) SSA - (3 Pointspending) | 3.18 | OISD/MDSA/SSA compliance reviewed | 1424 | JABALPUR DEPOT | Location is advised to take immediate action for closure of open audit observation points | SOD | Marketing | CEN | 2026-12-31 | COST-CUTTING COMPROMISING SAFETY | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-31 | AUD-2026-03-2000010981ACN-2026-03-4000127629 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127629 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127629 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127629 | AUD-2026-03-2000010981ACN-2026-03-4000127629 | 21 | 21 | 26 | 80 | 0 | 0 | 70 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | Location has taken up with the Retails for the Stipulated Time unloading Operation at the Retail Outlet. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127630 | Closed | KUMAR MANISH | 2026-05-15 | Yes, meeting had with Transportor at location on 20.02.2026. The issues raised by them have been addressed. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1424 | JABALPUR DEPOT | Location is advised to coordinate with Dealears for hassle free unloading of Trpt TT's in a stipulated time. | SOD | Marketing | CEN | 2026-09-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127630 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127630 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127630 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127630 | AUD-2026-03-2000010981ACN-2026-03-4000127630 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | HSD Tanks painting work has been Complted on 24/03/2026 | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127631 | Closed | KUMAR MANISH | 2026-05-15 | Taken full field round covering TT Gantry, Tank Farm area, TW and TLF Pump House, Railway siding, Control Room, Security & Admin Blocks and get to know about completion of pending jobs. Currently, Tank painting jobs are in progress at location. It was suggested to take up with the contractor by asking him to deploy more manpower, working in two batches for expediting and timely completion. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1424 | JABALPUR DEPOT | Tank painting work needs to be expedited before 31.03.26. | SOD | Marketing | CEN | 2026-03-30 | COST-CUTTING COMPROMISING SAFETY | 2 | PROCESS SAFETY | S1 | F2 | 2026-03-30 | AUD-2026-03-2000010981ACN-2026-03-4000127631 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127631 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127631 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127631 | AUD-2026-03-2000010981ACN-2026-03-4000127631 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 37
SATHYAJITH A. | 2026-05-15 | KUMAR MANISH | 2026-05-15 | RFD has been Initiated and sent for the Approval. Cureently with the HQO . And as per the last visist of the Ed SOD , Disposal has been Kept On Hold. | LOCATION VISIT AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010981 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127632 | Closed | KUMAR MANISH | 2026-05-15 | Nil scrap at the location. However, action has been initiated by location for disposal of idle FO facilities. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1424 | JABALPUR DEPOT | Expedite disposal of FO facilities. | SOD | Marketing | CEN | 2026-09-30 | OUTDATED OR COMPLEX SOPS | 1 | PROCESS SAFETY | S1 | F1 | 2026-09-30 | AUD-2026-03-2000010981ACN-2026-03-4000127632 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010981ACN-2026-03-4000127632 | 2026-09-26 17:30 | 23.0247 | 256 | >20 | AUD-2026-03-2000010981 - ACN-2026-03-4000127632 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010981ACN-2026-03-4000127632 | AUD-2026-03-2000010981ACN-2026-03-4000127632 | 21 | 21 | 26 | 80 | 0 | 0 | 57 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Training to TAS officer is provided on 10-11 April. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122682 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Yes, Interacted with all officers . The newly joined officers were guided to be more involved and execute the given task independently. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1656 | DURGAPUR DEPOT | The officers were guided to be alert on safe practice in operations. They should have hands on experience to operate all the safetycritical equipment. TAS being critical area in day to day operation, it is recommended to have close checks and controls | SOD | Marketing | EZ | 2026-03-10 | POOR PLANNING OR RISK ASSESSMENT | 10 | EMERGENCY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122682 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122682 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122682 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122682 | AUD-2026-03-2000011011ACN-2026-03-4000122682 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | HVLR is now operable from 10.04.2026 | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122694 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | HVLR no. 2 & 3 observed down and the panels were sent to OEM. MOC approval for the non functional HVLR 2 & 4 is not taken. ESD operated and worked properly. All the associated logic worked in field and TAS control system | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1656 | DURGAPUR DEPOT | HVLR being safety critical equipment, must be brought back to operation urgently in close coordination with vendor. | SOD | Marketing | EZ | 2026-03-10 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 15 | ASSET INTEGRITY | S3 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122694 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122694 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122694 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122694 | AUD-2026-03-2000011011ACN-2026-03-4000122694 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | FE, HVLR, CCTV, DG, PUMPS are working | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122695 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Yes FE, Monitor, MEFG were operated by officers. Heavy leakage observed from the swivel joint of Fire water monitor no. 7 | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1656 | DURGAPUR DEPOT | DSO & LIC to ensure all safety critical equipment works properly. | SOD | Marketing | EZ | 2026-03-10 | COMPLACENCY OR RISK NORMALIZATION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122695 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122695 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122695 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122695 | AUD-2026-03-2000011011ACN-2026-03-4000122695 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Training compliant to CMV Rule-9 is completed, WB-RTO endorsement process is pending. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122696 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Trained personnel is available in depot but there is no HVD/HZA endorsement | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1656 | DURGAPUR DEPOT | Location to engages/ arrange the make shift arrangement for such availability | SOD | Marketing | EZ | 2026-03-10 | THIRD PARTY ERRORS | 10 | EMERGENCY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122696 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122696 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122696 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122696 | AUD-2026-03-2000011011ACN-2026-03-4000122696 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Training to TT Crew is provided for handling Road side emergencies. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.15 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122697 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Roadside emergency procedure awareness check carried out with TT crews. TT crews were found partial aware of emergency procedure. | 2.15 | TT crew roadside emergency procedures checked | 1656 | DURGAPUR DEPOT | DSO and LIC is advised to have proper dissemination of the information w.r.t action to be taken in such cases | SOD | Marketing | EZ | 2026-03-10 | INADEQUATE SAFETY CULTURE | 10 | EMERGENCY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122697 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122697 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122697 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122697 | AUD-2026-03-2000011011ACN-2026-03-4000122697 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Conducted Similar Mock Drill on 27.04.2026 by including all ooficers and stakeholders. Corrective action was taken. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122688 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Location is single contingency. A leakage scenario from TK-4 was given to the officers who were engaged in planning late evening and following are the observations : 1. Delay observed in start of the drill 2. There was communication gap b/w officers and security 3. Sprinkler was operated for Tk-3 (nearby tank) and later for Tk-4 4. There was no usages of MEFG 6. Officer entered the tank dyke without product savaging 7. ESD/ siren was not operated | 2.2 | Double contingency scenario simulated; observations recorded | 1656 | DURGAPUR DEPOT | It was advised to conduct more similar drill with more inclusion of all officers and stakeholders. Corrective actions advised to be taken care | SOD | Marketing | EZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122688 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122688 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122688 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122688 | AUD-2026-03-2000011011ACN-2026-03-4000122688 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Fortnightly night inspection is being carried out now. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122690 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Night visit was made on 27.02.26 and security alertness was checked. The condition was found satisfactory. | 2.4 | Security alertness checked (night-halt / surprise checks) | 1656 | DURGAPUR DEPOT | Location didn't produced the records and evidence of fortnightly surprise night inspection from Dec'25 onwards. LIC to ensure fortnightly night inspection is carried out | SOD | Marketing | EZ | 2026-03-15 | THIRD PARTY ERRORS | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122690 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122690 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122690 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122690 | AUD-2026-03-2000011011ACN-2026-03-4000122690 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Yearly fire drill planning is made covering all scenario as per the ERDMP. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122691 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | During the fire drill it was checked | 2.5 | Emergency response preparedness reviewed | 1656 | DURGAPUR DEPOT | Depot has been advised to have a calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual | SOD | Marketing | EZ | 2026-03-15 | INSUFFICIENT SUPERVISION | 5 | EMERGENCY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122691 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122691 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122691 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000122691 | AUD-2026-03-2000011011ACN-2026-03-4000122691 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Non-working CCTV cameras are now working. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122692 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | 3 cameras were not active I.e. Perimeter 6, Bay 3&4, Out Gate locking. | 2.6 | CCTV functioning checked | 1656 | DURGAPUR DEPOT | All the non working CCTV cameras are of critical area. Location to ensure to bring these camera back to operation ASAP in close coordination with vendor | SOD | Marketing | EZ | 2026-03-15 | THIRD PARTY ERRORS | 10 | EMERGENCY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122692 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122692 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122692 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122692 | AUD-2026-03-2000011011ACN-2026-03-4000122692 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | VA alerts are being closed timely | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122693 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. However, it was observed that the supporting document in line with alert closure not available with location e.g. records of counselling the TT crew for wearing safety harness belt/ wheel choke non compliance. | 2.7 | VA alerts checked / analysed | 1656 | DURGAPUR DEPOT | It is advised to coordinate with the vendor and to have all the cameras live on VA. Further, It is also advised to have written record for such compliance advice to the TT crew and to take their acknowledgement | SOD | Marketing | EZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 10 | EMERGENCY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000122693 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122693 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122693 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122693 | AUD-2026-03-2000011011ACN-2026-03-4000122693 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | MOC for the same has been taken. Tanks are put in exception. Radar gauge procurement from Hassan Terminal in process. Tender from HQO awaited. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123953 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Location has confirmed that the auto dips are not getting posted for TK-1, TK-2, TK-13 and TK-14 due to radar gauge issue. | 3.10 | TFMS/SAP reconciliation checked | 1656 | DURGAPUR DEPOT | Location to take MOC approval immediately for conducting the reco on manual dips. Also, to take up the matter with vendor for earlyrectification of radar dips not getting posted | SOD | Marketing | EZ | 2026-03-10 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123953 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123953 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123953 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123953 | AUD-2026-03-2000011011ACN-2026-03-4000123953 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | BAY 1,3 was powered off. Since MFMs for these bays along with Bay 2 are coonected in a single loop and cutoff in between leads to lag in communication and abnormal readings of MFM captured in system communicated by AST. No abnormal difference showing now | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123954 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Checked same. In BCU no. 502A on 31.12.2025, difference of 185 litre was observed | 3.11 | MFM vs BCU totalizer comparison checked | 1656 | DURGAPUR DEPOT | Location to revert with their analysis and revert with the justification/ corrective action taken | SOD | Marketing | EZ | 2026-03-10 | INSTRUMENTATION OR ALARM FAILURES | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123954 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123954 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123954 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123954 | AUD-2026-03-2000011011ACN-2026-03-4000123954 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | MOC obtained for the same. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123955 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | It is observed that the water tank dips are not getting posted in TAS and hence location is operating acknowledging the gantry permissive. It is given to understand that the radar gauzes are out of CAMC and vendor is not providing the service for this and hence, radar gauze procurement is being carried out thru HQO tender It is noted that there is no approved MOC available | 3.12 | Critical alarms checked & corrective actions reviewed | 1656 | DURGAPUR DEPOT | Location to immediately get the MOC approval followed by close coordination with HQO for early procurement and installation of radar gauge | SOD | Marketing | EZ | 2026-03-09 | COMPLACENCY OR RISK NORMALIZATION | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-09 | AUD-2026-03-2000011011ACN-2026-03-4000123955 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123955 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123955 | 532 | 8294 | 21 | 8294 | 224 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123955 | AUD-2026-03-2000011011ACN-2026-03-4000123955 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Pending points are closed now | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123959 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | SSA- 1 point is open having target date of 30.06.26 MDSA -1 point is open having target date of 30.11.25 | 3.18 | OISD/MDSA/SSA compliance reviewed | 1656 | DURGAPUR DEPOT | LIC to ensure close monitoring and SAP closure for MDSA point. If to be kept open, LIC to submit proper explanation | SOD | Marketing | EZ | 2026-03-09 | INSUFFICIENT SUPERVISION | 10 | EMERGENCY | S2 | F5 | 2026-03-09 | AUD-2026-03-2000011011ACN-2026-03-4000123959 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123959 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123959 | 532 | 8294 | 21 | 8294 | 224 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123959 | AUD-2026-03-2000011011ACN-2026-03-4000123959 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Ladder is removed from roof | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123964 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | ladder was found on the roof of HSD AG tank TK-2 | 6.1 | Additional Observations | 1656 | DURGAPUR DEPOT | To be removed immediately | SOD | Marketing | EZ | 2026-03-05 | INADEQUATE SAFETY CULTURE | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000123964 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123964 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123964 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123964 | AUD-2026-03-2000011011ACN-2026-03-4000123964 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Correct RH are reprinted | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123965 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | RH for AG tanks were not matching in field with actual after addition of spool piece in the dip gauge well | 6.2 | Additional Observations | 1656 | DURGAPUR DEPOT | Corrective action to be taken immediately | SOD | Marketing | EZ | 2026-03-05 | POOR COMMUNICATION | 10 | OCCUPATIONAL HEALTH | S2 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000123965 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123965 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123965 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123965 | AUD-2026-03-2000011011ACN-2026-03-4000123965 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-16 | HARAPRASAD GUCHHAIT | 2026-05-16 | Unsafe act are being recorded now. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123966 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Upon review of the CCTV camera recording for date 31.01.26 it is noticed that many unsafe proactive is being undertaken at depot Ingate however, no such activity has been reported. | 6.3 | Additional Observations | 1656 | DURGAPUR DEPOT | Location to ensure 100% adherence of SOP and NIL unsafe act is performed inside depot. | SOD | Marketing | EZ | 2026-03-05 | INADEQUATE SAFETY CULTURE | 15 | EMERGENCY | S3 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000123966 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123966 | 2026-08-07 13:00 | 73.2122 | 257 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123966 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123966 | AUD-2026-03-2000011011ACN-2026-03-4000123966 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | 18 Secondary Routes created post review of route deviation in novex platform limiting VTS violations.to minimum Dip checking & recording of 100% of TTs are done. Dip checking done of first three loads after calibration and records maintained. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123990 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Day-to-day operational activities were reviewed. Both Junior Executives were appreciated, in the presence of the LIC, for their commendable performance and initiative in independently handling planning, rake loading, rake unloading, and tanker unloading operations, reflecting effective ownership and operational competence. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1650 | HALDIA TERMINAL | Location to improve secondary route creation, control TDG violations, DIP checking by officers at TT gantry for 100% of TTs loaded and for first 3 loads post TT calibration | SOD | Marketing | EZ | 2026-03-21 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-21 | AUD-2026-03-2000011013ACN-2026-03-4000123990 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123990 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123990 | 532 | 8294 | 21 | 8294 | 212 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123990 | AUD-2026-03-2000011013ACN-2026-03-4000123990 | 21 | 21 | 26 | 80 | 5 | 5 | 29 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Both the JEO have had hands on training & have led both Combat teams and have fought fire scenarios in all drills subsequently ,same also appreciated in Comprehensive Audit.LIC to arrest the black oil rake receipt losses by suitable coordination and actions. All JVs with HPPL should be completed. LIC to take up with HPPCL for boundary wall b/w Terminal and HPPCL station. Proposal for ECapproval initiated for security services eff. 01.07.2026 and is in process of approval. The payment anomaly with HDC is under reconciliation . Additional TT induction donevas per requirement . Meeting with transporters and DCTs scheduled on 25th May to take on board for conversion of their TTs to bottom loading. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123991 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Individual review of officer carried out with respect to KPI and overall location performance with respect to monthly MIS reports. | 1.2 | Performance review conducted | 1650 | HALDIA TERMINAL | Both the Junior Executives were advised to have hand on exercise for operating all the fire fighting equipment. LIC to arrest the black oil rake receipt losses by suitable coordination and actions. All JVs with HPPL should be completed. LIC to take up with HPPCL for boundary wall b/w Terminal and HPPCL station. Proposal for EC approval should be initiated for security services eff. 01.07.2026. The payment anomaly with HDC should be reconciled. Additional TT induction process to be initiated. Transporters and DCTs to be taken on board for conversion of their TTs to bottom loading. | SOD | Marketing | EZ | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011013ACN-2026-03-4000123991 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123991 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123991 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123991 | AUD-2026-03-2000011013ACN-2026-03-4000123991 | 21 | 21 | 26 | 80 | 5 | 5 | 31 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | All IRR closed. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123992 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Nil issue reported by location officers | 1.3 | Pending issues reviewed | 1650 | HALDIA TERMINAL | 1 no. of IRR to be closed | SOD | Marketing | EZ | 2026-03-07 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-07 | AUD-2026-03-2000011013ACN-2026-03-4000123992 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123992 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123992 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123992 | AUD-2026-03-2000011013ACN-2026-03-4000123992 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | 100% TT dip checking data is updated in SAP on regular basis. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123993 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Compliance to zonal/HQO circular is being carried out | 1.7 | Compliance to HQO/Zonal circulars reviewed | 1650 | HALDIA TERMINAL | Location to upload the 100%TT dip checking data in SAP. | SOD | Marketing | EZ | 2026-03-05 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011013ACN-2026-03-4000123993 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123993 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123993 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123993 | AUD-2026-03-2000011013ACN-2026-03-4000123993 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Monthly & half yearly drills conducted in line with ERDMP scenarios and performance reviewed and Trainings conducted with contract workmen regarding emergency response. Location has since covered all the scenarios as per ERDMP and was appreciated in last conducted Comprehensive Audit in Jan26. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123994 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Fire Scenarios in Black oil tank was simulated and mobile HVLR was asked to operate. There was a delay in pulling the mobile HVLR from its original position to the simulated site. However the mobile HVLR operated satisfactorily. All the stakeholders were well aware w.r.t its functionality | 2.1 | Fire drill conducted in last 6 months (surprise) | 1650 | HALDIA TERMINAL | It was advised to have quick response in case of any such scenario. Location to cover all the scenario as per ERDMP during their fire drills. It is advised to have a calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual | SOD | Marketing | EZ | 2026-03-10 | POOR COMMUNICATION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011013ACN-2026-03-4000123994 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123994 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123994 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123994 | AUD-2026-03-2000011013ACN-2026-03-4000123994 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Performance reviewed in each Mockdrills & Recommendations are implemented in the conducted drills.Mega Phone is used now extensively along with Walkie tales which is now integrated with PA system of terminal during Mock Drills. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123995 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Double contingency fire simulated in the TWG and AG Tank Farm. The drill scenario was well communicated to all the stakeholders. The drill went well & all the members of different teams executed their role properly. Mega Phone to be used in all the drills | 2.2 | Double contingency scenario simulated; observations recorded | 1650 | HALDIA TERMINAL | All the observation and recommendation of the drill to be implemented in the next drill | SOD | Marketing | EZ | 2026-03-10 | POOR COMMUNICATION | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011013ACN-2026-03-4000123995 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123995 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123995 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123995 | AUD-2026-03-2000011013ACN-2026-03-4000123995 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | AllOldFlood lights LEDd have been repaired. Lux levels gabe bee reverified in secondary roads post flood lights rectification and found at 16 lux levels which is greater than required levels | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123996 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Lux level checked : TT gantry : Required : 60 and observed : 157 Secondary roads : Required 10 and observed 8 at several places | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1650 | HALDIA TERMINAL | It was advised to improve the lux levels on the secondary roads by repairing the old lights | SOD | Marketing | EZ | 2026-03-10 | POOR EQUIPMENT MAINTENANCE | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-10 | AUD-2026-03-2000011013ACN-2026-03-4000123996 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123996 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123996 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011013ACN-2026-03-4000123996 | AUD-2026-03-2000011013ACN-2026-03-4000123996 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Security maintaining stringent frisking procedures of the personnel entering Terminal. Each Tank Truck Cabin is checked by Securityprior entry to the Terminal. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123997 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Location has total of 68 CCTV Camera and all were active on the date of visit | 2.6 | CCTV functioning checked | 1650 | HALDIA TERMINAL | Randaom video recording of the CCTV at main gate area were chevked and it was advised to have more stringent frisking of the personnel entering terminal premise to be done. Security personnel were advised to be more watchful in the cabins of the Trucks entering the depot. | SOD | Marketing | EZ | 2026-03-05 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011013ACN-2026-03-4000123997 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123997 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123997 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123997 | AUD-2026-03-2000011013ACN-2026-03-4000123997 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Supporting document in line with alert closure prepared. Records maintained. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123998 | Closed | ISLAM SK WAHIUL | 2026-05-16 | VA Alerts were randomly reviewed. It is noticed that location is timely closing the VA alerts. However, it was observed that the supporting document in line with alert closure not available with location e.g. records of counselling the TT crew for not wearing safety harness belt/ wheel choke non compliance. | 2.7 | VA alerts checked / analysed | 1650 | HALDIA TERMINAL | It was advised to have written record for such complaince advice to the TT crew and to take their acknowledgement | SOD | Marketing | EZ | 2026-03-05 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011013ACN-2026-03-4000123998 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123998 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123998 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123998 | AUD-2026-03-2000011013ACN-2026-03-4000123998 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Access control system of the license entry gate is fully functional now. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123999 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Access control system of the lisence entry gate was not functional. Location informed that the vendor M/s godrej already visited the site and it will be rectified by Feb'26 | 2.8 | Access control systems checked | 1650 | HALDIA TERMINAL | Location to clsoely coordinate with M/s Godrej and ensure 100% functionality of the access control system | SOD | Marketing | EZ | 2026-03-05 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011013ACN-2026-03-4000123999 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000123999 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000123999 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000123999 | AUD-2026-03-2000011013ACN-2026-03-4000123999 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | All open points pertaining to SSA & MDSA are pertaining to Tank repairs and will be closed in current FY2026-27 along with Comprehensive inspection. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124004 | Closed | ISLAM SK WAHIUL | 2026-05-16 | OISD - NIL pending Point SSA - 5 Pending point MDSA - 6 pending point | 3.18 | OISD/MDSA/SSA compliance reviewed | 1650 | HALDIA TERMINAL | Location to clsoe the open points at the earliest | SOD | Marketing | EZ | 2026-03-31 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-31 | AUD-2026-03-2000011013ACN-2026-03-4000124004 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124004 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124004 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011013ACN-2026-03-4000124004 | AUD-2026-03-2000011013ACN-2026-03-4000124004 | 21 | 21 | 26 | 80 | 5 | 5 | 31 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | 18 Secondary Routes created after analysing route deviation which has reduced VTS violations to minimum | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124000 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Review of VTS deviation done on regualr basis from zone. Location is taking action on VTS deviation basis mail received from zone and from OCC | 3.3 | VTS deviations reviewed | 1650 | HALDIA TERMINAL | Location is advised to create the secondary route wherever applicable | SOD | Marketing | EZ | 2026-03-10 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-10 | AUD-2026-03-2000011013ACN-2026-03-4000124000 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124000 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124000 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011013ACN-2026-03-4000124000 | AUD-2026-03-2000011013ACN-2026-03-4000124000 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | EBP checked on regular basis and records maintained in daily closing stock reports | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124001 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Random chekcing of EBP done from the all level sample of TT and the EBP% found ok | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1650 | HALDIA TERMINAL | Location to ensure EBP checks daily of the outgoing trucks and records maintained. | SOD | Marketing | EZ | 2026-03-05 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-05 | AUD-2026-03-2000011013ACN-2026-03-4000124001 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124001 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124001 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000124001 | AUD-2026-03-2000011013ACN-2026-03-4000124001 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | the said set of Locks has been sent to Lock testing facility in Coimbatore and needful ITDG action will be taken once report is received and lock found tampered with | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124002 | Closed | ISLAM SK WAHIUL | 2026-05-16 | EM lock SOP compliance verified at field and found to be being followed. TT no WB29B6336 & WB29A7912 checked with I-key and the result was satisfactory. I-key was not getting inserted in the lock no. HE24351 of TT no. WB136480 and lock no. HE33544 of TT no. WB29B5626. Sterna representative at site was also advised on the non insertion of the i-key. | 3.5 | EM Lock SOP compliance verified | 1650 | HALDIA TERMINAL | Lock no. HE9318 of TPT TT no. WB11C5095 was suspected to have abused. LIC was adviced to sent the lock to the sterna workshop/ lab for further investigation | SOD | Marketing | EZ | 2026-03-15 | POOR EQUIPMENT MAINTENANCE | 10 | ASSET INTEGRITY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011013ACN-2026-03-4000124002 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124002 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124002 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011013ACN-2026-03-4000124002 | AUD-2026-03-2000011013ACN-2026-03-4000124002 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | Black Oil Is received in Rakes and in last FY huge receipt losses have been received and Wagon wise dip &temp Sheet shared with VNBOT against each rakes receipts. Although Terminal could book operation gains but Receipt losses have summarily consumed the Opns gains. | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000124003 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Abnormal stock variations are being analysed periodically by zone and response from location are reviewed. | 3.9 | Abnormal variations / unused assets reviewed | 1650 | HALDIA TERMINAL | Black oil losses to be brought under control | SOD | Marketing | EZ | 2026-03-07 | POOR PLANNING OR RISK ASSESSMENT | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-07 | AUD-2026-03-2000011013ACN-2026-03-4000124003 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124003 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124003 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000124003 | AUD-2026-03-2000011013ACN-2026-03-4000124003 | 21 | 21 | 26 | 80 | 5 | 5 | 27 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | MS rake unloading PO being placed by CPO in current month, Jobs will commence once PO is released . | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124005 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Each Project progress was reviewed and depot ensured to close all the project witin timeline. | 4.3 | Project progress reviewed | 1650 | HALDIA TERMINAL | It is advised to process the tendering for MS rake unloading line facility and ensure to complete the facility well within scheduled AR closure date | SOD | Marketing | EZ | 2026-07-31 | POOR COMMUNICATION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-07-31 | AUD-2026-03-2000011013ACN-2026-03-4000124005 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124005 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124005 | 532 | 8294 | 21 | 8294 | 80 | 80 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000124005 | AUD-2026-03-2000011013ACN-2026-03-4000124005 | 21 | 21 | 26 | 80 | 5 | 5 | 48 | 37
KUNDU DEBARUN | 2026-05-16 | ISLAM SK WAHIUL | 2026-05-16 | 100% of identified Physical scrap disposed with a Sale value 70.6 Lakhs | LOCATION VISIT - EZ | 2026-01-30 | AUD-2026-03-2000011013 | 2026-01-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124006 | Closed | ISLAM SK WAHIUL | 2026-05-16 | Scrap Dispoal activity was not on the track. Special drive taken from Zone to facilitate the scrap disposal in this FY | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1650 | HALDIA TERMINAL | LIC to ensure 100% physical disposal by 20th Mar'26 | SOD | Marketing | EZ | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 4 | ASSET INTEGRITY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011013ACN-2026-03-4000124006 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011013ACN-2026-03-4000124006 | 2026-08-20 00:14 | 60.7441 | 257 | >20 | AUD-2026-03-2000011013 - ACN-2026-03-4000124006 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011013ACN-2026-03-4000124006 | AUD-2026-03-2000011013ACN-2026-03-4000124006 | 21 | 21 | 26 | 80 | 5 | 5 | 31 | 37
MAJUMDER BIRAJ | 2026-05-16 | BUDHI VEERAIAH | 2026-05-16 | i) The CBAC system is operational and regular followup is being made with M/s Godrej to maintain it operational uninterruptedly. ii) Necessary trainings and briefings have been provided to the security guads on security checks of Bio diesel and Ethanol TTs entering product pump house area. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127097 | Closed | MAJUMDER BIRAJ | 2026-05-16 | Improvement plans vis-à-vis different parameters being shared time to time from zone. Location to act on priority and in a timely manner on all the observations/ advice | 1.8 | Improvement plans discussed | 1644 | KOLKATA-I TERMINAL | CBAC to be made operational in Tank Farm, TT Gantry. Security check for Ethanol and Biodiesel TT entry in Pump house area for unloading to be strengthened. | SOD | Marketing | EZ | 2026-04-15 | LACK OF TRAINING OR COMPETENCY | 10 | PROCESS SAFETY | S2 | F5 | 2026-04-15 | AUD-2026-03-2000010730ACN-2026-03-4000127097 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127097 | 2026-09-18 | 31.7538 | 257 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127097 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010730ACN-2026-03-4000127097 | AUD-2026-03-2000010730ACN-2026-03-4000127097 | 21 | 21 | 26 | 80 | 0 | -7 | 33 | 37
MAJUMDER BIRAJ | 2026-05-16 | BUDHI VEERAIAH | 2026-05-16 | CBAC system is made operational at the site and regular followup is being with M/s Godrej to maintain it operational uninterruptedly. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127502 | Closed | MAJUMDER BIRAJ | 2026-05-16 | Access control system at Tank farm, TTG found to be non functional. | 2.8 | Access control systems checked | 1644 | KOLKATA-I TERMINAL | Location to clsoely coordinate with M/s Godrej and ensure 100% functionality of the access control system | SOD | Marketing | EZ | 2026-04-15 | INSUFFICIENT SUPERVISION | 8 | PROCESS SAFETY | S2 | F4 | 2026-04-15 | AUD-2026-03-2000010730ACN-2026-03-4000127502 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127502 | 2026-09-18 | 31.7538 | 257 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127502 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010730ACN-2026-03-4000127502 | AUD-2026-03-2000010730ACN-2026-03-4000127502 | 21 | 21 | 26 | 80 | 0 | -7 | 33 | 37
MAJUMDER BIRAJ | 2026-05-16 | BUDHI VEERAIAH | 2026-05-16 | All Earthpit boards have been updated as per the latest test record. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127508 | Closed | MAJUMDER BIRAJ | 2026-05-16 | Earthpit board to be corrected. All the boards were having stickers pasted with EP details. | 3.16 | Earth pits / boundary / vegetation control checked | 1644 | KOLKATA-I TERMINAL | Corrective action to be taken | SOD | Marketing | EZ | 2026-04-15 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-15 | AUD-2026-03-2000010730ACN-2026-03-4000127508 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127508 | 2026-09-18 | 31.7538 | 257 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127508 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127508 | AUD-2026-03-2000010730ACN-2026-03-4000127508 | 21 | 21 | 26 | 80 | 0 | -7 | 33 | 37
MAJUMDER BIRAJ | 2026-05-16 | BUDHI VEERAIAH | 2026-05-16 | Siphon breaker and Rim seal change have been completed is done for all the 3 MS EFR tanks. Off-spec inventory liquidation is expedited through regular follow ups with HQO Team . | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127511 | Closed | MAJUMDER BIRAJ | 2026-05-16 | Siphon breaker and Rim seal change job was undergoing. Completed for 2 out of 3 tanks. | 4.2 | Maintenance activities reviewed | 1644 | KOLKATA-I TERMINAL | Location to expedire the job for the 3rd tank and complete it on priority Off Spec inventory liquidation to be expedited | SOD | Marketing | EZ | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-03-2000010730ACN-2026-03-4000127511 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127511 | 2026-09-18 | 31.7538 | 257 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127511 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010730ACN-2026-03-4000127511 | AUD-2026-03-2000010730ACN-2026-03-4000127511 | 21 | 21 | 26 | 80 | 0 | -7 | 35 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | New Lights has been provided and checking of the lights is in progress. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122689 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Lux level checked : TT gantry : Required : 60 and observed : 105 Secondary roads : Required 10 and observed 4 at several places | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1656 | DURGAPUR DEPOT | It is advised to improve the lighting on the secondary roads as per the requirement | SOD | Marketing | EZ | 2026-03-15 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 10 | PROCESS SAFETY | S2 | F5 | 2026-03-15 | AUD-2026-03-2000011011ACN-2026-03-4000122689 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000122689 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000122689 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000122689 | AUD-2026-03-2000011011ACN-2026-03-4000122689 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | Second Safety harness gauge has been installed at all the bays of TTG. Second Safety harness also installed at Ethanol TT unloadingshed. NIL PPE usages deviation and 100% SOP compliance has been ensured. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123957 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Housekeeping practice is found satisfactory. PPE usages needs to be more strengthened. Second safety harness belt were missing for 5 bays at TTG and Ethanol unloading shed. Many PPE usages violations observed Safety harness not available for TT In and Out gate. Single harness is available at Ethanol TT unloading shed | 3.15 | Housekeeping & PPE usage checked | 1656 | DURGAPUR DEPOT | Second Safety harness gauge to be installed at all the bays of TTG. Second Safety harness also to be installed at Ethanol TT unloading shed. LIC to ensured NIL PPE usages deviation and 100% SOP compliance. Double safety harness belt is to be provided at all applicable places | SOD | Marketing | EZ | 2026-03-05 | INADEQUATE SAFETY CULTURE | 15 | ASSET INTEGRITY | S3 | F5 | 2026-03-05 | AUD-2026-03-2000011011ACN-2026-03-4000123957 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123957 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123957 | 532 | 8294 | 21 | 8294 | 228 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011011ACN-2026-03-4000123957 | AUD-2026-03-2000011011ACN-2026-03-4000123957 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | Replacement of communication devices of gauges in tanks by procuring new radar gauges for which PO placement from HQO is awaited. Levels monitored through manual dip checking daily. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123951 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Physical dip taken for AG TK-2 (HSD) , AG TK-4 (MS) and UG TK-7 (HSD) & UG TK-9 (MS). Observed difference in product and water dip for TK-4, TK7 & TK-9. Difference observed in mentioned TAS V/s Actual dip and also RH of AG tanks | 3.7 | Inventory physical dip of minimum two tanks taken | 1656 | DURGAPUR DEPOT | Location to immediately carry out the necessary corrective action in coordination with the vendor and till that time auto dip for all the tanks to be verified with manual dip for all the tanks and reco to be done accordingly. MOC to be taken for above. All RH of the tanks to be corrected. | SOD | Marketing | EZ | 2026-03-07 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-07 | AUD-2026-03-2000011011ACN-2026-03-4000123951 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123951 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123951 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123951 | AUD-2026-03-2000011011ACN-2026-03-4000123951 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | MOC taken. Tanks put in exception | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 3.8 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123952 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Location has confirmed that the auto dips are not getting posted for TK-1, TK-2, TK-13 and TK-14 due to radar gauge issue. | 3.8 | Auto vs Manual reconciliation checked | 1656 | DURGAPUR DEPOT | Location to take MOC approval immediately for conducting the reco on manual dips. Also, to take up the matter with vendor for earlyrectification of radar dips not getting posted | SOD | Marketing | EZ | 2026-03-10 | THIRD PARTY ERRORS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123952 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123952 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123952 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123952 | AUD-2026-03-2000011011ACN-2026-03-4000123952 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | RFD will be prepared by next week i.e. by 23.05.2026. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123962 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | Scrap Disposal activity is on the track. Physical disposal completed for Rs. 2.31 Lakhs and Rs. 4.45 lakhs scrap auction scheduled. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1656 | DURGAPUR DEPOT | LIC to ensure 100% disposal of scrap by Mar'26 | SOD | Marketing | EZ | 2026-03-25 | INSUFFICIENT SUPERVISION | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-03-25 | AUD-2026-03-2000011011ACN-2026-03-4000123962 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123962 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123962 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123962 | AUD-2026-03-2000011011ACN-2026-03-4000123962 | 21 | 21 | 26 | 80 | 0 | 0 | 30 | 37
KUMAR ANAND | 2026-05-17 | HARAPRASAD GUCHHAIT | 2026-05-16 | Yes, 100% updation of all the reading with signature on the same day of PLT operation has been ensured. | LOCATION VISIT - EZ | 2026-02-27 23:59 | AUD-2026-03-2000011011 | 2026-02-26 13:26 | Confirmed | I1815 | PM - Senior Management Inspection | 5.1 POST-VISIT REPORTING | ACN-2026-03-4000123963 | Closed | HARAPRASAD GUCHHAIT | 2026-05-16 | It is given to understand that the location is carrying out the MFM based accounting only. However, the opening / closing details of IOC MFM data was not available for many last PLTs. Upon review of the signed scan data of MFM opening and closing reading for 15.01.26, there was no details mention in HPCL register. Signatures/ opening closing reading at IOC an HPC end were missing for may transactions | 5.1 | MFM based accounting at Pipeline and OMC location | 1656 | DURGAPUR DEPOT | Location to ensure 100% updation of all the reading with signature on the same day of PLT operation. The IOC signed documents to be maintained in a file so that it is available for inspection / cross verification at a later date | SOD | Marketing | EZ | 2026-03-10 | INSUFFICIENT SUPERVISION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000011011ACN-2026-03-4000123963 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011011ACN-2026-03-4000123963 | 2026-08-07 13:00 | 73.2122 | 258 | >20 | AUD-2026-03-2000011011 - ACN-2026-03-4000123963 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011011ACN-2026-03-4000123963 | AUD-2026-03-2000011011ACN-2026-03-4000123963 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 37
|  | JERRY JOSEPH | 2026-05-18 | Secondary Routes have been created | ZONAL VISIT REPORT25.02.2026LONITERMINAL | 2026-02-25 | AUD-2026-03-2000011168 | 2026-02-25 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123416 | Completed | JERRY JOSEPH | 2026-05-18 | Deviations reviewed and advised correction/ secondary route creation for 13 routes | 3.3 | VTS deviations reviewed | 1584 | LONI TERMINAL | XX | SOD | Marketing | WZ | 2026-03-31 |  | 2 |  | S1 | F2 | 2026-03-31 | AUD-2026-03-2000011168ACN-2026-03-4000123416 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011168ACN-2026-03-4000123416 | 2026-10-15 | 4.7538 | 211 | >20 | AUD-2026-03-2000011168 - ACN-2026-03-4000123416 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011168ACN-2026-03-4000123416 |  | AUD-2026-03-2000011168ACN-2026-03-4000123416 | 21 |  | 26 | 80 | 18 | 18 | 31
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-19 | DIWAKAR KAMLESH KUMAR | 2026-05-15 | VA alerts are being monitored and are closed on daily basis. VTS is being monitored and corrective action are being taken place. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125081 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-15 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, CCTV and VA alerts monitoring ,Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 3708 | VISAKH NBOT | VA alerts to be reviewed and closed on daily basis | SOD | Marketing | SCR | 2026-03-11 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-11 | AUD-2026-03-2000011315ACN-2026-03-4000125081 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125081 | 2026-09-18 17:30 | 31.0247 | 260 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125081 | 532 | 8294 | 21 | 8294 | 222 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125081 | AUD-2026-03-2000011315ACN-2026-03-4000125081 | 21 | 21 | 26 | 80 | 2 | 1 | 28 | 38
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-19 | DIWAKAR KAMLESH KUMAR | 2026-05-15 | Emergency Gate Hooter rectified and now alarm can be heard. Fireman axe procured and kept in Emergency trolley. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125085 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-15 | Emergency response preparedness checked during fire drill. DCP FE , Foam Monitors , operated by location officers, Emergency Trolley checked, Emergency gate opened and checked | 2.5 | Emergency response preparedness reviewed | 3708 | VISAKH NBOT | Emergency gate Hooter not working , to be rectified. Emergency Trolley items are not as per displayed name plate and many items were found missing. | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125085 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125085 | 2026-09-18 17:30 | 31.0247 | 260 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125085 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125085 | AUD-2026-03-2000011315ACN-2026-03-4000125085 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 38
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-19 | DIWAKAR KAMLESH KUMAR | 2026-05-15 | New CCTV camera procured vide Contract No : 5300043818 Date : 06.02.2026 placed on M/s VIHAWK TECH SOLUTIONS PVT. LTD. Installation of Camera completed and now all cameras are working.Corrective action taken on CCTV cameras nos 167,168 ,170 . Camera no 176 focusadjusted. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125086 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-15 | CCTV functioning checked . 39 out 39 cameras are active in VA. Out of the total 59 CCTV cameras , 4 cameras beyond repair and PO placed for new cameras and installation of new CCTV cameras is in progress. CCTV cameras nos 167 and 168 to be realigned . CCTV Camera170 is hazy , Camera no 176 focus to be adjusted. | 2.6 | CCTV functioning checked | 3708 | VISAKH NBOT | New CCTV cameras installation to be expedited. CCTV cameras nos 167 and 168 to be realigned . CCTV Camera 170 is hazy , Camera no 176 focus to be adjusted. | SOD | Marketing | SCR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125086 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125086 | 2026-09-18 17:30 | 31.0247 | 260 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125086 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125086 | AUD-2026-03-2000011315ACN-2026-03-4000125086 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 38
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-19 | DIWAKAR KAMLESH KUMAR | 2026-05-15 | VA alerts time has been increased for TT Gantry 2 | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125087 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-15 | VA alerts checked , analysed and closed by Location Officers/ LIC | 2.7 | VA alerts checked / analysed | 3708 | VISAKH NBOT | VA alerts time to be increased for bitumen gantry , to take up with vendor for modification | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125087 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125087 | 2026-09-18 17:30 | 31.0247 | 260 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125087 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125087 | AUD-2026-03-2000011315ACN-2026-03-4000125087 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | All NPCB Project AR comleted within given timeline. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127855 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Performance review done. NPCB projects to be completed within time and no AR extension | 1.2 | Performance review conducted | 1953 | RAJAHMUNDRY TERMINAL | 3 AR s to be closed by 31.03.26 . | SOD | Marketing | SCR | 2026-03-31 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127855 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127855 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127855 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127855 | AUD-2026-04-2000011082ACN-2026-04-4000127855 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Open irregularity Closed applicable dormant keys recovered. Capex achieved 4.39 against target of 4.3 Total Capatilization completed 4.55 Cr | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127856 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Pending Issues reviewed. Irregularity pertaining TT contaminated product submitted for closure . Dormant Keys to be recovered. Capex to be improved | 1.3 | Pending issues reviewed | 1953 | RAJAHMUNDRY TERMINAL | To follow up and close the Open irregularity and get back the dormant keys . Capex to be improved and max. capitalisation to be done before year end. | SOD | Marketing | SCR | 2026-04-30 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011082ACN-2026-04-4000127856 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127856 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127856 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127856 | AUD-2026-04-2000011082ACN-2026-04-4000127856 | 21 | 21 | 26 | 80 | 1 | 2 | 35 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | NA6A sprinkler valve greasing completed and moving smoothly, Mock fire Drills being conducted every month and also table top excercise being conducted before fire drill to improve communication and performance during drill. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127859 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Fire drill with double contingency scenario conducted on 25.03.2026. Observations - Fire at Slop Pump was declared and due to improper communication workman operated DCP FE at a different place initially and later operated at correct place.MEFG was not operated in time.SCABA rope length not proper and not properly wound. Tank 6A sprinklers could not be operated in time. | 2.2 | Double contingency scenario simulated; observations recorded | 1953 | RAJAHMUNDRY TERMINAL | Communication among the team members need to be improved. Fire chief to improve communication during the fire fighting operations, To find root cause of failure to operate TK6A sprinklers. Mock fire Drills to be practised for further improvement. | SOD | Marketing | SCR | 2026-03-31 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127859 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127859 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127859 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127859 | AUD-2026-04-2000011082ACN-2026-04-4000127859 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Turnstile issue rectified and made functional during vendor visit dated 21.04.2026. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127862 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | CBAC at Terminal Entrance gate the incoming turnstile is working, outgoing Turnstile under repair. Presently for both incoming and outgoing same Turnstile is being used. | 2.8 | Access control systems checked | 1953 | RAJAHMUNDRY TERMINAL | Turnstile to be rectified and put back in use. | SOD | Marketing | SCR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127862 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127862 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127862 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127862 | AUD-2026-04-2000011082ACN-2026-04-4000127862 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Pending Route corrections completed. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127864 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | VTS deviations reviewed | 3.3 | VTS deviations reviewed | 1953 | RAJAHMUNDRY TERMINAL | Pending Route corrections to be completed. | SOD | Marketing | SCR | 2026-04-15 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-15 | AUD-2026-04-2000011082ACN-2026-04-4000127864 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127864 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127864 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127864 | AUD-2026-04-2000011082ACN-2026-04-4000127864 | 21 | 21 | 26 | 80 | 1 | 2 | 33 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Lock no 29267 of TT AP02TE3456 and lock no 29068 of TT AP39Y6089 sent to M/S STERNA for Third party checking. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127865 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | EM Locks verfied for TTs AP39WE8497, AP02TE3456, AP16TA0005, AP39Y6089,AP39UA9465. Lock no 29267 of TT AP02TE3456 and lock no 29068of TT AP39Y6089 to be sent to M/S STERNA for checking | 3.5 | EM Lock SOP compliance verified | 1953 | RAJAHMUNDRY TERMINAL | Lock no 29267 of TT AP02TE3456 and lock no 29068 of TT AP39Y6089 to be sent to M/S STERNA for checking | SOD | Marketing | SCR | 2026-04-15 | INSTRUMENTATION OR ALARM FAILURES | 5 | ASSET INTEGRITY | S1 | F5 | 2026-04-15 | AUD-2026-04-2000011082ACN-2026-04-4000127865 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127865 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127865 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127865 | AUD-2026-04-2000011082ACN-2026-04-4000127865 | 21 | 21 | 26 | 80 | 1 | 2 | 33 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | MFM vs BCU report being reviewed and signed by LIC and sent to zone for review on daily basis. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127867 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | MFM VS BCU totalizer comparision checked on random basis, no abnormal variation. | 3.11 | MFM vs BCU totalizer comparison checked | 1953 | RAJAHMUNDRY TERMINAL | LIC to review and sign on daily basis | SOD | Marketing | SCR | 2026-03-26 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-26 | AUD-2026-04-2000011082ACN-2026-04-4000127867 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127867 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127867 | 532 | 8294 | 21 | 8294 | 207 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127867 | AUD-2026-04-2000011082ACN-2026-04-4000127867 | 21 | 21 | 26 | 80 | 1 | 2 | 30 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | False alarm for Tank NA6A rectified by vendor during AMC visit in April 2026. Tank Leakage alarm configured in TAS. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127868 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Critical alarms reviewed | 3.12 | Critical alarms checked & corrective actions reviewed | 1953 | RAJAHMUNDRY TERMINAL | HHH alarms for empty tank TK6B generated , to take up with vendor for stopping of false alarms. Tank Leakage alarms to be configured. | SOD | Marketing | SCR | 2026-04-15 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-15 | AUD-2026-04-2000011082ACN-2026-04-4000127868 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127868 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127868 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127868 | AUD-2026-04-2000011082ACN-2026-04-4000127868 | 21 | 21 | 26 | 80 | 1 | 2 | 33 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Strainer cleaning completed reference workpermit no 100000761517 and all DCP FE servicing dates updated. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127870 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Maintenance activities reviewed, Strainer cleaning at product pump house and OMC pump house is over due. Fire extinguishers servicing dates to be updated. | 4.2 | Maintenance activities reviewed | 1953 | RAJAHMUNDRY TERMINAL | Strainer cleaning to be completed within due date . DCP FE servicing dates to be updated. | SOD | Marketing | SCR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127870 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127870 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127870 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127870 | AUD-2026-04-2000011082ACN-2026-04-4000127870 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | No NPCB Project for UPS allotted. Other allotted NPCB projects completed within given timeline. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127871 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | NPCB project for Supply and Installation of UPS is delayed. | 4.3 | Project progress reviewed | 1953 | RAJAHMUNDRY TERMINAL | To follow up with vendor for supply of UPS by 15.03.26 | SOD | Marketing | SCR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127871 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127871 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127871 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127871 | AUD-2026-04-2000011082ACN-2026-04-4000127871 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Ensured timely completion of PM Jobs and closing of PM orders in system. For FY 2025-26 100% PM jobs completed in given timeline and for april 2026 also all PM order closed in given timeline. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-04-4000127872 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | PM compliance reviewed , delay in closing of PM orders | 4.4 | Quality of PM compliance reviewed | 1953 | RAJAHMUNDRY TERMINAL | To ensure timely completion of PM Jobs and closing of PM orders | SOD | Marketing | SCR | 2026-03-26 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-26 | AUD-2026-04-2000011082ACN-2026-04-4000127872 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127872 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127872 | 532 | 8294 | 21 | 8294 | 207 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127872 | AUD-2026-04-2000011082ACN-2026-04-4000127872 | 21 | 21 | 26 | 80 | 1 | 2 | 30 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | Security advised and trained to do proper frisking of all employees, contractors, workmen and visitors without fail. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-04-4000127875 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Security did not do frisking properly | 6.1 |  | 1953 | RAJAHMUNDRY TERMINAL | Security to do proper frisking of all employees, contractors, workmen and visitors | SOD | Marketing | SCR | 2026-03-26 | FAILURE TO FOLLOW PROCEDURES | 5 | CONTRACTOR SAFETY | S1 | F5 | 2026-03-26 | AUD-2026-04-2000011082ACN-2026-04-4000127875 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127875 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127875 | 532 | 8294 | 21 | 8294 | 207 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127875 | AUD-2026-04-2000011082ACN-2026-04-4000127875 | 21 | 21 | 26 | 80 | 1 | 2 | 30 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-20 | Work Completed. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000127860 | Closed | JAYA PRAKASH PRADHAN | 2026-05-20 | Emergency response preparedness checked during fire drill. DCP FE , HVLRs , Foam Monitors , MEFGs , Tank Sprinklers operated by location officers, Emergency Trolley checked, Emergency exit gate checked. | 2.5 | Emergency response preparedness reviewed | 1953 | RAJAHMUNDRY TERMINAL | Emergency Trolley items are not as per name plate. Some of the items viz SCABA, Search Lights, Safety Goggles, Electrical Gloves , Electric tester, Petroleum clean up chemical are missing . To take corrective action for emergency trolley availability with all therequired items. | SOD | Marketing | SCR | 2026-03-31 | FATIGUE AND STRESS | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011082ACN-2026-04-4000127860 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127860 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127860 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127860 | AUD-2026-04-2000011082ACN-2026-04-4000127860 | 21 | 21 | 26 | 80 | 1 | 2 | 31 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-20 | Dips corrected in the system during TFMS AMC visit on Date 19.05.2026. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000127866 | Closed | JAYA PRAKASH PRADHAN | 2026-05-20 | MS tank Tank 2B and Ethanol Tank 1C Physical dip checked. TK2B physical dip 194.8 cms, water nil against TAS dip of 194.8 cms. Water - nil , TK 1C Physical dip 704.7 cms and TAS dip is 704.2 cms. | 3.7 | Inventory physical dip of minimum two tanks taken | 1953 | RAJAHMUNDRY TERMINAL | to take up with TAS vendor for the variation in physical and TAS dip for tank 1C | SOD | Marketing | SCR | 2026-04-15 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-04-15 | AUD-2026-04-2000011082ACN-2026-04-4000127866 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127866 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127866 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127866 | AUD-2026-04-2000011082ACN-2026-04-4000127866 | 21 | 21 | 26 | 80 | 1 | 2 | 33 | 38
SINGH SOMESH | 2026-05-20 | JAYA PRAKASH PRADHAN | 2026-05-02 | SOPs being followed for all opertaions by officers officers taking regular field rounds and reporting near miss if any Location is doing VTS monitoring for nil route deviations and nil speed violations CCTV monitoring done on regular basis by officer and security and records maintained. | AUDIT UPLOAD IN SAP | 2026-03-25 17:15 | AUD-2026-04-2000011082 | 2026-03-25 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000127857 | Closed | JAYA PRAKASH PRADHAN | 2026-05-02 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, Nil pending indents, Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 1953 | RAJAHMUNDRY TERMINAL | SOPs to be followed for all opertaions , officers to take regular field rounds, VTS monitoring for nil route deviations and nil speed violations, CCTV monitoring on daily basis and records to be maintained | SOD | Marketing | SCR | 2026-03-26 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-26 | AUD-2026-04-2000011082ACN-2026-04-4000127857 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011082ACN-2026-04-4000127857 | 2026-07-22 18:30 | 88.983 | 261 | >20 | AUD-2026-04-2000011082 - ACN-2026-04-4000127857 | 532 | 8294 | 21 | 8294 | 207 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-04-2000011082ACN-2026-04-4000127857 | AUD-2026-04-2000011082ACN-2026-04-4000127857 | 21 | 21 | 26 | 80 | 1 | 2 | 30 | 38
|  | PAMPANABOYINA SWARNA REKHA | 2026-05-21 | Four tanks are idle since 2012. To assess the fitness of the tank a comprehensive inspection for tk1, tk3,tk5,&tk6 were conducted byTUV RHEINLAND(INDIA) PVT.LTD. | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000126438 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-05-21 | The idling four tanks heavily rusted | 1.8 | Improvement plans discussed | 3693 | KAKINADA TML | The idling four tanks comprehensive inspection to be carried out | SOD | Marketing | SCR | 2026-03-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000126438 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126438 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126438 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126438 |  | AUD-2026-04-2000011081ACN-2026-04-4000126438 | 21 |  | 26 | 80 | 0 | 0 | 31
|  |  |  | Bio Diesel Tank is Comissioned and 58KL is taken in Tank of 70 KL Capacity . Receipt -Dispatch Line work is completed for Bio Diesel facility. Loading Arms at Bay No 8. works under progress. Wiring of MFM/DCV Completed. Comissioning /Stamping will be completed by31.10.2026 | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.7 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125484 | Open | NEHARA AJAY | 2026-10-17 | It was observed that location is not ensuring sufficient bio diesel blending in TT dispatches. Advised location to follow up and ensure improved performance. | 1.7 | Bio Diesel Tank is Comissioned and 58KL is taken in Tank of 70 KL Capacity . Receipt -Dispatch Line work is completed for Bio Diesel facility. Loading Arms at Bay No 8. works under progress. Wiring of MFM/DCV Completed. Comissioning /Stamping will be completed by30.09.2026 | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2026-10-31 | AUD-2026-03-2000011072ACN-2026-03-4000125484 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125484 | 2026-08-16 | 64.7538 | 210 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125484 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011072ACN-2026-03-4000125484 |  | AUD-2026-03-2000011072ACN-2026-03-4000125484 | 21 |  | 26 | 80 | 2 | 2 | 30
|  |  |  | Presently Provisioning of additional lights provided and repair of existing lights completed to meet OISD 244 lux requirements. However due to low lux level proposal for two Nos of additional High Mast Towers were approved but budget was not allocated in this FY | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125486 | Open | NEHARA AJAY | 2026-10-17 | Lux levels were checked in night time and observed not meeting at some areas as work is already in progress for provisioning of additional lights and repair of existing lights to meet OISD 244 lux requirements. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2027-12-31 | AUD-2026-03-2000011072ACN-2026-03-4000125486 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125486 | 2026-08-16 | 64.7538 | 241 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125486 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011072ACN-2026-03-4000125486 |  | AUD-2026-03-2000011072ACN-2026-03-4000125486 | 21 |  | 26 | 80 | 2 | 2 | 35
|  |  |  | "1. TT Parking Facility to be provided . 2. ERDMP manual prepared and audit completed in 10.10.2026. Fire emergency manual is being prepared .3.ETP Work is in progress. TOTAL 3 PENDING & 3 COMPLETED . EDC except parkingpoint - 31.12.2026, EDC - Parking - 31.12.2027" | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125494 | Open | NEHARA AJAY | 2026-10-17 | Current compliance status of SSA has been discussed with Kandla team with action plan for ensuring time bound closure of pending 6 Nos recommendations. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S2 | F2 | 2027-12-31 | AUD-2026-03-2000011072ACN-2026-03-4000125494 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125494 | 2026-08-16 | 64.7538 | 394 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125494 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011072ACN-2026-03-4000125494 |  | AUD-2026-03-2000011072ACN-2026-03-4000125494 | 21 |  | 26 | 80 | 2 | 2 | 57
TAK MITHLESH KUMAR | 2026-05-21 |  |  | Matter is taken up with Zone /HQO for Allocation of Funds | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000126000 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | It is observed that some of the required materials are not avaialble in trolley and kept in Admin building. | 6.2 | Emergency Trolley | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000011072ACN-2026-03-4000126000 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000126000 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000126000 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000126000 | AUD-2026-03-2000011072ACN-2026-03-4000126000 | 21 | 21 | 26 | 80 | 2 | 2 | 30 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | HMT was proposed in NPCB 2026-27 cycle . However Budget was put on hold till date | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125495 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | Full field visit of Tank farm area, pump house, foam shed etc, housekeeping and clearance of roads around tank farm area to be improved. Project material is lying along the road adjacent to black oil dyke which is damaged due to ongoing project work. Advised location to complete the construction of road for vehicle movement at the earliest. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125495 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125495 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125495 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125495 | AUD-2026-03-2000011072ACN-2026-03-4000125495 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | Presently VTS deviations are reviwed on Novex Portal. All deviations are handled to Novex portal Only. Action Taken is also recorded in Novex Portal. For Route Deviations further take up with Sales Officers on email for correction of routes . | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125490 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | Yes reviewed and observed that verification is not done by LIC with provided Intelligent key by HQO. | 3.5 | EM Lock SOP compliance verified | 1583 | KANDLA TERMINAL | Location to ensure correction action in line with circular for verification within 15 days. LIC to ensure verification of locks using Intelligent Key provided by HQO and record details on provided link by HQO in line with SOP/Circular. | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125490 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125490 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125490 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011072ACN-2026-03-4000125490 | AUD-2026-03-2000011072ACN-2026-03-4000125490 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | Verification by LIC is carried out for truck No: GJ12BZ5373/GJ12BZ6237/GJ12AZ7654 on 18.05.2026 | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125489 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | Yes reviewed but records not maintained for action taken cases. | 3.3 | VTS deviations reviewed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125489 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125489 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125489 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011072ACN-2026-03-4000125489 | AUD-2026-03-2000011072ACN-2026-03-4000125489 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | Dyke wall/Road-01, ETP-01, TAS/ESD-01, Earthpits-01, TT Parking -01 and ERDMP-01 | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125492 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | During field round of Tank farm area, pump house, foam shed etc, housekeeping and clearance of roads around tank farm area to be improved. Project material is lying along the road adjacent to black oil dyke which is damaged due to ongoing project work. Advised location to complete the construction of road for vehicle movement at the earliest. | 3.15 | Housekeeping & PPE usage checked | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125492 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125492 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125492 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011072ACN-2026-03-4000125492 | AUD-2026-03-2000011072ACN-2026-03-4000125492 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | FLP torch and First Aid Box are provided in trolly. | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125483 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | Yes discussed. Support required for fund allocation for tank dismantleing under revenue budget 2026-27. | 1.5 | HQO / Zonal support required identified | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-12-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-30 | AUD-2026-03-2000011072ACN-2026-03-4000125483 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125483 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125483 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125483 | AUD-2026-03-2000011072ACN-2026-03-4000125483 | 21 | 21 | 26 | 80 | 2 | 2 | 70 | 38
TAK MITHLESH KUMAR | 2026-05-21 |  |  | 1. Lock No : Top-21963 has been sent to OEM via gate pass No : 11583-O-006039 dated 06.02.2026. Third Party Inspection report fromOEM Sterna Pvt Ltd not yet received. | SENIOR MANAGEMENT INSPECTION KANDLA TERM | 2026-02-05 | AUD-2026-03-2000011072 | 2026-02-04 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125482 | Closed | TAK MITHLESH KUMAR | 2026-05-21 | Following pending issues were discussed with Location team- 1. Availbility of sufficient tankage for bio diesel storage and provisioning of bio diesel blending at TTG. 2. Status of dismantalling of Old scrap tanks advised during HQO visit. 3. Segregation of reusable items collected during dismantalling of facilities and to be shared with zone. | 1.3 | Pending issues reviewed | 1583 | KANDLA TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011072ACN-2026-03-4000125482 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011072ACN-2026-03-4000125482 | 2026-08-16 | 64.7538 | 262 | >20 | AUD-2026-03-2000011072 - ACN-2026-03-4000125482 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011072ACN-2026-03-4000125482 | AUD-2026-03-2000011072ACN-2026-03-4000125482 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Officers are regularly taking field rounds across the Terminal to monitor ongoing activities and ensure adherence to safety procedures and operational discipline. Safety observations are being communicated to concerned personnel for immediate corrective action wherever required. | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125057 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Interacted with all officers of terminal. Overview of terminal facilities, project status & operational issues at terminal | 1.1 | Interaction with all officers (1–1.5 hrs) | 1992 | VISAKH WHITE OIL TERMINAL | Officers to take regular field rounds to ensure safety in Terminal activities | SOD | Marketing | SCR | 2026-03-12 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-12 | AUD-2026-03-2000011314ACN-2026-03-4000125057 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125057 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125057 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125057 | AUD-2026-03-2000011314ACN-2026-03-4000125057 | 21 | 21 | 26 | 80 | 3 | 2 | 28 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Closed ARs NPCB projects | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125058 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Performance review done. NPCB projects to be completed within time . | 1.2 | Performance review conducted | 1992 | VISAKH WHITE OIL TERMINAL | Seven ARs to be closed by 31.03.2026 | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125058 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125058 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125058 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125058 | AUD-2026-03-2000011314ACN-2026-03-4000125058 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Made first payment to VPA for ABD project and completed SS JEtty pipeline hookup | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125059 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Pending Issues reviewed . | 1.3 | Pending issues reviewed | 1992 | VISAKH WHITE OIL TERMINAL | First payment to VPA to be made for ABD project, SS Jetty pipeline hook up to be completed before 23.03.2026 | SOD | Marketing | SCR | 2026-03-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000011314ACN-2026-03-4000125059 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125059 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125059 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125059 | AUD-2026-03-2000011314ACN-2026-03-4000125059 | 21 | 21 | 26 | 80 | 3 | 2 | 29 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | VA alerts are being monitored daily and being closed | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125060 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, CCTV and VA alerts monitoring ,Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 1992 | VISAKH WHITE OIL TERMINAL | VA alerts to be reviewed and closed on daily basis | SOD | Marketing | SCR | 2026-03-12 | POOR COMMUNICATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-12 | AUD-2026-03-2000011314ACN-2026-03-4000125060 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125060 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125060 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125060 | AUD-2026-03-2000011314ACN-2026-03-4000125060 | 21 | 21 | 26 | 80 | 3 | 2 | 28 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | VTS and CCTV monitoring is being done and records maintained | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125061 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | VTS monitoring , CCTV monitoring by officers on daily basis. | 1.8 | Improvement plans discussed | 1992 | VISAKH WHITE OIL TERMINAL | VTS monitoring , CCTV monitoring to be done by officers on daily basis and records to be maintained | SOD | Marketing | SCR | 2026-03-12 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-12 | AUD-2026-03-2000011314ACN-2026-03-4000125061 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125061 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125061 | 532 | 8294 | 21 | 8294 | 221 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125061 | AUD-2026-03-2000011314ACN-2026-03-4000125061 | 21 | 21 | 26 | 80 | 3 | 2 | 28 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Shortcomings observed are improved in next drill | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125062 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Mock Drill conducted on 10.03.2026 with Double contingency scenario. Mock Drill Observations for improvement i) Emergency Trolley not reported at incident site ii) Delay by rescue team in providing stretcher at second incident site iii) Communication team could not demonstrate active participation in the fire drill iv) All clear siren not operated properly as per norms. | 2.2 | Double contingency scenario simulated; observations recorded | 1992 | VISAKH WHITE OIL TERMINAL | Short comings observed in the fire drill to be improved in next mock drills | SOD | Marketing | SCR | 2026-03-31 | INADEQUATE SAFETY CULTURE | 5 | EMERGENCY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125062 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125062 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125062 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125062 | AUD-2026-03-2000011314ACN-2026-03-4000125062 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Items as per OISD are made available in the Emergency Trolley | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125064 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Emergency response preparedness checked HVLR , MEFG , Tank Sprinklers operated by location officers, Emergency Trolley checked, Emergency gate opened and checked | 2.5 | Emergency response preparedness reviewed | 1992 | VISAKH WHITE OIL TERMINAL | Emergency Trolley items are not as per displayed name plate and some items found missing | SOD | Marketing | SCR | 2026-03-20 | POOR EQUIPMENT MAINTENANCE | 5 | EMERGENCY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000011314ACN-2026-03-4000125064 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125064 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125064 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125064 | AUD-2026-03-2000011314ACN-2026-03-4000125064 | 21 | 21 | 26 | 80 | 3 | 2 | 29 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Corrective action for CCTV cameras taken | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125065 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | CCTV functioning checked . 67 out 67 cameras are active in VA. CCTV cameras nos 160 focus to be corrected, camera no 218 focus is not proper, camera nos 161 & 162 light focus alignment to be corrected, for camera no 160 tree branches are obstructing , to be trimmed. | 2.6 | CCTV functioning checked | 1992 | VISAKH WHITE OIL TERMINAL | Corrective action to be taken for CCTV nos mentioned in observation. | SOD | Marketing | SCR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125065 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125065 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125065 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125065 | AUD-2026-03-2000011314ACN-2026-03-4000125065 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Taken up the issue with vendor and it is rectified | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125066 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Very few VA alerts being generated . VA alerts for DCP, wheel Choke not generated . | 2.7 | VA alerts checked / analysed | 1992 | VISAKH WHITE OIL TERMINAL | Location to take up with vendor for VA alerts not getting generated for TT Gantry area | SOD | Marketing | SCR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125066 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125066 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125066 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125066 | AUD-2026-03-2000011314ACN-2026-03-4000125066 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Received 20kl ARAFFF vide contract 5300041264 | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125067 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Total Foam Available 38.1 KL against requirement of 36.3 KL . | 2.9 | Foam inventory verified | 1992 | VISAKH WHITE OIL TERMINAL | PO placed for ARFFF foam, to follow up with vendor and receive the PO quantity by 31.03.2026 | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | EMERGENCY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125067 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125067 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125067 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125067 | AUD-2026-03-2000011314ACN-2026-03-4000125067 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Ensuring 5% dips check on daily basis | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125068 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Post Loading dip checks verified for TTs AP31TP2679 and AP28TE7269.For TT no AP31TP2679 filled dip is excess by 1 mm for comp 4 & 5and 3 mm for compt 3 . For TT no AP28TE 7269 excess dip of 1 mm observed for compt 2 and 3. | 3.2 | Post-loading dip checks verified | 1992 | VISAKH WHITE OIL TERMINAL | Location to closely monitor the post loading dips of TTs ( Min 5% on daily basis). In case of excess qty, to cross check qty with prover calibration. | SOD | Marketing | SCR | 2026-03-25 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-25 | AUD-2026-03-2000011314ACN-2026-03-4000125068 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125068 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125068 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125068 | AUD-2026-03-2000011314ACN-2026-03-4000125068 | 21 | 21 | 26 | 80 | 3 | 2 | 30 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Water dip correction done in coordination with HAIL | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125069 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Tank 205 and Tank 206 Physical dip checked. TK 205 physical dip 168.8 cms(O+W) versus TAS dip of 168.6cms and water dip of 7.3 cms against TAS water dip of 6.4 cms. TK 206 Physical dip 918.4 cms(O+W) and TAS dip of 918.2 cms and water dip of 4.0 cms against TAS water dip of 3.9 cms. | 3.7 | Inventory physical dip of minimum two tanks taken | 1992 | VISAKH WHITE OIL TERMINAL | To take up withTAS vendor for Tank 205 water dip correction. | SOD | Marketing | SCR | 2026-03-25 | INADEQUATE SAFETY CULTURE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-25 | AUD-2026-03-2000011314ACN-2026-03-4000125069 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125069 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125069 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125069 | AUD-2026-03-2000011314ACN-2026-03-4000125069 | 21 | 21 | 26 | 80 | 3 | 2 | 30 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Necessary action is taken and closing alerts | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.12 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125070 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Critical alarms of tank leakage generated for ethanol tank and no of HHH alarms generated for tank 504 which were found to be falsealarms. | 3.12 | Critical alarms checked & corrective actions reviewed | 1992 | VISAKH WHITE OIL TERMINAL | All critical alarms to be checked , root cause to be analysed , recorded before closing the alerts. Location to take up with TAS Vendor to rectify the false alarms being generated. | SOD | Marketing | SCR | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000011314ACN-2026-03-4000125070 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125070 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125070 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125070 | AUD-2026-03-2000011314ACN-2026-03-4000125070 | 21 | 21 | 26 | 80 | 3 | 2 | 28 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | PM jobs are being completed and closed without delay | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125075 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | PM compliance reviewed , delay in closing of PM orders | 4.4 | Quality of PM compliance reviewed | 1992 | VISAKH WHITE OIL TERMINAL | PM Jobs to be completed in time and PM orders closed without delay | SOD | Marketing | SCR | 2026-05-30 | POOR EQUIPMENT MAINTENANCE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-05-30 | AUD-2026-03-2000011314ACN-2026-03-4000125075 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125075 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125075 | 532 | 8294 | 21 | 8294 | 142 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125075 | AUD-2026-03-2000011314ACN-2026-03-4000125075 | 21 | 21 | 26 | 80 | 3 | 2 | 39 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | PULI JYOTSNA LATHA | 2026-05-21 | Disposal completed | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125076 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | Scrap worth Rs 20.0 lakhs disposed and another Rs.16.0 Lakhs of miscellaneous scrap sold and DO expected shortly. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1992 | VISAKH WHITE OIL TERMINAL | To follow up with vendor for payment to enable release of DO . | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011314ACN-2026-03-4000125076 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125076 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125076 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125076 | AUD-2026-03-2000011314ACN-2026-03-4000125076 | 21 | 21 | 26 | 80 | 3 | 2 | 31 | 38
BUDAMPATI GOPALA KRISHNA | 2026-05-21 | Abhishek Singh | 2026-05-21 | MCC repair job completed | AUDIT UPLOAD IN SAP | 2026-03-11 20:00 | AUD-2026-03-2000011314 | 2026-03-11 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125077 | Closed | PULI JYOTSNA LATHA | 2026-05-21 | MCC building repairs under progresss. To be expedited | 6.1 |  | 1992 | VISAKH WHITE OIL TERMINAL | MCC building repairs to be completed as per target date | SOD | Marketing | SCR | 2026-04-15 | INADEQUATE SAFETY CULTURE | 5 | ASSET INTEGRITY | S1 | F5 | 2026-04-15 | AUD-2026-03-2000011314ACN-2026-03-4000125077 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011314ACN-2026-03-4000125077 | 2026-09-17 20:00 | 31.9205 | 262 | >20 | AUD-2026-03-2000011314 - ACN-2026-03-4000125077 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011314ACN-2026-03-4000125077 | AUD-2026-03-2000011314ACN-2026-03-4000125077 | 21 | 21 | 26 | 80 | 3 | 2 | 33 | 38
[5 empty] | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130273 | Open |  |  | CCTV footage checked & found okay . Location advised to have old depot CCTV footage and control room feed to new depot | 2.6 | CCTV functioning checked | 1528 | RAIPUR IRD-II | Same need to be carried out with CCTV vendor | SOD | Marketing | ECZ | 2026-09-30 |  | 6 |  | S3 | F2 | 2026-09-30 | AUD-2026-05-2000012405ACN-2026-05-4000130273 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130273 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130273 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-05-2000012405ACN-2026-05-4000130273 |  | AUD-2026-05-2000012405ACN-2026-05-4000130273 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000130274 | Open |  |  | VA system not yet activated at new depot | 2.7 | VA alerts checked / analysed | 1528 | RAIPUR IRD-II | to be followed up with DI team / HQO | SOD | Marketing | ECZ | 2026-09-30 |  | 3 |  | S3 | F1 | 2026-09-30 | AUD-2026-05-2000012405ACN-2026-05-4000130274 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130274 | 2026-08-28 18:00 | 52.0038 | 394 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130274 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012405ACN-2026-05-4000130274 |  | AUD-2026-05-2000012405ACN-2026-05-4000130274 | 21 |  | 27 | 80 | 3 | 3 | 57
[5 empty] | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130277 | Open |  |  | Several project material lying idle like valves , fittings , strainer , etc which was shifted from other locations by project team | 3.9 | Abnormal variations / unused assets reviewed | 1528 | RAIPUR IRD-II | Location advised to seggregate the material in usable and scrap items and take action | SOD | Marketing | ECZ | 2026-08-31 |  | 1 |  | S1 | F1 | 2026-08-31 | AUD-2026-05-2000012405ACN-2026-05-4000130277 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130277 | 2026-08-28 18:00 | 52.0038 | 364 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130277 | 532 | 8294 | 21 | 8294 | 49 | 50 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012405ACN-2026-05-4000130277 |  | AUD-2026-05-2000012405ACN-2026-05-4000130277 | 21 |  | 27 | 80 | 3 | 3 | 52
[5 empty] | SR MANAGEMENT AUDIT BY ECZ | 2026-04-30 17:00 | AUD-2026-05-2000012405 | 2026-04-29 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000130284 | Open |  |  | Lot of scrap material , particularly project items and old depot scrap to be identified | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1528 | RAIPUR IRD-II | RFD of all these material to be made | SOD | Marketing | ECZ | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012405ACN-2026-05-4000130284 | CG | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012405ACN-2026-05-4000130284 | 2026-08-28 18:00 | 52.0038 | 302 | >20 | AUD-2026-05-2000012405 - ACN-2026-05-4000130284 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012405ACN-2026-05-4000130284 |  | AUD-2026-05-2000012405ACN-2026-05-4000130284 | 21 |  | 27 | 80 | 3 | 3 | 44
NIDAMARTHI NAGA KIRAN | 2026-05-23 | SATYENDRA CHOURASIA | 2026-05-22 | Trainings as per OISD 154 arranged frequently. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123657 | Closed | SATYENDRA CHOURASIA | 2026-05-22 | Interacted with all officers at location. Their respective roles and responsibilities, performance, and expectations were discussed | 1.1 | Interaction with all officers (1–1.5 hrs) | 1919 | SECUNDERABAD TERMINAL | Officers to be thorough with all SOPs for all the operations / works at Terminal. | SOD | Marketing | SCR | 2026-01-27 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-01-27 | AUD-2026-03-2000011062ACN-2026-03-4000123657 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123657 | 2026-08-06 19:00 | 73.9622 | 264 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123657 | 532 | 8294 | 21 | 8294 | 265 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123657 | AUD-2026-03-2000011062ACN-2026-03-4000123657 | 21 | 21 | 26 | 80 | 1 | -12 | 22 | 38
NIDAMARTHI NAGA KIRAN | 2026-05-23 | SATYENDRA CHOURASIA | 2026-05-22 | Tank painting completed, DGCA Inspected and currently ATF service is being used. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123659 | Closed | SATYENDRA CHOURASIA | 2026-05-22 | Tank 2B conversion to ATF | 1.3 | Pending issues reviewed | 1919 | SECUNDERABAD TERMINAL | Tank Painting works to be completed and offer tank for DGCA inspection. | SOD | Marketing | SCR | 2026-02-28 | POOR PLANNING OR RISK ASSESSMENT | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011062ACN-2026-03-4000123659 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123659 | 2026-08-06 19:00 | 73.9622 | 264 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123659 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123659 | AUD-2026-03-2000011062ACN-2026-03-4000123659 | 21 | 21 | 26 | 80 | 1 | -12 | 26 | 38
NIDAMARTHI NAGA KIRAN | 2026-05-23 | SATYENDRA CHOURASIA | 2026-05-22 | All three CCTVs are functional. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123664 | Closed | SATYENDRA CHOURASIA | 2026-05-22 | Checked . 3 cameras are down. Location has identified the issues & necessary action is initiated . | 2.6 | CCTV functioning checked | 1919 | SECUNDERABAD TERMINAL | Location to ensure that 3 nos CCTV put back into service on priority basis. | SOD | Marketing | SCR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011062ACN-2026-03-4000123664 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123664 | 2026-08-06 19:00 | 73.9622 | 264 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123664 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123664 | AUD-2026-03-2000011062ACN-2026-03-4000123664 | 21 | 21 | 26 | 80 | 1 | -12 | 31 | 38
NIDAMARTHI NAGA KIRAN | 2026-05-23 | SATYENDRA CHOURASIA | 2026-05-22 | Successfully disposed of scrap and sludge worth Rs.45.6 lakhs, marking the terminal a scrap-free location. | AUDIT UPLOAD IN SAP | 2026-01-23 20:00 | AUD-2026-03-2000011062 | 2026-01-23 10:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123668 | Closed | SATYENDRA CHOURASIA | 2026-05-22 | Scrap was sold in auction. Delivery orders were issued to remove scrap. | 4.4 | Quality of PM compliance reviewed | 1919 | SECUNDERABAD TERMINAL | Location to coordinate and remove scrap at earliest | SOD | Marketing | SCR | 2026-03-31 | POOR PLANNING OR RISK ASSESSMENT | 5 | ENVIRONMENTAL | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011062ACN-2026-03-4000123668 | TS | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011062ACN-2026-03-4000123668 | 2026-08-06 19:00 | 73.9622 | 264 | >20 | AUD-2026-03-2000011062 - ACN-2026-03-4000123668 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011062ACN-2026-03-4000123668 | AUD-2026-03-2000011062ACN-2026-03-4000123668 | 21 | 21 | 26 | 80 | 1 | -12 | 31 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | Route corrections are regularly checked and done in coordination with sales officers. | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122285 | Closed | JOSVIN SUNNY | 2026-05-23 | All necessary targets with referecne to KPI and its associated works are clearly communicated to officer. Route corrections are allcompleted. Training to transporters planned on route violations , speed violations | 1.6 | Expectations clearly communicated to officers | 1892 | KOZHIKODE DEPOT | Route corrections to be regularly checked and done in coordination with sales officers. | SOD | Marketing | CZR | 2026-02-28 | FATIGUE AND STRESS | 6 | EMERGENCY | S2 | F3 | 2026-02-28 | AUD-2026-02-2000010911ACN-2026-03-4000122285 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122285 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122285 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-02-2000010911ACN-2026-03-4000122285 | AUD-2026-02-2000010911ACN-2026-03-4000122285 | 21 | 21 | 26 | 80 | 2 | -4 | 26 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | all recomendatiions are complied | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122286 | Closed | JOSVIN SUNNY | 2026-05-23 | All mock fire drills are single cotingency. Drills conducted in all ERDMP scenarios . Observation recorded and corrective actions taken. Safety committee conducted on 04-02-2026. 4 Recommendation were recorded . One pending to be complied. | 2.2 | Double contingency scenario simulated; observations recorded | 1892 | KOZHIKODE DEPOT | One pending point to be complied by 15-03-2026 | SOD | Marketing | CZR | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010911ACN-2026-03-4000122286 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122286 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122286 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122286 | AUD-2026-02-2000010911ACN-2026-03-4000122286 | 21 | 21 | 26 | 80 | 2 | -4 | 28 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | lighting improvement completed | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122287 | Closed | JOSVIN SUNNY | 2026-05-23 | LUX level improvement in progress near UG tank farm. Additional LEDs installation for HM Work in progress. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1892 | KOZHIKODE DEPOT | Lighting inporvement to be completed by 10.03.2026 | SOD | Marketing | CZR | 2026-03-10 | POOR PLANNING OR RISK ASSESSMENT | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-10 | AUD-2026-02-2000010911ACN-2026-03-4000122287 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122287 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122287 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122287 | AUD-2026-02-2000010911ACN-2026-03-4000122287 | 21 | 21 | 26 | 80 | 2 | -4 | 28 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | CCTV is functioning | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122288 | Closed | JOSVIN SUNNY | 2026-05-23 | 1 CCTV are not working | 2.6 | CCTV functioning checked | 1892 | KOZHIKODE DEPOT | To be rectified | SOD | Marketing | CZR | 2026-03-31 | THIRD PARTY ERRORS | 2 | OCCUPATIONAL HEALTH | S2 | F1 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122288 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122288 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122288 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122288 | AUD-2026-02-2000010911ACN-2026-03-4000122288 | 21 | 21 | 26 | 80 | 2 | -4 | 31 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | all VA alerts generated at location is closed with valid justification. | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122289 | Closed | JOSVIN SUNNY | 2026-05-23 | Observed that all VA alerts generated at location is closed with valid justification. | 2.7 | VA alerts checked / analysed | 1892 | KOZHIKODE DEPOT | XX | SOD | Marketing | CZR | 2026-03-31 | POOR COMMUNICATION | 2 | EMERGENCY | S2 | F1 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122289 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122289 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122289 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122289 | AUD-2026-02-2000010911ACN-2026-03-4000122289 | 21 | 21 | 26 | 80 | 2 | -4 | 31 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | HCD repaired and installed | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122290 | Closed | JOSVIN SUNNY | 2026-05-23 | Checked open patch HCD of TK-2 and point type HCD for Ethanol UG dyke, alarm triggered in Control room, main gate and local hooter also activated. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1892 | KOZHIKODE DEPOT | HCD at TK2 dyke is sent for rectification. | SOD | Marketing | CZR | 2026-03-31 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122290 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122290 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122290 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122290 | AUD-2026-02-2000010911ACN-2026-03-4000122290 | 21 | 21 | 26 | 80 | 2 | -4 | 31 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | metal sheet in the backside in place of galss window is ensured for all TT | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122291 | Closed | JOSVIN SUNNY | 2026-05-23 | Randomly two TTs checked for TT fittings as well as EM locking. Observed that Two TTs are having glass windows behind driver seat in cabin. | 3.1 | TT fittings & discipline checked | 1892 | KOZHIKODE DEPOT | Driver cabin shall have metal sheet in the backside in place of galss window. Location to ensure no tt with glass window is permitted for loading. | SOD | Marketing | CZR | 2026-03-15 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-15 | AUD-2026-02-2000010911ACN-2026-03-4000122291 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122291 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122291 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122291 | AUD-2026-02-2000010911ACN-2026-03-4000122291 | 21 | 21 | 26 | 80 | 2 | -4 | 28 | 38
HARINIVAS S | 2026-05-23 | JOSVIN SUNNY | 2026-05-23 | 1. full tank painting complete for tk1,2 2. greasing done for the bolts | 2. GREASING DONE FOR THE BOLTSOZHIKODE | 2026-02-27 | AUD-2026-02-2000010911 | 2026-02-27 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122293 | Closed | JOSVIN SUNNY | 2026-05-23 | Tank1 was found with many corrosion patches. Tank 2 also has developed corrosion after last monsoon. Bolts of TSV flanges and fire water line flanges found rusted. | 4.1 | Full Field round completed. | 1892 | KOZHIKODE DEPOT | 1. Patch painting and painting under side of wind girder to be carried out on TK-2. TK1 full painting to be done. 2. Location is advised to have grease application on TSV flange bolts and other rusted flanges. | SOD | Marketing | CZR | 2026-03-31 | POOR COMMUNICATION | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-03-31 | AUD-2026-02-2000010911ACN-2026-03-4000122293 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000010911ACN-2026-03-4000122293 | 2026-09-17 16:00 | 32.0872 | 264 | >20 | AUD-2026-02-2000010911 - ACN-2026-03-4000122293 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-02-2000010911ACN-2026-03-4000122293 | AUD-2026-02-2000010911ACN-2026-03-4000122293 | 21 | 21 | 26 | 80 | 2 | -4 | 31 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-19 | Corrective action will be taken after fund allocation (MEB/Capital). | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124904 | Closed | SINGH PREETI | 2026-05-19 | Yes discussed. Support required for fund allocation for MOV Actuator replacement under NPCB 2026-27. | 1.5 | HQO / Zonal support required identified | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-12-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 4 | PROCESS SAFETY | S2 | F2 | 2026-12-30 | AUD-2026-03-2000011223ACN-2026-03-4000124904 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124904 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124904 | 532 | 8294 | 21 | 8294 | -71 | 10 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124904 | AUD-2026-03-2000011223ACN-2026-03-4000124904 | 21 | 21 | 26 | 80 | 1 | 1 | 70 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-20 | File Note approval was taken by location for induction of 4 additional 12/14KL TTs. Accordingly, Local notification for induction of additional TTs was issued by the location to all existing successful transporters, against which 7 TTs were offered by 3 transporters. As per the methodology communicated for additional TT induction, local notification is required to be issued to all existing successful transporters and induction is to be carried out following the original tender ranking. However, the original tender ranking was finalized capacity schedule-wise. In the present case, the additional requirement pertains specifically to 12/14 KL TTs only. Out of the 3 transporters who offered TTs against the local notification, 2 transporters had not quoted for 12/14 KL TTs in the original tender and, therefore, do not appear in the original ranking for this capacity category. Accordingly, a detailed file note is being prepared seeking approval for induction of 4 TTs out of the 7 TTs offered, considering operational requirement and availability of eligible 12/14 KL TTs. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000124906 | Closed | SINGH PREETI | 2026-05-20 | The efficacy of present available transport TT fleet was discussed in detail and advised location for ensuring 100% indent execution at all times. At present location is facing occasional 12KL TT shortage as currently more dealers are pushing for 12 KL indents. Location has been advised to induct additional TTs as per tender terms and conditions by local notification. Draft local notificationhas been reviewed, corrected and finalized to release to transporters as per tender provisions. | 1.8 | Improvement plans discussed | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR PLANNING OR RISK ASSESSMENT | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011223ACN-2026-03-4000124906 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124906 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124906 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124906 | AUD-2026-03-2000011223ACN-2026-03-4000124906 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-21 | Breakdown issues have been attended, Close monitoring is ensured now and Routine cleaning is being done. Solar generation from Feb'26 onwards is ensured to be above 90% of design capacity. Daily solar generation units are updated in portal, and same is above 90%. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124911 | Closed | SINGH PREETI | 2026-05-21 | Solar generation for a period Apr’25 to Jan’26 was reviewed and observed that frequent inverter tripping was happened due to which generation on those days were affected. Location has been advised to ensure close monitoring of solar generation for generation as per design basis. | 4.2 | Maintenance activities reviewed | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 4 | ENVIRONMENTAL | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011223ACN-2026-03-4000124911 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124911 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124911 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124911 | AUD-2026-03-2000011223ACN-2026-03-4000124911 | 21 | 21 | 26 | 80 | 1 | 1 | 35 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-21 | Scraps disposed off and material uplifted vide Invoice Nos. 9020570513 and 9022178348. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000124912 | Closed | SINGH PREETI | 2026-05-21 | Yes done. 2 RFD proposals are under approval stage. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-03-2000011223ACN-2026-03-4000124912 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124912 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124912 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124912 | AUD-2026-03-2000011223ACN-2026-03-4000124912 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-19 | Against AOP Target of 0.00%, Location achieved +0.092% stock gain in SKO and +0.008% gain in Ethanol in FY 2025-26. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124913 | Closed | SINGH PREETI | 2026-05-19 | Location to ensure stock loss for SKO and Ethanol to be within AOP Targets | 6.1 | Stockloss | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000011223ACN-2026-03-4000124913 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124913 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124913 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124913 | AUD-2026-03-2000011223ACN-2026-03-4000124913 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-21 | All required materials have been kept in Emergency Trolley now. Photos attached. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124914 | Closed | SINGH PREETI | 2026-05-21 | It is observed that some of the required materials are not avaialble in trolley and kept in Admin building. | 6.1 | Emergency Trolley | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-03-30 | LACK OF OR UNCLEAR SAFETY PROCEDURES | 4 | EMERGENCY | S2 | F2 | 2026-03-30 | AUD-2026-03-2000011223ACN-2026-03-4000124914 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124914 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124914 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124914 | AUD-2026-03-2000011223ACN-2026-03-4000124914 | 21 | 21 | 26 | 80 | 1 | 1 | 30 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-21 | The new ethanol pump house is at 15m distance from existing 30 m high highmast. As per IEC 62305-3 Clause 5.2.2, Pump house lies within the protection zone of the existing 30 m high mast, and therefore a separate dedicated LPS is not required. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.4 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124916 | Closed | SINGH PREETI | 2026-05-21 | It is observed that LPS is not provided at New Ethanol Pump House. | 6.1 | LPS | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | NATURAL DISASTERS OR UNFORESEEN EVENTS | 4 | PROCESS SAFETY | S2 | F2 | 2026-06-30 | AUD-2026-03-2000011223ACN-2026-03-4000124916 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124916 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124916 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124916 | AUD-2026-03-2000011223ACN-2026-03-4000124916 | 21 | 21 | 26 | 80 | 1 | 1 | 44 | 38
SABLE RONAK MOHANKUMAR | 2026-05-23 | SINGH PREETI | 2026-05-21 | SCN issued to DCT Bahucharkrupa petroleum for Tampering of Locks. Further action will be taken as per ITDG. | SENIOR MANAGEMENT INSPECTION PALANPUR TE | 2026-03-11 | AUD-2026-03-2000011223 | 2026-03-10 | Confirmed | I1815 | PM - Senior Management Inspection | 6.3 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000124915 | Closed | SINGH PREETI | 2026-05-21 | Following TTs were checked using Intelligent key by GM-SOD, NWZ and details as below- 1. GJ01KT4931-Jainam Logistics-20 Top-HE13107-OK Bottom-HE31575-OK 2. GJ18BT8121-Shree Bhagwati Transport-20 Top-HE12173-Replaced Bottom-HE13013-OK 3. GJ03BZ3486-Shree Rajkhodal Transport-20 Top-HE13029-OK Bottom-HE12188-OK 4. GJ38TB0218-Bahucharkrupa Petroleum-20 Top-HE12166-Sent to sterna Bottom-HE34688-Sent to sterna | 6.1 | EM Lock verification using Inetlligent Key | 1385 | PALANPUR TERMINAL | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | INSUFFICIENT SUPERVISION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011223ACN-2026-03-4000124915 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011223ACN-2026-03-4000124915 | 2026-08-22 22:00 | 57.8372 | 264 | >20 | AUD-2026-03-2000011223 - ACN-2026-03-4000124915 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011223ACN-2026-03-4000124915 | AUD-2026-03-2000011223ACN-2026-03-4000124915 | 21 | 21 | 26 | 80 | 1 | 1 | 57 | 38
|  | DIWAKAR KAMLESH KUMAR | 2026-05-23 | 3 keys returned: key No 1.20145 -M/s: STP LIMITED Code: 41001050 as same has been returned to M/s STERNA SECURITY DEVICES PRIVATE LIMITED. key No 1.33685 -M/s: Adani Power Code: 41076634 as same has been returned to M/s STERNA SECURITY DEVICES PRIVATE LIMITED. Key No 1.20137-M/s. NTPC Limited Barh (41019769) as same has been returned to terminal. 3 sets abused locks (6 locks) -payment settled to sterna: AP05TD8188 HE23667,HE23668 AP05TD7425 HE23671,HE23672 AP05TB4667 HE23670,HE23669 4 setsdormant locks (8 locks) of TT being sent to while oil handed over to sterna: AP31TF6377 : Lock id:23811-23812 AP31TG8586 :Lock ID: 28606-23695 AP35Y3636 : Lock ID:29311,29312 AP39TK1314 :Lock iD: 26145,26146 Follow up is maintained with Sales for return of remaining dormant keys and locks.. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125550 | Completed | DIWAKAR KAMLESH KUMAR | 2026-05-23 | Dormant Keys and locks to be sent to M/S STERNA | 6.6 |  | 3708 | VISAKH NBOT | 32 dormant keys and 20 dormant locks to be sent to M/S STERNA | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125550 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125550 | 2026-09-18 17:30 | 31.0247 | 211 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125550 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-03-2000011315ACN-2026-03-4000125550 |  | AUD-2026-03-2000011315ACN-2026-03-4000125550 | 21 |  | 26 | 80 | 2 | 1 | 31
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-23 | DIWAKAR KAMLESH KUMAR | 2026-05-23 | Following up with sales for correction of routed 15 routes got corrected .TT crew members are educated on night driving in daily morning gate talk and transporters are also advised for zero night driving. Point 1 : 15 route corrections with old and new routeno taken from VTS portal: Old Route No New Route No Customer Name DS00076326 DS00076803 0041053972( JINDAL STEEL LIMITED ) DS00069035 DS00076755 0041017585( AMALGAM STEEL PRIVATE LIMITED ) DS00070475 DS00076757 0041070527( JINDAL STEEL & POWER ) DS00073357 DS00077084 0041015010( M/S NTPC LTD ) DS00075163 DS00072965 0041072031( TELANGANA STATE POWER GENERATION ) DS00076341 DS000767200041051761( CSPGCL ABVTPS, MARWA ) DS00058872 DS00076584 0041013060( THE ANDHRA SUGARS LIMITED ) DS00073478 DS00076578 0041004917( TELAGANA STATE POWER GENERATION- VI ) DS00074364 DS00076650 0041066766( JBO- DURGAPUR STEEL PLANT ) DS00073466 DS00076800 0041026545( SAMYU GLASS PRIVATE LIMITED ) DS00069492 DS00076768 0041051485( CSPGCL HTPS KORBA WEST ) DS00058672 DS00076816 0041035706( NUCLEAR FUEL COMPLEX ) DS00058993 DS00075189 0041007792( TELANGANA SUPER THERMAL POWER STATI ) DS00075858 DS00076702 0041051765( DB POWER LIMITED ) DS00075631 DS00076721 0041052421( M/S R.K.M. POWERGEN PVT LTD ) | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125082 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-23 | Improvement plans for transportation related issues discussed | 1.8 | Improvement plans discussed | 3708 | VISAKH NBOT | Route deviations and night driving to be minimized | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125082 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125082 | 2026-09-18 17:30 | 31.0247 | 264 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125082 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125082 | AUD-2026-03-2000011315ACN-2026-03-4000125082 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-04-01 | Soft Copy of health register available. Contract workers and TT crew are briefed on the test reports to ensure adequate follow up. Test report consolidated sheet attaached for reference | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.16 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125838 | Closed | Sreelal P P | 2026-04-01 | Checked during fit for road campaign. Medical checkup done for all TT crew once in 6 months. Last medical checkup done from 17 to 22 Nov 2025. Location also conducts external free eye check up campaign. Last conducted on 13.03.2026 | 2.16 | Eyesight / colour-blindness awareness checked | 1845 | IRUMPANAM TERMINAL | Location to maintain the health records in soft form for having better control and effective monitoring | SOD | Marketing | CZR | 2026-03-31 | FATIGUE AND STRESS | 6 | OCCUPATIONAL HEALTH | S2 | F3 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125838 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125838 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125838 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125838 | AUD-2026-03-2000011133ACN-2026-03-4000125838 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-04-01 | Regular grass cutting being done inside terminal premise. Grass cutting improved near TK26,ETP. Photos attached for reference. | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125840 | Closed | Sreelal P P | 2026-04-01 | Grass cutting to be done near TK26. Boundary wall maintenance to be carried out as discussed | 3.16 | Earth pits / boundary / vegetation control checked | 1845 | IRUMPANAM TERMINAL | Grass cutting to be done near TK26 | SOD | Marketing | CZR | 2026-03-31 | POOR EQUIPMENT MAINTENANCE | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125840 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125840 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125840 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125840 | AUD-2026-03-2000011133ACN-2026-03-4000125840 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-05-23 | Location has closed all pending MOC for which works has been completed | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.17 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125841 | Closed | Sreelal P P | 2026-05-23 | Open MOCs - 9. Out of 9, 4 are pertaining to manual locking of trucks for DS customers for a duration of 1 year. Work under progress for remaining 5 jobs | 3.17 | MOC status reviewed | 1845 | IRUMPANAM TERMINAL | Timely closure of MOCs to be done | SOD | Marketing | CZR | 2026-04-30 | INADEQUATE MANAGEMENT OF CHANGE (MOC) | 6 | PROCESS SAFETY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011133ACN-2026-03-4000125841 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125841 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125841 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125841 | AUD-2026-03-2000011133ACN-2026-03-4000125841 | 21 | 21 | 26 | 80 | 1 | -4 | 35 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-05-23 | Structural painting carried out for TK5 by M/s D1 ANTICORROSIVE COATINGS INDIA PRIVATE LIMITED VIDE PO No: 5300046169 | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125844 | Closed | Sreelal P P | 2026-05-23 | Full round taken with entire maintenance team. Operated dyke valve No:8 and HVLR 4. Visited ETP area. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1845 | IRUMPANAM TERMINAL | Structural painting to be carried out for TK-5 | SOD | Marketing | CZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011133ACN-2026-03-4000125844 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125844 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125844 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011133ACN-2026-03-4000125844 | AUD-2026-03-2000011133ACN-2026-03-4000125844 | 21 | 21 | 26 | 80 | 1 | -4 | 35 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-05-23 | Location has disposed off Misc.MS Scrap-10 MT vide RFD no.1006588 and 1006581 kept near pump house. | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125845 | Closed | Sreelal P P | 2026-05-23 | One lot of MS scrap is under auction with a due date of 16.03.2026. Location is optimistic that DO will be issued before 31.03.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1845 | IRUMPANAM TERMINAL | Location to co-ordinate with purchase for timely getting DO and try to dispose off scrap by 31.03.2026 | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 4 | ASSET INTEGRITY | S2 | F2 | 2026-03-31 | AUD-2026-03-2000011133ACN-2026-03-4000125845 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125845 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125845 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011133ACN-2026-03-4000125845 | AUD-2026-03-2000011133ACN-2026-03-4000125845 | 21 | 21 | 26 | 80 | 1 | -4 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Stock loss monitored & maintained within limits. nos NPCB projects completed and capitalised as per scheduled timelines. One pilot project of Automatic Bay Positioning has been rolled over to FY 2026-27. Project extension approval obtained for 3 months. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123577 | Closed | SALADI SRINIVASU | 2026-05-23 | Performance review done. Stock Loss in SKO , Bio diesel to be reduced. NPCB projects to be completed within time and no AR extension | 1.2 | Performance review conducted | 1979 | VIJAYAWADA TERMINAL | Close monitoring to be done and to ensure Stock loss to be within target. NPCB projects to be completed in time. | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123577 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123577 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123577 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123577 | AUD-2026-03-2000011121ACN-2026-03-4000123577 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | There were 2 open irregularies (IRR No 2025001165 & IRR No 6701) pertains to TT accidents. Both IIRs are closed. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123578 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Pending Issues reviewed. Open irregularities pertaining to TT accidents to be closed . | 1.3 | Pending issues reviewed | 1979 | VIJAYAWADA TERMINAL | Open irregularities pertaining to TT accidents to be closed . | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123578 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123578 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123578 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123578 | AUD-2026-03-2000011121ACN-2026-03-4000123578 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Noted. Location is strictly adopted the SOP procedures and implemented. Close monitoring of VTS is done and ITDG actions are initiated. For route deviations and speed violations. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123579 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, Nil pending indents, Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 1979 | VIJAYAWADA TERMINAL | SOPs to be followed for all opertaions , officers to take regular field rounds, VTS monitoring for nil route deviations and nil speed violations | SOD | Marketing | SCR | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123579 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123579 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123579 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123579 | AUD-2026-03-2000011121ACN-2026-03-4000123579 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Stock loss has been closely monitored and maintained within the limits. Daily safety talks and regular interactions with drivers and transporters has ensured to minimise the route deviations other than administrative orders. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123580 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Improvement plans for stock loss performance , transportation related issues discussed | 1.8 | Improvement plans discussed | 1979 | VIJAYAWADA TERMINAL | Stock loss of SKO, Bio Diesel to be closely monitored. Route deviations to be minimized | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123580 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123580 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123580 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123580 | AUD-2026-03-2000011121ACN-2026-03-4000123580 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Pipeline leakage of RSFPS has been rectified.Hooter made functional. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123587 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | HVLR/RSFPS/HCD/ESD functionality checked, . Leakage in pipe of RSFPS was observed | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1979 | VIJAYAWADA TERMINAL | Leakage in pipe of RSFPS to be rectified , hooter functioning to be rectified | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | ASSET INTEGRITY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123587 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123587 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123587 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123587 | AUD-2026-03-2000011121ACN-2026-03-4000123587 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | 1) Noted, small droplets from sprinkler header line has been rectified. 2) Noted and practice is done on continuous basis 3) Additional wind sock provided, which is visible rom TT Gantry. 4) Noted and practice is done to bring normalcy of the fire clock after the fire drill. 5) Noted, Megaphone is used on need basis as per site requirement. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123581 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Fire drill with double contingency scenario conducted on 26.02.2026. Fire drill report attached | 2.2 | Double contingency scenario simulated; observations recorded | 1979 | VIJAYAWADA TERMINAL | Areas of Improvement - 1) Sprinkler header line near Bay no 17 leaking profusely, to be rectfied. 2) Auxiliary team could not replenish Foam to the Fire combat team 3) Wind Sock not visible 4) Fire clock not made to normal after all clear given by Fire chief. 5)Megaphone not used by Fire chief. | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123581 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123581 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123581 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123581 | AUD-2026-03-2000011121ACN-2026-03-4000123581 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Foam Leakage from the flange joint of TK1B has been rectified by replacement of gasket. Missing items replenished in the fire emergency trolley replaced. Updated the list of items. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123583 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Emergency response preparedness checked during fire drill. DCP FE , HVLRs , Foam Monitors , MEFGs , Rim Seal Protection operated bylocation officers, Emergency Trolley checked, Emergency gate opened and checked | 2.5 | Emergency response preparedness reviewed | 1979 | VIJAYAWADA TERMINAL | RSFPS of TK1B , leakage of foam observed at flange joint to be rectified. Field hooter and control room hooter not functioned. Emergency Trolley some items are missing and some items not matching with name plate, to be rectified. | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123583 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123583 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123583 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123583 | AUD-2026-03-2000011121ACN-2026-03-4000123583 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | CBAC made functional. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123585 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | CBAC near TT gantry entrance not working , sent for repair | 2.8 | Access control systems checked | 1979 | VIJAYAWADA TERMINAL | CBAC to be rectified | SOD | Marketing | SCR | 2026-03-31 | HARSH WORKING CONDITIONS | 5 | ASSET INTEGRITY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123585 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123585 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123585 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123585 | AUD-2026-03-2000011121ACN-2026-03-4000123585 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Foam procured & available qty is 65KL. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123586 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Total Foam Available 58 KL against requirement of 65 KL . PO placed for 15 KL ARFFF foam | 2.9 | Foam inventory verified | 1979 | VIJAYAWADA TERMINAL | To follow up with vendor for receiving ARAFFF | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123586 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123586 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123586 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123586 | AUD-2026-03-2000011121ACN-2026-03-4000123586 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
AILAVARAPU VENKATA KRISHNA MURTY | 2026-05-23 | DIWAKAR KAMLESH KUMAR | 2026-05-23 | HHE35767 was checked by Sterna & programming key at location was found ok. HE23837 was checked remotely by Sterna at location & there was cap issued which was rectified and kept as spare. Rectification done remotely by sterna at the location. | AUDIT UPLOAD IN SAP | 2026-03-10 20:00 | AUD-2026-03-2000011315 | 2026-03-10 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125089 | Closed | DIWAKAR KAMLESH KUMAR | 2026-05-23 | EM Locks verfied for 5 nos TTs AP39UO 3767,AP39TK1224,AP31TF3659,AP39UE7699,AP39WC2257 . Two locks HE35767 and HE23837 sent for checking.. | 3.5 | EM Lock SOP compliance verified | 3708 | VISAKH NBOT | Two locks to be sent to M/S STERNA for checking | SOD | Marketing | SCR | 2026-03-31 | INSUFFICIENT SUPERVISION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011315ACN-2026-03-4000125089 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011315ACN-2026-03-4000125089 | 2026-09-18 17:30 | 31.0247 | 264 | >20 | AUD-2026-03-2000011315 - ACN-2026-03-4000125089 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011315ACN-2026-03-4000125089 | AUD-2026-03-2000011315ACN-2026-03-4000125089 | 21 | 21 | 26 | 80 | 2 | 1 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Noted & being carried out. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.10 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123590 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | TFMS/SAP reconciliation checked. Reco as per TFMS dips done , for quarter end manual dips reco done. | 3.10 | TFMS/SAP reconciliation checked | 1979 | VIJAYAWADA TERMINAL | Month end physical dips of tanks to be taken and reco to be carried out as per the physical manual dips for month end dates. | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123590 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123590 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123590 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123590 | AUD-2026-03-2000011121ACN-2026-03-4000123590 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Register for exceptions is maintained.It is being verified and signed by LIC at regular intervals. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123591 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Local Loading register checked. local loading done for prover checking , unloading of hazy product in UG tank and local loading forcompletion of the load. | 3.14 | Local loading checks (if applicable) | 1979 | VIJAYAWADA TERMINAL | Local Loading reasons to be mentioned clearly in the register and ensure montoring . | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123591 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123591 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123591 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123591 | AUD-2026-03-2000011121ACN-2026-03-4000123591 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
TILKAN RAVINDRA KUMAR | 2026-05-23 | Sreelal P P | 2026-05-23 | Monthly meetings being conducted with transporters/dealers. Last conducted in 02 May 2026. | SENIOR MANAGEMENT INSPN IRUMPANAM TML | 2026-03-14 18:00 | AUD-2026-03-2000011133 | 2026-03-14 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125843 | Closed | Sreelal P P | 2026-05-23 | Location has conducted transporter meeting on 09.03.2026 | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1845 | IRUMPANAM TERMINAL | Monthly meetings to be conducted with transporters, dealer | SOD | Marketing | CZR | 2026-04-30 | POOR COMMUNICATION | 6 | EMERGENCY | S2 | F3 | 2026-04-30 | AUD-2026-03-2000011133ACN-2026-03-4000125843 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011133ACN-2026-03-4000125843 | 2026-09-02 16:30 | 47.0663 | 264 | >20 | AUD-2026-03-2000011133 - ACN-2026-03-4000125843 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011133ACN-2026-03-4000125843 | AUD-2026-03-2000011133ACN-2026-03-4000125843 | 21 | 21 | 26 | 80 | 1 | -4 | 35 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Regular dip checks are being carried out to ensure no excess product filing. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123589 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Post Loading dip checks verified for TT nos AP39UL 4779, AP39UH5269 and found OK. For TT no AP39WJ3688 excess of 4 litres observed. | 3.2 | Post-loading dip checks verified | 1979 | VIJAYAWADA TERMINAL | Corrective action to be taken to ensure that no excess filling occurs at TT Gantry by taking with TAS vendor | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123589 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123589 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123589 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123589 | AUD-2026-03-2000011121ACN-2026-03-4000123589 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Calibration of PGs Completed | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123593 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Maintenance activities reviewed, Calibration of pressure guages falling due on 28.02.26 | 4.2 | Maintenance activities reviewed | 1979 | VIJAYAWADA TERMINAL | Calibration of Pressure guages to be completed | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123593 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123593 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123593 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123593 | AUD-2026-03-2000011121ACN-2026-03-4000123593 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | UPS commissioned | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123594 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | NPCB project for Supply and Installation of UPS is delayed. | 4.3 | Project progress reviewed | 1979 | VIJAYAWADA TERMINAL | To follow up with vendor for supply of UPS by 15.03.26 | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 4 | ASSET INTEGRITY | S1 | F4 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123594 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123594 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123594 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123594 | AUD-2026-03-2000011121ACN-2026-03-4000123594 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Achieved the completion of PM jobs by 100%. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123595 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | PM compliance reviewed , delay in closing of PM orders | 4.4 | Quality of PM compliance reviewed | 1979 | VIJAYAWADA TERMINAL | To ensure timely completion of PM Jobs and closing of PM orders | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000011121ACN-2026-03-4000123595 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123595 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123595 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123595 | AUD-2026-03-2000011121ACN-2026-03-4000123595 | 21 | 21 | 26 | 80 | 12 | 12 | 26 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Hooter is rectified and made functional. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 5.2 POST-VISIT REPORTING | ACN-2026-03-4000123596 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Functioning of Hooter for HCD , ESD checked and found OK. RSFPS hooter failed , to be rectified | 5.2 | Functioning of all Hooters in control room | 1979 | VIJAYAWADA TERMINAL | RSFPS hooter to be rectified | SOD | Marketing | SCR | 2026-03-10 | HARSH WORKING CONDITIONS | 8 | ASSET INTEGRITY | S2 | F4 | 2026-03-10 | AUD-2026-03-2000011121ACN-2026-03-4000123596 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123596 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123596 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011121ACN-2026-03-4000123596 | AUD-2026-03-2000011121ACN-2026-03-4000123596 | 21 | 21 | 26 | 80 | 12 | 12 | 28 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | DCP Fire extinguishers are serviced and records updated. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.2 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123598 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | DCP Fire extingushers servicing due since 20.02.2026 | 6.2 |  | 1979 | VIJAYAWADA TERMINAL | To be completed by 07.03.2026 | SOD | Marketing | SCR | 2026-03-07 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-07 | AUD-2026-03-2000011121ACN-2026-03-4000123598 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123598 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123598 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123598 | AUD-2026-03-2000011121ACN-2026-03-4000123598 | 21 | 21 | 26 | 80 | 12 | 12 | 27 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | LOTO register is maintained & updated. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123600 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | LOTO not done for capacitor panel 1 which is under maintenance. LOTO register not available at MCC room. | 6.5 |  | 1979 | VIJAYAWADA TERMINAL | LOTO register to be updated | SOD | Marketing | SCR | 2026-03-07 | COMPLACENCY OR RISK NORMALIZATION | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-07 | AUD-2026-03-2000011121ACN-2026-03-4000123600 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123600 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123600 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011121ACN-2026-03-4000123600 | AUD-2026-03-2000011121ACN-2026-03-4000123600 | 21 | 21 | 26 | 80 | 12 | 12 | 27 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Emergency gate lock key hooter is made functional | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123601 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Emergency exit gate lock key hooter not working | 6.7 |  | 1979 | VIJAYAWADA TERMINAL | To be rectified. | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | EMERGENCY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000011121ACN-2026-03-4000123601 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123601 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123601 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123601 | AUD-2026-03-2000011121ACN-2026-03-4000123601 | 21 | 21 | 26 | 80 | 12 | 12 | 31 | 38
SALADI SRINIVASU | 2026-05-23 | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Procurement of spill collection brooms is in progress. Fire proximity suit has been made available at security gte for ease of access. | AUDIT UPLOAD IN SAP | 2026-02-27 20:00 | AUD-2026-03-2000011121 | 2026-02-26 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.8 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000123602 | Closed | GANDRAPATI DAYANANDA REDDY | 2026-05-23 | Emergency Trolley items not as per the name plate , spill collection broom in torn condtion, fire proximity suit not available. | 6.8 |  | 1979 | VIJAYAWADA TERMINAL | To be rectified. | SOD | Marketing | SCR | 2026-03-07 | HARSH WORKING CONDITIONS | 5 | EMERGENCY | S1 | F5 | 2026-03-07 | AUD-2026-03-2000011121ACN-2026-03-4000123602 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011121ACN-2026-03-4000123602 | 2026-08-21 16:00 | 59.0872 | 264 | >20 | AUD-2026-03-2000011121 - ACN-2026-03-4000123602 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011121ACN-2026-03-4000123602 | AUD-2026-03-2000011121ACN-2026-03-4000123602 | 21 | 21 | 26 | 80 | 12 | 12 | 27 | 38
ALBY ABRAHAM ARACKAL | 2026-05-23 |  |  | Civil consulatant deployed for assessing the healthiness of boundary wall.It was observed that most of the sections are covered with vegetations. The walkway along the compound wall was made clear and vegetations removed. The damaged compound wall portions were rectified. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000125848 | Closed | ALBY ABRAHAM ARACKAL | 2026-05-23 | Location to deploy civil consultant to assist the compound wall condition and establish healhiness. Budget required for civil repairs to be assesed. | 1.5 | HQO / Zonal support required identified | 1833 | COCHIN BLACK TERMINAL | Budget requirement to be submitted | SOD | Marketing | CZR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125848 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125848 | 2026-09-08 16:00 | 41.0872 | 264 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125848 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125848 | AUD-2026-03-2000011134ACN-2026-03-4000125848 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 38
ALBY ABRAHAM ARACKAL | 2026-05-23 |  |  | all the non working cameras rectified. | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125851 | Closed | ALBY ABRAHAM ARACKAL | 2026-05-23 | 4 out of 37 CCTV are not working. Location to restore 4 non workding cameras by 31st March. All the CCTV having storage data for 90days. | 2.6 | CCTV functioning checked | 1833 | COCHIN BLACK TERMINAL | Non working cameras to be made functional and MOC to be intaited | SOD | Marketing | CZR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125851 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125851 | 2026-09-08 16:00 | 41.0872 | 264 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125851 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125851 | AUD-2026-03-2000011134ACN-2026-03-4000125851 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 38
ALBY ABRAHAM ARACKAL | 2026-05-23 | SRIJIN S | 2026-04-21 | All the workman are using all the mandatory PPE`S | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125857 | Closed | SRIJIN S | 2026-04-21 | House keeping is well maintained at terminal. . All the workman using all the required PPE`s. | 3.15 | Housekeeping & PPE usage checked | 1833 | COCHIN BLACK TERMINAL | Location to ensure PPEs for all workmen | SOD | Marketing | CZR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 6 | ENVIRONMENTAL | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125857 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125857 | 2026-09-08 16:00 | 41.0872 | 264 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125857 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125857 | AUD-2026-03-2000011134ACN-2026-03-4000125857 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 38
ALBY ABRAHAM ARACKAL | 2026-05-23 | SRIJIN S | 2026-04-21 | Grass cutting carried out wherever required | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000125858 | Closed | SRIJIN S | 2026-04-21 | Grass cutting to the southern side of tank farm needs attention | 3.16 | Earth pits / boundary / vegetation control checked | 1833 | COCHIN BLACK TERMINAL | Grass cutting to be done | SOD | Marketing | CZR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 6 | ENVIRONMENTAL | S3 | F2 | 2026-03-31 | AUD-2026-03-2000011134ACN-2026-03-4000125858 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125858 | 2026-09-08 16:00 | 41.0872 | 264 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125858 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125858 | AUD-2026-03-2000011134ACN-2026-03-4000125858 | 21 | 21 | 26 | 80 | 2 | 0 | 31 | 38
ALBY ABRAHAM ARACKAL | 2026-05-23 | SRIJIN S | 2026-04-21 | Greasing is being done on regular basis | SENIOR MANAGEMENT INSPN COCHIN BLACK OIL | 2026-03-16 18:00 | AUD-2026-03-2000011134 | 2026-03-16 09:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125862 | Closed | SRIJIN S | 2026-04-21 | Greasing of all nut bolts of flanges to be done on regular basis. | 4.4 | PM jobs are being done with the time line, where as the jobs are being done in the last week of month. | 1833 | COCHIN BLACK TERMINAL | Greasing to be done on regular basis | SOD | Marketing | CZR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 6 | ASSET INTEGRITY | S3 | F2 | 2026-04-30 | AUD-2026-03-2000011134ACN-2026-03-4000125862 | KL | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011134ACN-2026-03-4000125862 | 2026-09-08 16:00 | 41.0872 | 264 | >20 | AUD-2026-03-2000011134 - ACN-2026-03-4000125862 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011134ACN-2026-03-4000125862 | AUD-2026-03-2000011134ACN-2026-03-4000125862 | 21 | 21 | 26 | 80 | 2 | 0 | 35 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-21 | LT Supply from VDPL- Pannel received, Cables yet to received, execution completed. TAS Revamp Project tender floated. Ethanol TT Free exist work completed Fire Engine panel - work is in progress Pending Em locks keys work completed TT induction - work completed T4S audit completed | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123014 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-21 | Pending issues and compliances, Projects status, and the status of action points from the last BCM review | 1.3 | Pending issues reviewed | 1940 | KADAPA DEPOT | LT Supply from VDPL – Cabling works, TAS Revamp, Ethanol TT free exit & Fire engine panel replacement, Pending EM locks/ EM keys , TT induction, T4S Audit discussed | SOD | Marketing | SCR | 2026-03-10 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-10 | AUD-2026-03-2000010862ACN-2026-03-4000123014 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123014 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123014 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123014 | AUD-2026-03-2000010862ACN-2026-03-4000123014 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-21 | 12 No. fake keys assigned were deleted by sterna. Point complied | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123016 | Closed | PANDEY AKHIL | 2026-03-07 | 12 EM keys are identified as not available and they are assigned temporarily for opening of locks due to Key shortage. These Keys to be deleted. Quotation for TAS AMC to be obtained | 1.5 | HQO / Zonal support required identified | 1940 | KADAPA DEPOT | Zone to take up with Sterna for deletion of the 12 EM keys | SOD | Marketing | SCR | 2026-03-06 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-06 | AUD-2026-03-2000010862ACN-2026-03-4000123016 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123016 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123016 | 532 | 8294 | 21 | 8294 | 227 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123016 | AUD-2026-03-2000010862ACN-2026-03-4000123016 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Stock loss for the year within limits, OLA performance as per target,opex meeting as per target,dormant locks recovered and collected keys. vts mointoring and tt induction as per LOA | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000123017 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Areas requiring improvements were discussed with all the officers. | 1.8 | Improvement plans discussed | 1940 | KADAPA DEPOT | MS Stock Loss, OLA Performance, Opex, Dormant Locks and Keys, VTS Monitoring, TT induction | SOD | Marketing | SCR | 2026-03-31 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010862ACN-2026-03-4000123017 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123017 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123017 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123017 | AUD-2026-03-2000010862ACN-2026-03-4000123017 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | mock drill near Ethanol tank - scenario completed | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123018 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | All scenarios of ERDMP are to be covered. Fire in Ethanol tank area not covered | 2.1 | Fire drill conducted in last 6 months (surprise) | 1940 | KADAPA DEPOT | Complete the scenario for ethanol unloading | SOD | Marketing | SCR | 2026-03-31 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-31 | AUD-2026-03-2000010862ACN-2026-03-4000123018 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123018 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123018 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123018 | AUD-2026-03-2000010862ACN-2026-03-4000123018 | 21 | 21 | 26 | 80 | 0 | 0 | 31 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | regualr training are being given to all workmen about emergency procedures and on rescue operations | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123019 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Fire drill conducted with 2 scenarios. 1. Leak in MS wagon unloading pump 2. Fire in Ethanol tank 202B manifold area - Delay in rescue of Injured person near tank, No foam monitor is operated for ROSOV of tank only MEFG is operated | 2.2 | Double contingency scenario simulated; observations recorded | 1940 | KADAPA DEPOT | 1.Regular trainings to be conducted regarding clarity in communication during emergency scenarios 2.Training to be carried out on rescue operations | SOD | Marketing | SCR | 2026-03-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000010862ACN-2026-03-4000123019 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123019 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123019 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123019 | AUD-2026-03-2000010862ACN-2026-03-4000123019 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 38
DANTHAMALLA SATISH KUMAR | 2026-05-23 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | additional lighting arrangement provided wherever lux level not meeting | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123020 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Lux level checked in areas having less light, on roads and tank 201A dyke. Lux level on road is 15 and at tank 201A ROSOV area it is 11 | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1940 | KADAPA DEPOT | Lux level to be improved for 201A tank dyke. Non fuctioning FLP lights in the dyke area to be rectified | SOD | Marketing | SCR | 2026-03-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000010862ACN-2026-03-4000123020 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123020 | 2026-08-20 11:30 | 60.2747 | 264 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123020 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123020 | AUD-2026-03-2000010862ACN-2026-03-4000123020 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 38
|  | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | 3 KL AFFF Foam shifted from Rajahmundry Terminal | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126444 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | Total Foam Available 2 KL against requirement of 4.6 KL . | 2.9 | Foam inventory verified | 3693 | KAKINADA TML | 3 KL AFFF Foam to be shifted from Rajahmundry Terminal | SOD | Marketing | SCR | 2026-04-26 |  | 5 |  | S1 | F5 | 2026-04-26 | AUD-2026-04-2000011081ACN-2026-04-4000126444 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126444 | 2026-09-16 16:00 | 33.0872 | 237 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126444 | 532 | 8294 | 21 | 8294 | 176 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126444 |  | AUD-2026-04-2000011081ACN-2026-04-4000126444 | 21 |  | 26 | 80 | 0 | 0 | 34
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | Foam Monitor near Tank 3A has been checked, rectified and tested. | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000128224 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | Officers operated firefighting equipment themselves ( HVLR , Foam Monitor ,MEFG, Tank Sprinklers). Foam Monitor near Tank 3A throw not reaching the top of the tank | 2.12 | Officers operated firefighting equipment themselves (HVLR/Foammonitor/MEFG/Sprinklers etc.) | 1937 | SURYAPET TERMINAL | Foam Monitor near Tank 3A to be checked for proper throw. | SOD | Marketing | SCR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128224 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128224 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128224 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128224 | AUD-2026-04-2000011400ACN-2026-04-4000128224 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 38
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | All the earth pits are properly maintained. For this cycle after maintaining through salt and water, the earth pit resistance values were recorded to be lower and within the limits. | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128227 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | Two earth pits checked . E.P. no 211 (Additive shed) individual resistance is 0.49 Ohms and grid resistance is 0.01 ohms. E.P.no 221 (TT gantry structure) individual resistance is 1.09 Ohms and grid resistance is 0.95 ohms | 3.16 | Earth pits / boundary / vegetation control checked | 1937 | SURYAPET TERMINAL | For EP 221 maintenance to be done to ensure lower resistance values | SOD | Marketing | SCR | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128227 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128227 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128227 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128227 | AUD-2026-04-2000011400ACN-2026-04-4000128227 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 38
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | LIC is reviewing and signing on the MFM vs BCU totalisers sheet on a daily basis | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000128226 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | MFM VS BCU totalizer comparision checked on random basis, no abnormal variation. | 3.11 | MFM vs BCU totalizer comparison checked | 1937 | SURYAPET TERMINAL | LIC to review and sign on daily basis | SOD | Marketing | SCR | 2026-04-21 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-21 | AUD-2026-04-2000011400ACN-2026-04-4000128226 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128226 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128226 | 532 | 8294 | 21 | 8294 | 181 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128226 | AUD-2026-04-2000011400ACN-2026-04-4000128226 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 38
|  | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | All items placed in emergency trolley as per name plate and the keys are properly placed. | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 2.5 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-04-4000126441 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | Emergency response preparedness checked during fire drill. Foam Monitors operated by location officers, Emergency Trolley checked, Emergency Exit gate opened and checked | 2.5 | Emergency response preparedness reviewed | 3693 | KAKINADA TML | Emergency Trolley to be used in fire drills. Search Lights, manual siren removed from emergency trolley to be put back. All items to be placed in emergency trolley as per name plate and the keys to the cabinets to be placed properly to avoid time delays in emergency | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000126441 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126441 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126441 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126441 |  | AUD-2026-04-2000011081ACN-2026-04-4000126441 | 21 |  | 26 | 80 | 0 | 0 | 31
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | SOPs are strictly followed for all operations officers are taking regular field rounds Regular VTS monitoring is carried out to ensure nil route deviations and nil speed voilations CCTV monitoring is done on daily basis, it is recorded and sending report to zone on a daily basis | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128219 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | Expectations clearly communicated to officers regarding following of SOPs , Taking regular field rounds for safety in field activities, Nil pending indents, Close monitoring of VTS, No route deviations & Speed violations | 1.6 | Expectations clearly communicated to officers | 1937 | SURYAPET TERMINAL | SOPs to be followed for all opertaions , officers to take regular field rounds, VTS monitoring for nil route deviations and nil speed violations, CCTV monitoring on daily basis and records to be maintained | SOD | Marketing | SCR | 2026-04-21 | POOR EQUIPMENT MAINTENANCE | 4 | PROCESS SAFETY | S1 | F4 | 2026-04-21 | AUD-2026-04-2000011400ACN-2026-04-4000128219 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128219 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128219 | 532 | 8294 | 21 | 8294 | 181 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128219 | AUD-2026-04-2000011400ACN-2026-04-4000128219 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 38
|  | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | Dip tape replaced. | AUDIT UPLOAD IN SAP | 2026-03-24 16:30 | AUD-2026-04-2000011081 | 2026-03-24 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 3.7 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-04-4000126445 | Completed | PAMPANABOYINA SWARNA REKHA | 2026-05-23 | Tank TK 2 and Tank TK 4 Physical dip checked. TK 2 physical dip 572.6 cms(O+W) , water dip 12.3 cms tank temp 29.0 C and standard density 839.4. TK 4 Physical dip 538.2 cms(O+W) , water dip of 17.0 cms , tank temp. 30.0 and standard density 837.9 . Dips , temp , standard density are matching with guage book readings. | 3.7 | Inventory physical dip of minimum two tanks taken | 3693 | KAKINADA TML | Dip tape faded, to be replaced . | SOD | Marketing | SCR | 2026-03-31 |  | 5 |  | S1 | F5 | 2026-03-31 | AUD-2026-04-2000011081ACN-2026-04-4000126445 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-04-2000011081ACN-2026-04-4000126445 | 2026-09-16 16:00 | 33.0872 | 211 | >20 | AUD-2026-04-2000011081 - ACN-2026-04-4000126445 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW | AUD-2026-04-2000011081ACN-2026-04-4000126445 |  | AUD-2026-04-2000011081ACN-2026-04-4000126445 | 21 |  | 26 | 80 | 0 | 0 | 31
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | No bio-diesel stock loss reported | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.4 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128218 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | Pending issues and compliances, Projects status, and the status of action points from the last BCM review | 1.4 | Earlier action points status checked | 1937 | SURYAPET TERMINAL | Bio diesel stock loss to be monitored to ensure stock loss is within target. EM Locks & Keys to be retreived. | SOD | Marketing | SCR | 2026-04-30 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-30 | AUD-2026-04-2000011400ACN-2026-04-4000128218 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128218 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128218 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128218 | AUD-2026-04-2000011400ACN-2026-04-4000128218 | 21 | 21 | 27 | 80 | 0 | 0 | 35 | 38
CHOPPA SANTHOSH KUMAR | 2026-05-23 | DAMARAKONDA VARSHITHA | 2026-05-23 | Bottom loading project (AR no: 241809) has been closed, the Solar 400KW project (AR No: 242005) has been sent for closure to HQO commercial | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011400 | 2026-04-08 09:30 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-04-4000128216 | Closed | DAMARAKONDA VARSHITHA | 2026-05-23 | Performance review done. NPCB projects to be completed within time and no AR extension | 1.2 | Performance review conducted | 1937 | SURYAPET TERMINAL | 2 AR s i.e. Bottom loading bay conversion and 400 KW solar system to be closed by 31.03.26 and deleted by 20.04.26 | SOD | Marketing | SCR | 2026-04-21 | FAILURE TO FOLLOW PROCEDURES | 5 | PROCESS SAFETY | S1 | F5 | 2026-04-21 | AUD-2026-04-2000011400ACN-2026-04-4000128216 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011400ACN-2026-04-4000128216 | 2026-08-04 18:45 | 75.9726 | 264 | >20 | AUD-2026-04-2000011400 - ACN-2026-04-4000128216 | 532 | 8294 | 21 | 8294 | 181 | >90 | 2026-27 | 0 | 21 | LOW |  | AUD-2026-04-2000011400ACN-2026-04-4000128216 | AUD-2026-04-2000011400ACN-2026-04-4000128216 | 21 | 21 | 27 | 80 | 0 | 0 | 34 | 38
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-05-15 | AUD-2026-05-2000012507 | 2026-05-14 | Confirmed | I1815 | PM - Senior Management Inspection | 3.18 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000130677 | Open |  |  | OISD - 2, MDSA - 7 and SSA - 3, points are open. Comprehensive MDSA was carried out in August' 2025, wherein out of 51 points, 44 points are complied and 07 are still open. Targeted to complete it by August' 2026. | 3.18 | OISD/MDSA/SSA compliance reviewed | 1436 | SAGAR DEPOT | Location to expedite closure of all open Audit observation open points in time bound manner. | SOD | Marketing | CEN | 2026-12-31 |  | 1 |  | S1 | F1 | 2026-12-31 | AUD-2026-05-2000012507ACN-2026-05-4000130677 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012507ACN-2026-05-4000130677 | 2026-08-07 19:00 | 72.9622 | 486 | >20 | AUD-2026-05-2000012507 - ACN-2026-05-4000130677 | 532 | 8294 | 21 | 8294 | -72 | 10 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012507ACN-2026-05-4000130677 |  | AUD-2026-05-2000012507ACN-2026-05-4000130677 | 21 |  | 27 | 80 | 4 | 2 | 70
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Group meeting are being performed among officers and discussed for way forward | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.2 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122828 | Closed | ROY TAVARES | 2026-05-23 | Individual performace are reviewed and encouraged for their best performance area. Training requirements discussed | 1.2 | Performance review conducted | 1797 | GULBARGA NEW IRD | Route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-02-28 | INSUFFICIENT SUPERVISION | 4 | CONTRACTOR SAFETY | S2 | F2 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122828 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122828 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122828 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010764ACN-2026-03-4000122828 | AUD-2026-03-2000010764ACN-2026-03-4000122828 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Pending dues of railway have been cleared | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122829 | Closed | ROY TAVARES | 2026-05-23 | TT induction.Railway payment 53 lakhs pending. (total 93 l, paid 40 L, 53 lakhs more needed) | 1.3 | Pending issues reviewed | 1797 | GULBARGA NEW IRD | Coordinate with CPO | SOD | Marketing | SWZ | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 8 | ASSET INTEGRITY | S2 | F4 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122829 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122829 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122829 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122829 | AUD-2026-03-2000010764ACN-2026-03-4000122829 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Funds alloted for peding payement of Railways and same processed | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.5 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122830 | Closed | ROY TAVARES | 2026-05-23 | Railway payment to IOC pending, TT allotment of 35 TTs from CPO. | 1.5 | HQO / Zonal support required identified | 1797 | GULBARGA NEW IRD | Funds for railway payment, TT allotment from CPO. | SOD | Marketing | SWZ | 2026-02-28 | POOR COMMUNICATION | 8 | ASSET INTEGRITY | S2 | F4 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122830 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122830 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122830 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122830 | AUD-2026-03-2000010764ACN-2026-03-4000122830 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | DCT inducted as per LOIs pending non reporting data has been shared with RO for cancellation . Accident prone spots have been marked in VTS portal | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.6 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122831 | Closed | ROY TAVARES | 2026-05-23 | Induction of DCT LOIs pending, Route correction pending to be completed by 28.02.26, Accident spots review for relevance | 1.6 | Expectations clearly communicated to officers | 1797 | GULBARGA NEW IRD | DCT LOIs to be send for cancellation bt 20.2.26. Accident spot review and route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 6 | CONTRACTOR SAFETY | S3 | F2 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122831 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122831 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122831 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122831 | AUD-2026-03-2000010764ACN-2026-03-4000122831 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Training imparted to officers in line with OISD 154 and records maintained | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000122832 | Closed | ROY TAVARES | 2026-05-23 | Discussed trainings to be imparted to new officers | 1.8 | Improvement plans discussed | 1797 | GULBARGA NEW IRD | Records to be submitted by 28.2.26 to SWZ | SOD | Marketing | SWZ | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122832 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122832 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122832 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010764ACN-2026-03-4000122832 | AUD-2026-03-2000010764ACN-2026-03-4000122832 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | ERDMP scenarios TT gantry has been completed on 13.04.2026 | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122833 | Closed | ROY TAVARES | 2026-05-23 | Surprise Fire drill done 21/Aug, 2025 | 2.1 | Fire drill conducted in last 6 months (surprise) | 1797 | GULBARGA NEW IRD | Not done in Q3, Shall comply in Q4 | SOD | Marketing | SWZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122833 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122833 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122833 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122833 | AUD-2026-03-2000010764ACN-2026-03-4000122833 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | ERDMP scenario of TT gantry has been completed on 13.04.2026 | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122834 | Closed | ROY TAVARES | 2026-05-23 | Single contingency location | 2.2 | Double contingency scenario simulated; observations recorded | 1797 | GULBARGA NEW IRD | To be done in all ERDMP scenarios, Not done in TT gantry in 25-26. | SOD | Marketing | SWZ | 2026-03-15 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122834 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122834 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122834 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122834 | AUD-2026-03-2000010764ACN-2026-03-4000122834 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Route correction done asn requirement and onservations in Novex portal as of 28.02.2026 | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.3 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122839 | Closed | ROY TAVARES | 2026-05-23 | Carried out | 3.3 | VTS deviations reviewed | 1797 | GULBARGA NEW IRD | Route correction by 28.2.26 | SOD | Marketing | SWZ | 2026-02-28 | FAILURE TO FOLLOW PROCEDURES | 6 | CONTRACTOR SAFETY | S3 | F2 | 2026-02-28 | AUD-2026-03-2000010764ACN-2026-03-4000122839 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122839 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122839 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122839 | AUD-2026-03-2000010764ACN-2026-03-4000122839 | 21 | 21 | 26 | 80 | 5 | 5 | 26 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Housekeeping has been done near primary and secondary roads, UG tank farm surounding | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.15 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122840 | Closed | ROY TAVARES | 2026-05-23 | House keeping is good. | 3.15 | Housekeeping & PPE usage checked | 1797 | GULBARGA NEW IRD | Improvements near primary and secondary roads, UG tank farm surounding. | SOD | Marketing | SWZ | 2026-03-10 | FAILURE TO FOLLOW PROCEDURES | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-03-10 | AUD-2026-03-2000010764ACN-2026-03-4000122840 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122840 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122840 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010764ACN-2026-03-4000122840 | AUD-2026-03-2000010764ACN-2026-03-4000122840 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Schedule prepared for timely removal of vegatation around operating area | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000122841 | Closed | ROY TAVARES | 2026-05-23 | Good, still improvemnts required. | 3.16 | Earth pits / boundary / vegetation control checked | 1797 | GULBARGA NEW IRD | Vegetation is removed, still requires dedicated cleaning. | SOD | Marketing | SWZ | 2026-03-10 | FAILURE TO FOLLOW PROCEDURES | 5 | OCCUPATIONAL HEALTH | S1 | F5 | 2026-03-10 | AUD-2026-03-2000010764ACN-2026-03-4000122841 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122841 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122841 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010764ACN-2026-03-4000122841 | AUD-2026-03-2000010764ACN-2026-03-4000122841 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 38
CHANDRAKANTH JOSHI | 2026-05-23 | ROY TAVARES | 2026-05-23 | Pending scrap has been disposed as of 22.05.2026. New scrap shall be indentified and initatiated accordingly | SENIOR MANAGEMENT INSPECTION GULBARGA | 2026-02-18 | AUD-2026-03-2000010764 | 2026-02-18 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122844 | Closed | ROY TAVARES | 2026-05-23 | 9 numbers of RFDs has been sent for Accution on 09/02/2026. One RFD penfing for approval. | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1797 | GULBARGA NEW IRD | Close monitoring and compliance is required. | SOD | Marketing | SWZ | 2026-03-15 | LACK OF TRAINING OR COMPETENCY | 6 | OCCUPATIONAL HEALTH | S3 | F2 | 2026-03-15 | AUD-2026-03-2000010764ACN-2026-03-4000122844 | KA | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010764ACN-2026-03-4000122844 | 2026-08-19 18:00 | 61.0038 | 264 | >20 | AUD-2026-03-2000010764 - ACN-2026-03-4000122844 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010764ACN-2026-03-4000122844 | AUD-2026-03-2000010764ACN-2026-03-4000122844 | 21 | 21 | 26 | 80 | 5 | 5 | 28 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | All CCTVs are functional & uptime has been improved | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.6 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125725 | Closed | LAD SARTHAK DILIP | 2026-05-25 | 2 CCTV cameras are not working | 2.6 | CCTV functioning checked | 1504 | MIRAJ TERMINAL | All CCTV should be made functional and uptime to be improved. | SOD | Marketing | WZ | 2026-04-15 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010875ACN-2026-03-4000125725 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125725 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125725 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125725 | AUD-2026-03-2000010875ACN-2026-03-4000125725 | 21 | 21 | 26 | 80 | 0 | -1 | 33 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | Camera re-positioning done | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000125726 | Closed | LAD SARTHAK DILIP | 2026-05-25 | Continuous alerts are getting generated for bay number 7 and 8. | 2.7 | VA alerts checked / analysed | 1504 | MIRAJ TERMINAL | Camera repositioning required for bay number 7-8. | SOD | Marketing | WZ | 2026-04-15 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-04-15 | AUD-2026-03-2000010875ACN-2026-03-4000125726 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125726 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125726 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125726 | AUD-2026-03-2000010875ACN-2026-03-4000125726 | 21 | 21 | 26 | 80 | 0 | -1 | 33 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | Proper isolation has been provided | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125727 | Closed | LAD SARTHAK DILIP | 2026-05-25 | Earth strips are touching gantry structure at platform level | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1504 | MIRAJ TERMINAL | Isolation to be provided. | SOD | Marketing | WZ | 2026-04-25 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-04-25 | AUD-2026-03-2000010875ACN-2026-03-4000125727 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125727 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125727 | 532 | 8294 | 21 | 8294 | 177 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125727 | AUD-2026-03-2000010875ACN-2026-03-4000125727 | 21 | 21 | 26 | 80 | 0 | -1 | 34 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | PM jobs are completed before month end | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000125728 | Closed | LAD SARTHAK DILIP | 2026-05-25 | 55 % for current month | 4.4 | Quality of PM compliance reviewed | 1504 | MIRAJ TERMINAL | To be completed | SOD | Marketing | WZ | 2026-03-30 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-03-30 | AUD-2026-03-2000010875ACN-2026-03-4000125728 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125728 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125728 | 532 | 8294 | 21 | 8294 | 203 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125728 | AUD-2026-03-2000010875ACN-2026-03-4000125728 | 21 | 21 | 26 | 80 | 0 | -1 | 30 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | Needful action is taken | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.1 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125729 | Closed | LAD SARTHAK DILIP | 2026-05-25 | Sample Room consisted things not belonging to QC & sampling | 6.1 | QC Sample Room near TT gantry | 1504 | MIRAJ TERMINAL | Unwanted items to be kept & rempved from QC sample room | SOD | Marketing | WZ | 2026-03-25 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-03-25 | AUD-2026-03-2000010875ACN-2026-03-4000125729 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125729 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125729 | 532 | 8294 | 21 | 8294 | 208 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125729 | AUD-2026-03-2000010875ACN-2026-03-4000125729 | 21 | 21 | 26 | 80 | 0 | -1 | 30 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | Pathway has been cleared | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.5 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125733 | Closed | LAD SARTHAK DILIP | 2026-05-25 | Dry grass accumulated on the way to railway siding | 6.5 | Railway siding | 1504 | MIRAJ TERMINAL | Action to be taken to clear the pathway | SOD | Marketing | WZ | 2026-04-30 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000010875ACN-2026-03-4000125733 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125733 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125733 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125733 | AUD-2026-03-2000010875ACN-2026-03-4000125733 | 21 | 21 | 26 | 80 | 0 | -1 | 35 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | Declared as surplus | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.6 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125734 | Closed | LAD SARTHAK DILIP | 2026-05-25 | TW pumps are idle | 6.6 | Railway siding | 1504 | MIRAJ TERMINAL | Pumps located at TW to be declared as surplus | SOD | Marketing | WZ | 2026-03-31 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | EMERGENCY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000010875ACN-2026-03-4000125734 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125734 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125734 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125734 | AUD-2026-03-2000010875ACN-2026-03-4000125734 | 21 | 21 | 26 | 80 | 0 | -1 | 31 | 38
DEWADE SHAHAJI NAGORAO | 2026-05-25 | LAD SARTHAK DILIP | 2026-05-25 | drainage is cleaned & there is no blockage | ZONAL VISIT REPORT MIRAJ 17.03.2026 | 2026-03-17 | AUD-2026-03-2000010875 | 2026-03-17 | Confirmed | I1815 | PM - Senior Management Inspection | 6.7 ADDITIONAL OBSERVATIONS | ACN-2026-03-4000125735 | Closed | LAD SARTHAK DILIP | 2026-05-25 | VRU water drain sump is having garbage | 6.7 | VRU | 1504 | MIRAJ TERMINAL | to be cleaned frequently to avoid any blockage of drain water pumps | SOD | Marketing | WZ | 2026-03-28 | POOR EQUIPMENT MAINTENANCE | 1 | EMERGENCY | S1 | F1 | 2026-03-28 | AUD-2026-03-2000010875ACN-2026-03-4000125735 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010875ACN-2026-03-4000125735 | 2026-09-01 | 48.7538 | 266 | >20 | AUD-2026-03-2000010875 - ACN-2026-03-4000125735 | 532 | 8294 | 21 | 8294 | 205 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010875ACN-2026-03-4000125735 | AUD-2026-03-2000010875ACN-2026-03-4000125735 | 21 | 21 | 26 | 80 | 0 | -1 | 30 | 38
SUJEET KUMAR | 2026-05-26 | SAXENA UMESH CHANDRA | 2026-05-25 | Newly joined officers are being trained by senior officers. Senior Officers are monitoring their learnings, extending necessary guidance and support in all critical activities | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.1 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127173 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | Interected with newly joined officers and had a discussion about their training, current understanding of depot and future vision for organisation. | 1.1 | Interaction with all officers (1–1.5 hrs) | 1457 | INDORE DEPOT | Advised location to be alert and vigilant | SOD | Marketing | CEN | 2026-03-31 | INSUFFICIENT SUPERVISION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011235ACN-2026-03-4000127173 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127173 | 2026-09-09 19:00 | 39.9622 | 267 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127173 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127173 | AUD-2026-03-2000011235ACN-2026-03-4000127173 | 21 | 21 | 26 | 80 | 0 | -3 | 31 | 39
GIRI ANJANI KUMAR | 2026-05-27 | AGARWAL RAVI KUMAR | 2026-05-27 | Scrap has been disposed. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122724 | Closed | AGARWAL RAVI KUMAR | 2026-05-27 | Sr No Scrap Description Qty Unit Estimate Value Status 1 Misc Mild Steel Scrap like MS cut piece/sheet pieces, MS Pipe (1412/25-26/2) 4000 KG 1,00,000 MSTC Auction successfully completed. 2 UG Tank-16 (3X10.5 Mtr) (1412/25-26/4) 1 LS 60,000 MSTC Auction successfully completed. 3 Misc Steel Scrap such as Valve, MS Pipes, Foam Monitor, Hydrant (1412/25-26/6) 9700 KG 286760 MSTC Auction successfully completed. 4 Concertina Coil & Angle 2000 KG 60000 E-RFD initiated 5 Fire Extinguisher Disposal 26 EA 18,400 E-RFD being initiated 6 Top Loading Arms 1833.6 KG 70,500 E-RFD being initiated 7 Fire Engine with Pump 5 EA 1,75,000 E-RFD being initiated | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-06-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-06-30 | AUD-2026-03-2000011215ACN-2026-03-4000122724 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122724 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122724 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122724 | AUD-2026-03-2000011215ACN-2026-03-4000122724 | 21 | 21 | 26 | 80 | 2 | 2 | 44 | 39
GIRI ANJANI KUMAR | 2026-05-27 | AGARWAL RAVI KUMAR | 2026-05-27 | All the work has been completed. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 4.3 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000122723 | Closed | AGARWAL RAVI KUMAR | 2026-05-27 | • Project works concertina replacement near water tank was going one. Additionally tank comprehensive inspection of TK01, TK03 & TK04 were in progress. | 4.3 | Project progress reviewed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-09-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-09-30 | AUD-2026-03-2000011215ACN-2026-03-4000122723 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122723 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122723 | 532 | 8294 | 21 | 8294 | 19 | 20 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122723 | AUD-2026-03-2000011215ACN-2026-03-4000122723 | 21 | 21 | 26 | 80 | 2 | 2 | 57 | 39
GIRI ANJANI KUMAR | 2026-05-27 |  |  | Hooter has been replaced and now working fine. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.11 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122717 | Closed | AGARWAL RAVI KUMAR | 2026-05-27 | Dyke-3 Open Path HCD was tested using the 20% and 40% LEL testing kit and observed functionality along with indication in Control Room. Observed local hooter is not working. Advised location to rectify as early as possible. | 2.11 | HVLR/RSFPS/HCD/ESD functionality checked | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | ASSET INTEGRITY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122717 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122717 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122717 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122717 | AUD-2026-03-2000011215ACN-2026-03-4000122717 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 39
GIRI ANJANI KUMAR | 2026-05-27 | AGARWAL RAVI KUMAR | 2026-05-27 | ARAFFF Foam has been procured and replenished. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.9 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122716 | Closed | AGARWAL RAVI KUMAR | 2026-05-27 | Verification of FW availability (5400 KL) from TAS and observed availability of Fire Water is in line with OISD requirement (4940 KL). Availability of Foam (12.50 KL) was not in line with OISD requirement of 15.18 KL, for which Release Order already placed on supplier and expected to receive foam by 28.02.2026. Location has been advised to follow up with supplier. | 2.9 | Foam inventory verified | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 9 | PROCESS SAFETY | S3 | F3 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122716 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122716 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122716 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000011215ACN-2026-03-4000122716 | AUD-2026-03-2000011215ACN-2026-03-4000122716 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 39
GIRI ANJANI KUMAR | 2026-05-27 | AGARWAL RAVI KUMAR | 2026-05-27 | Training has been provided. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.4 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122714 | Closed | AGARWAL RAVI KUMAR | 2026-05-27 | Yes checked and observed that safety briefing to be further strengthend by imparting training | 2.4 | Security alertness checked (night-halt / surprise checks) | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 1 | ASSET INTEGRITY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122714 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122714 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122714 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122714 | AUD-2026-03-2000011215ACN-2026-03-4000122714 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 39
GIRI ANJANI KUMAR | 2026-05-27 |  |  | VA Alerts are fine tunned. | SR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011215 | 2026-02-12 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000122715 | Closed | GIRI ANJANI KUMAR | 2026-05-27 | Verified the CCTV/VA functioning and observed that frequent false alerts are being generated for unauthorized intrusion (due to security patrolling), wheel choke and Fire Extinguisher at TTG in system. Location has been advised to analyze the alerts and suitably take up with vendor for rectification. | 2.7 | VA alerts checked / analysed | 1412 | HAZIRA IRD (STP 1044) | Location to take corrective action | SOD | Marketing | NWR | 2026-04-30 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S2 | F2 | 2026-04-30 | AUD-2026-03-2000011215ACN-2026-03-4000122715 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011215ACN-2026-03-4000122715 | 2026-08-06 | 74.7538 | 268 | >20 | AUD-2026-03-2000011215 - ACN-2026-03-4000122715 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011215ACN-2026-03-4000122715 | AUD-2026-03-2000011215ACN-2026-03-4000122715 | 21 | 21 | 26 | 80 | 2 | 2 | 35 | 39
[5 empty] | PATNA Q1 AUDIT | 2026-05-22 19:00 | AUD-2026-05-2000012310 | 2026-05-21 11:00 | Confirmed | I1815 | PM - Senior Management Inspection | 6.39QUARTERLY INSPECTION | ACN-2026-05-4000131543 | Open |  |  | Point type HCD required before ETP currently available only at dykes. | 6.39 | Quarterly Inspection | 1723 | PATNA DEPOT | Location to ensure installing point type HCD before ETP | SOD | Marketing | PZR | 2026-06-30 | FAILURE TO FOLLOW PROCEDURES | 8 | PROCESS SAFETY | S2 | F4 | 2026-06-30 | AUD-2026-05-2000012310ACN-2026-05-4000131543 | BR | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012310ACN-2026-05-4000131543 | 2026-08-03 | 77.7538 | 302 | >20 | AUD-2026-05-2000012310 - ACN-2026-05-4000131543 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | MEDIUM | AUD-2026-05-2000012310ACN-2026-05-4000131543 |  | AUD-2026-05-2000012310ACN-2026-05-4000131543 | 21 |  | 27 | 80 | 0 | 0 | 44
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | SKO facility is ready and 5 wagons have been brought from Kanpur and unloaded in TK3 as per HQO advice following MP govt's circulardated 25.03.2026 for arrangement and storage of SKO for distribution as PDS SKO. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 1.3 ENGAGEMENT & COMMUNICATION | ACN-2026-03-4000127174 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | No such issues of location presented during visit. Checked the preparedness to handle PDS SKO in current allotment. | 1.3 | Pending issues reviewed | 1457 | INDORE DEPOT | Completion and making readiness of SKO facility | SOD | Marketing | CEN | 2026-03-31 | POOR COMMUNICATION | 1 | PROCESS SAFETY | S1 | F1 | 2026-03-31 | AUD-2026-03-2000011235ACN-2026-03-4000127174 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127174 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127174 | 532 | 8294 | 21 | 8294 | 202 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127174 | AUD-2026-03-2000011235ACN-2026-03-4000127174 | 21 | 21 | 26 | 80 | 0 | -3 | 31 | 39
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | All new officers have been imparted field training on operations of fire fighting equipment on 20.05.2026. All officers operated HVLRs, Foam Monitors, MEFG and Sprinklers etc. Additionally, New Officer Vishruti Shah is also attending live fire-fighting training at IFSDMS-Vadodara from 25th to 27th May 2026. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.12 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127178 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | Yes, equipments were operated by officers during drill. New officers to be imparted with more training to give them confidence for operating Firefighting equipments. | 2.12 | Officers operated firefighting equipment themselves (FE/monitor/MEFG etc.) | 1457 | INDORE DEPOT | New officers to be imparted with more training to give them confidence for operating Firefighting equipments. | SOD | Marketing | CEN | 2026-05-31 | LACK OF TRAINING OR COMPETENCY | 1 | EMERGENCY | S1 | F1 | 2026-05-31 | AUD-2026-03-2000011235ACN-2026-03-4000127178 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127178 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127178 | 532 | 8294 | 21 | 8294 | 141 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127178 | AUD-2026-03-2000011235ACN-2026-03-4000127178 | 21 | 21 | 26 | 80 | 0 | -3 | 39 | 39
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | One faulty bulb near ETP area has been replaced and few additional lights have been provided near Transformer area to meet lux levels as specified in OISD-244. Lux level near ETP area is now 210 against the recommended level of 60. Similarly, Lux level near Transformer yard is 180 vs the recommended lux levels of 100-150. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127176 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | Yes, checked lux level on 16.03.2026 and found satisafctory. However, Lux level in ETP and Transformer Area requires improvement. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1457 | INDORE DEPOT | Lux level in ETP and Transformer area needs to be improved | SOD | Marketing | CEN | 2026-04-15 | POOR EQUIPMENT MAINTENANCE | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-04-15 | AUD-2026-03-2000011235ACN-2026-03-4000127176 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127176 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127176 | 532 | 8294 | 21 | 8294 | 187 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127176 | AUD-2026-03-2000011235ACN-2026-03-4000127176 | 21 | 21 | 26 | 80 | 0 | -3 | 33 | 39
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | Vendor confirmed that the material has been dispatched on 24.05.2026. VA integration shall be completed by 30.06.2026 | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 2.7 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127177 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | VA is not yet implemented at location. Purchase order placed for VA installation, the material is expected by 1st week of April andtherafter, coordination to be done with DI team for integration of the same. | 2.7 | VA alerts checked / analysed | 1457 | INDORE DEPOT | Location to expedite receipt of material for commissioning of VA system | SOD | Marketing | CEN | 2026-06-30 | OUTDATED OR INCOMPATIBLE TECHNOLOGY | 1 | OCCUPATIONAL HEALTH | S1 | F1 | 2026-06-30 | AUD-2026-03-2000011235ACN-2026-03-4000127177 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127177 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127177 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127177 | AUD-2026-03-2000011235ACN-2026-03-4000127177 | 21 | 21 | 26 | 80 | 0 | -3 | 44 | 39
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | Transporters meet is done bi-monthly at the location. Last meet was conducted on 22.05.2026 wherein transporters issues like updation of tolls, correction of routes etc were noted and resolution was committed. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000127180 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | Yes, meeting is being done by location on bi-monthly basis with dealers/transporters. | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1457 | INDORE DEPOT | Location is advised to give more thrust on communication and resolving issues of transporter/dealers | SOD | Marketing | CEN | 2026-04-30 | POOR COMMUNICATION | 1 | CONTRACTOR SAFETY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011235ACN-2026-03-4000127180 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127180 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127180 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127180 | AUD-2026-03-2000011235ACN-2026-03-4000127180 | 21 | 21 | 26 | 80 | 0 | -3 | 35 | 39
SUJEET KUMAR | 2026-05-27 | SAXENA UMESH CHANDRA | 2026-05-25 | Both projects viz PCC beneath pipeline and Imperviousness of UG tank farm area have been completed. | LOCATION VISIT AT INDORE IRD | 2026-03-17 | AUD-2026-03-2000011235 | 2026-03-16 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000127181 | Closed | SAXENA UMESH CHANDRA | 2026-05-25 | Yes, reviewed ongoing project work and maintenance work. | 4.2 | Maintenance activities reviewed | 1457 | INDORE DEPOT | Location to expedite completion of PCC beneth pipeline and imperviousness of UG tank area work | SOD | Marketing | CEN | 2026-04-30 | DESIGN FLAWS OR IMPROPER INSTALLATIONS | 1 | ASSET INTEGRITY | S1 | F1 | 2026-04-30 | AUD-2026-03-2000011235ACN-2026-03-4000127181 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011235ACN-2026-03-4000127181 | 2026-09-09 19:00 | 39.9622 | 268 | >20 | AUD-2026-03-2000011235 - ACN-2026-03-4000127181 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000011235ACN-2026-03-4000127181 | AUD-2026-03-2000011235ACN-2026-03-4000127181 | 21 | 21 | 26 | 80 | 0 | -3 | 35 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Exit road direction after emergency gate reviewed along with zonal safety - clearance to be maintained to main connection road | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 2.8 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000123023 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Emergency gate operation checked & found ok. Approach road after emergency gate towards Main road to be checked as per OISD Standard | 2.8 | Access control systems checked | 1940 | KADAPA DEPOT | Exit road direction after emergency gate to be reviewed along with zonal safety | SOD | Marketing | SCR | 2026-03-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-20 | AUD-2026-03-2000010862ACN-2026-03-4000123023 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123023 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123023 | 532 | 8294 | 21 | 8294 | 213 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123023 | AUD-2026-03-2000010862ACN-2026-03-4000123023 | 21 | 21 | 26 | 80 | 0 | 0 | 29 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | surprise tt checks are being carried out as per target and all tts are being covered. | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.1 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123025 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | TTs AP39UG3129,AP30WB4239,AP39WA3349,AP39VE5515 and AP39WK7417 checked & found ok | 3.1 | TT fittings & discipline checked | 1940 | KADAPA DEPOT | Surprise TT checking to be carried out for those TT's which are getting shortages | SOD | Marketing | SCR | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000010862ACN-2026-03-4000123025 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123025 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123025 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123025 | AUD-2026-03-2000010862ACN-2026-03-4000123025 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | all bays reverification carried out and found satisfactory | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.2 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123026 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Dips of3 TT s checked. 1. AP39WB2379 (Bay -4, 1 compartment +0.5 cm), 2. AP39WL8936 (Bay 6 , Comp 1 - +0.2 cm, Comp 2 +0.3 cm) and 3. AP39UM4388 (bay 8, Comp 1 - +0.8 cm) | 3.2 | Post-loading dip checks verified | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-02-28 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000010862ACN-2026-03-4000123026 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123026 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123026 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123026 | AUD-2026-03-2000010862ACN-2026-03-4000123026 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | replaced 3 locks and send for tpi inspection | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123028 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | EM locks of 8 TTs are verified. 5 TTs EM locks found ok. 3 TTs EM locks couldn't be verified as the key was not going inside the locks. | 3.5 | EM Lock SOP compliance verified | 1940 | KADAPA DEPOT | Location to replace the locks of the 3 TTs and send them to TPI for checking the locks. | SOD | Marketing | SCR | 2026-03-07 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-07 | AUD-2026-03-2000010862ACN-2026-03-4000123028 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123028 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123028 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123028 | AUD-2026-03-2000010862ACN-2026-03-4000123028 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | surplus data shared with other locations | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.9 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123029 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Location has additional FE & Jockey pump than the requirement. Apart from that 2 FE(410 Kl/hr) of Guntakal IRD are available | 3.9 | Abnormal variations / unused assets reviewed | 1940 | KADAPA DEPOT | Details of surplus pumps of Guntakal and Jockey pump of Kadapa to be shared with all locations | SOD | Marketing | SCR | 2026-02-25 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123029 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123029 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123029 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123029 | AUD-2026-03-2000010862ACN-2026-03-4000123029 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | tender floated for tas revamp project | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.11 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123030 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Location does not have MFMs at gantry. On PD Meters are there | 3.11 | MFM vs BCU totalizer comparison checked | 1940 | KADAPA DEPOT | TAS Revamp of the location to happen wherein MFMs will be installed. Location to expedite the tender. | SOD | Marketing | SCR | 2026-03-10 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-03-10 | AUD-2026-03-2000010862ACN-2026-03-4000123030 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123030 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123030 | 532 | 8294 | 21 | 8294 | 223 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123030 | AUD-2026-03-2000010862ACN-2026-03-4000123030 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 39
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 1.8 ENGAGEMENT & COMMUNICATION | ACN-2026-05-4000131769 | Open |  |  | Location is advise to complete the induction of additional TTs to meet DS requirement. | 1.8 | Improvement plans discussed | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-30 |  | 1 |  | S1 | F1 | 2026-06-30 | AUD-2026-05-2000012564ACN-2026-05-4000131769 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131769 | 2026-08-06 | 74.7538 | 302 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131769 | 532 | 8294 | 21 | 8294 | 111 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131769 |  | AUD-2026-05-2000012564ACN-2026-05-4000131769 | 21 |  | 27 | 80 | 2 | 2 | 44
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.3 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131771 | Open |  |  | Checked at Fire engine shed and TT gantry and observed within requirement. Lux level not meeting at primary and secondary roads and installation of high mast tower is in progress. | 2.3 | Lux levels checked (gantry/roads/admin) during night-halt | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 |  | 1 |  | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131771 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131771 | 2026-08-06 | 74.7538 | 291 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131771 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131771 |  | AUD-2026-05-2000012564ACN-2026-05-4000131771 | 21 |  | 27 | 80 | 2 | 2 | 42
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 2.13 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-05-4000131775 | Open |  |  | As of now, Location has not identified trained personnel with HVD/HZA to move TT. | 2.13 | Trained personnel with HVD/HZA endorsement available (move TT 50–100m) | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-07 |  | 1 |  | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131775 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131775 | 2026-08-06 | 74.7538 | 279 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131775 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131775 |  | AUD-2026-05-2000012564ACN-2026-05-4000131775 | 21 |  | 27 | 80 | 2 | 2 | 40
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 3.5 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-05-4000131781 | Open |  |  | Yes reviewed | 3.5 | EM Lock SOP compliance verified | 1412 | HAZIRA IRD (STP 1044) | Location to ensure correction action in line with circular for verification within 15 days | SOD | Marketing | NWR | 2026-06-07 |  | 1 |  | S1 | F1 | 2026-06-07 | AUD-2026-05-2000012564ACN-2026-05-4000131781 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131781 | 2026-08-06 | 74.7538 | 279 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131781 | 532 | 8294 | 21 | 8294 | 134 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131781 |  | AUD-2026-05-2000012564ACN-2026-05-4000131781 | 21 |  | 27 | 80 | 2 | 2 | 40
[5 empty] | SR MANAGEMENT INSPECTION HAZIRA Q1 26-27 | 2026-05-14 | AUD-2026-05-2000012564 | 2026-05-13 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-05-4000131787 | Open |  |  | Full field visit of Tank farm area, pump house, Sample Room, Fire Engine shed etc, housekeeping and clearance of roads around tank farm is satisfactory. Following observations are made. 1. SOPs are faded in the field. 2. Isolation valve of monitor M3 was passing. 3. TK24 sprinkler valve found passing. 4. BS grade to be updated in P&I layout behind TT gantry. 5. Level gauges of foam drum of 200 Ltr were found not showing correct foam level in tank. 6. Small plant (Peepal) found growing in TK06 annular plate. 7. Fencing is not available to prevent access to license area post entry from visitor entry gate to admin building. Visitor can go to license area gate by crossing available arrangement. 8. Tank information written/printed over above ground tank surface has faded. | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1412 | HAZIRA IRD (STP 1044) | Correctiver action to be taken. | SOD | Marketing | NWR | 2026-06-19 |  | 1 |  | S1 | F1 | 2026-06-19 | AUD-2026-05-2000012564ACN-2026-05-4000131787 | GJ | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012564ACN-2026-05-4000131787 | 2026-08-06 | 74.7538 | 291 | >20 | AUD-2026-05-2000012564 - ACN-2026-05-4000131787 | 532 | 8294 | 21 | 8294 | 122 | >90 | 2026-27 | 0 | 21 | LOW | AUD-2026-05-2000012564ACN-2026-05-4000131787 |  | AUD-2026-05-2000012564ACN-2026-05-4000131787 | 21 |  | 27 | 80 | 2 | 2 | 42
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | clarification taken from ast and record maintained | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.13 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123032 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | BCU K-factor report checked | 3.13 | K-factor changes reviewed (if any) | 1940 | KADAPA DEPOT | Clarification sought from Location on change observed on 12/12/2025 | SOD | Marketing | SCR | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123032 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123032 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123032 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123032 | AUD-2026-03-2000010862ACN-2026-03-4000123032 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | local loading records maintained and checks are being maintained for local loading | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.14 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123033 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Local loading reports checked.Abnormal variation observed in bay no 6 HSD quantity for the period 01.01.2026 to 18.02.2026. | 3.14 | Local loading checks (if applicable) | 1940 | KADAPA DEPOT | Loaction to give clarification on high variation of HSD quantity | SOD | Marketing | SCR | 2026-02-25 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123033 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123033 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123033 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123033 | AUD-2026-03-2000010862ACN-2026-03-4000123033 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | all earth pits are being checked half yearly and records are being maintained | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.16 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123034 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Earth pit No(104 & 105) pertains TT gantry checked. Grid resistance is within limit whereas individual Earth resistance is more than 2 ohms | 3.16 | Earth pits / boundary / vegetation control checked | 1940 | KADAPA DEPOT | All Earth pits to be checked and reconditioned | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-28 | AUD-2026-03-2000010862ACN-2026-03-4000123034 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123034 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123034 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123034 | AUD-2026-03-2000010862ACN-2026-03-4000123034 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | toll issues resloved, speed governer certificate are being collected | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.20 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123036 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Meeting conducted with transporters | 3.20 | Meetings with transporters/dealers/OMCs/statutory authorities (where relevant) | 1940 | KADAPA DEPOT | Toll Issue to be resolved. Speed Governor settings to be corrected to 55 km/hr | SOD | Marketing | SCR | 2026-02-28 | COMPLACENCY OR RISK NORMALIZATION | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-28 | AUD-2026-03-2000010862ACN-2026-03-4000123036 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123036 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123036 | 532 | 8294 | 21 | 8294 | 233 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123036 | AUD-2026-03-2000010862ACN-2026-03-4000123036 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | hand gloves provied in etp substation | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.2 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123038 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Hand gloves to be made available and smoke detectors to be made functional at ETP control room. | 4.2 | Maintenance activities reviewed | 1940 | KADAPA DEPOT | Hand gloves to be kept at ETP control room | SOD | Marketing | SCR | 2026-02-25 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123038 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123038 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123038 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123038 | AUD-2026-03-2000010862ACN-2026-03-4000123038 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Strainer cleaning due date correctly updated on strainers of all pump strainers | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.4 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123040 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | Strainer cleaning due date to be correctly updated on strainers of all pump strainers | 4.4 | Quality of PM compliance reviewed | 1940 | KADAPA DEPOT | Location to take corrective action | SOD | Marketing | SCR | 2026-02-25 | LACK OF TRAINING OR COMPETENCY | 4 | PROCESS SAFETY | S1 | F4 | 2026-02-25 | AUD-2026-03-2000010862ACN-2026-03-4000123040 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123040 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123040 | 532 | 8294 | 21 | 8294 | 236 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123040 | AUD-2026-03-2000010862ACN-2026-03-4000123040 | 21 | 21 | 26 | 80 | 0 | 0 | 26 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | scrap disposed on 26.02.2026 | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.5 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123041 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-23 | MSTC auction completed for Miscellaneous scrap items and DO issued. Vendor upliftment by 07.03.2026 | 4.5 | Scrap disposal progress reviewed / scrap-free environment checked | 1940 | KADAPA DEPOT | Location to be made scrap free by 7.3.2026. Location to take up with Retail/ VDPL team to remove their scrap | SOD | Marketing | SCR | 2026-03-07 | LACK OF TRAINING OR COMPETENCY | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-07 | AUD-2026-03-2000010862ACN-2026-03-4000123041 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123041 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123041 | 532 | 8294 | 21 | 8294 | 226 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123041 | AUD-2026-03-2000010862ACN-2026-03-4000123041 | 21 | 21 | 26 | 80 | 0 | 0 | 27 | 39
CHIRUMAMILLA G V S R K PRASAD | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-28 | Location taken all level sample of tank & checked blending percentage of Ethanol content in Gasohol & found blended percentage as 15%. | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 3.4 OPERATIONAL & COMPLIANCE DISCIPLINE | ACN-2026-03-4000123027 | Closed | PANDEY AKHIL | 2026-03-07 | location is receiving gasohol by rake from vizag. Observed variation in blending percentage from top to bottom. | 3.4 | Ethanol blending performance / discipline reviewed (where applicable) | 1940 | KADAPA DEPOT | Location to ensure Tank to Tank circulation before being dispatched to Gantry to avoid uneven blending & also to take it up with supply location in case lesser blending percentage is detected | SOD | Marketing | SCR | 2026-02-20 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-02-20 | AUD-2026-03-2000010862ACN-2026-03-4000123027 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123027 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123027 | 532 | 8294 | 21 | 8294 | 241 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123027 | AUD-2026-03-2000010862ACN-2026-03-4000123027 | 21 | 21 | 26 | 80 | 0 | 0 | 25 | 39
DANTHAMALLA SATISH KUMAR | 2026-05-28 | CHIRUMAMILLA G V S R K PRASAD | 2026-05-28 | cross over platform provided | AUDIT UPLOAD IN SAP | 2026-02-19 14:00 | AUD-2026-03-2000010862 | 2026-02-18 13:00 | Confirmed | I1815 | PM - Senior Management Inspection | 4.1 INFRASTRUCTURE, PROJECT & M&I ASSESS | ACN-2026-03-4000123037 | Closed | CHIRUMAMILLA G V S R K PRASAD | 2026-05-28 | Fuill field round of Gantry, tank farm/pump house/siding/ETP/control room/security/admin was made | 4.1 | Full field round completed (gantry/tank farm/jetty/pump house/siding/control room/security/admin) | 1940 | KADAPA DEPOT | Tank 301A ROSOV cross over platform to be made.HCD of TW Pump house to be made operational | SOD | Marketing | SCR | 2026-03-15 | COMPLACENCY OR RISK NORMALIZATION | 5 | PROCESS SAFETY | S1 | F5 | 2026-03-15 | AUD-2026-03-2000010862ACN-2026-03-4000123037 | AP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010862ACN-2026-03-4000123037 | 2026-08-20 11:30 | 60.2747 | 269 | >20 | AUD-2026-03-2000010862 - ACN-2026-03-4000123037 | 532 | 8294 | 21 | 8294 | 218 | >90 | 2025-26 | 0 | 21 | LOW |  | AUD-2026-03-2000010862ACN-2026-03-4000123037 | AUD-2026-03-2000010862ACN-2026-03-4000123037 | 21 | 21 | 26 | 80 | 0 | 0 | 28 | 39
MAJUMDER BIRAJ | 2026-05-28 | BUDHI VEERAIAH | 2026-05-28 | i) LIC conducted surprise fire drill on 26-05-26 @ 19:48 Hrs at Tank Farm with the scenario of TANK 207 (HSD) inlet ROSOV leakage during Tanker discharge was in progress. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.1 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127098 | Closed | MAJUMDER BIRAJ | 2026-05-28 | There was no record of surprise fire drill by LIC in last 6 months | 2.1 | LIC conducted surprise mock drill in the tank farm with scenario of leakage at Tank 207 (HSD) ROSOV inlet nozzle during tanker discharge. | 1644 | KOLKATA-I TERMINAL | LIC to conduct surprise fire drill Location to cover all the scenario as per ERDMP during their fire drills. It is advised to have a calendar for fire drill so as to cover all the mentioned fire hazard/ fire scenario as per the ERDMP manual | SOD | Marketing | EZ | 2026-04-30 | INSUFFICIENT SUPERVISION | 10 | PROCESS SAFETY | S2 | F5 | 2026-05-30 | AUD-2026-03-2000010730ACN-2026-03-4000127098 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127098 | 2026-09-18 | 31.7538 | 269 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127098 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010730ACN-2026-03-4000127098 | AUD-2026-03-2000010730ACN-2026-03-4000127098 | 21 | 21 | 26 | 80 | 0 | -7 | 35 | 39
MAJUMDER BIRAJ | 2026-05-28 | BUDHI VEERAIAH | 2026-05-28 | Necessary training provided to all participants of the Fire drill and discussed on the gap analysis and shortcomings which are observed in earlier mock drills. Teams effectively participated in mock fire drill on 26-05-26 for the Leakage scenario at TK-207 ( HSD) ROSOV inlet nozzle. Proper communication established during Mock Drill.Fire Extinguisher was not operated as there was no Fire scenario and it was only leakage at the site.Boarding officer promptly responded to shore officer message to stop the pump and tanker discharge.ESD was operated .Tank farm Security guards carried VHF set with them while in patrolling and at Tank farm Entrance room. | LOCATION VISIT - EZ | 2026-03-19 | AUD-2026-03-2000010730 | 2026-03-18 | Confirmed | I1815 | PM - Senior Management Inspection | 2.2 SAFETY & EMERGENCY PREPAREDNESS | ACN-2026-03-4000127099 | Closed | MAJUMDER BIRAJ | 2026-05-28 | Scenario : Shore officer is in tank farm monitoring the tanker receipt in HSD tank no. TK208. 2 no. of SG were available in the tank farm. Leakage scenario from HSD tank inlett nozzle was simulated wherein tanker receipt was ongoing in off shift hours at 1800 hrs. of 18th Mar'26 and following are the observations : 1. lack of clear communication w.r.t scenerio 2. SG entered the Tank dyke 3. Fire Extingusger was operated 4. Boarding officer was not advised on the development to stop the pumping 5. ESD was not operated 6. Tank farm Security was not having VHF set with them 7. Mutual aid members were not contacted 8. DSO and LIC was contacted over phone 9. No Fire Siren and All clear siren were operated | 2.2 | Double contingency scenario simulated; observations recorded | 1644 | KOLKATA-I TERMINAL | All the observations/ shortcoming and recommendation of the drill to be implemented/ improved in the next drill. | SOD | Marketing | EZ | 2026-04-30 | LACK OF TRAINING OR COMPETENCY | 10 | EMERGENCY | S2 | F5 | 2026-05-30 | AUD-2026-03-2000010730ACN-2026-03-4000127099 | WB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010730ACN-2026-03-4000127099 | 2026-09-18 | 31.7538 | 269 | >20 | AUD-2026-03-2000010730 - ACN-2026-03-4000127099 | 532 | 8294 | 21 | 8294 | 172 | >90 | 2025-26 | 0 | 21 | MEDIUM |  | AUD-2026-03-2000010730ACN-2026-03-4000127099 | AUD-2026-03-2000010730ACN-2026-03-4000127099 | 21 | 21 | 26 | 80 | 0 | -7 | 35 | 39
[5 empty] | VISIT BY ZONAL O&D HEAD | 2026-01-13 | AUD-2026-03-2000011312 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 1528 | RAIPUR IRD-II |  | SOD | Marketing | ECZ | [7 empty] | AUD-2026-03-2000011312 | CG | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011312 | 2026-08-28 18:00 | 52.0038 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 3 | 3
[5 empty] | SENIOR MANAGEMENT INSPECTION HAZIRA IRD | 2026-02-13 | AUD-2026-03-2000011175 | 2026-02-12 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1412 | HAZIRA IRD (STP 1044) |  | SOD | Marketing | NWR | [7 empty] | AUD-2026-03-2000011175 | GJ | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000011175 | 2026-08-06 | 74.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 2 | 2
[5 empty] | DHARMAPURI VISIT REPORT UPLOADING SAP | 2026-03-13 15:30 | AUD-2026-03-2000010867 | 2026-03-12 13:30 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1999 | DHARAMAPURI TERMINAL |  | SOD | Marketing | SZ | [7 empty] | AUD-2026-03-2000010867 | TN | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010867 | 2026-09-11 | 38.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 2 | 2
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 | AUD-2026-08-2000016367 | 2026-08-06 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-08-2000016367 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016367 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 4 | 2
[5 empty] | VISIT BY ZONAL O&D HEAD AT JABALPUR IRD | 2026-02-20 | AUD-2026-03-2000010972 | 2026-02-19 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 1424 | JABALPUR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-03-2000010972 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010972 | 2026-09-26 17:30 | 23.0247 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 0 | 0
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016263 | 2026-08-06 10:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-08-2000016263 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016263 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 4 | 2
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000010976 | 2026-03-12 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1435 | GWALIOR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-03-2000010976 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010976 | 2026-08-22 19:00 | 57.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 2 | 2
[5 empty] | LOCATION VISIT-JALANDHAR IRD | 2026-01-31 | AUD-2026-03-2000010722 | 2026-01-28 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1254 | JALANDHAR DEPOT |  | SOD | Marketing | NFZ | [7 empty] | AUD-2026-03-2000010722 | PB | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010722 | 2026-08-21 | 59.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 0 | -21
[5 empty] | SENIOR MANAGEMENT AUDIT-VASHI BLACK OIL | 2026-02-17 19:00 | AUD-2026-02-2000011303 | 2026-02-17 09:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 3562 | VASHI BO TML |  | SOD | Marketing | WZ | [7 empty] | AUD-2026-02-2000011303 | MH | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-02-2000011303 | 2026-09-15 | 34.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 9 | 9
[5 empty] | LOCATION VISIT-HMEL BITUMEN TML_17.06.26 | 2026-06-17 | AUD-2026-07-2000015566 | 2026-06-17 | Being Created | I1800 | PM - Senior Management Inspection | [8 empty] | 3129 | BATHINDA BIT HMEL |  | SOD | Marketing | NFZ | [7 empty] | AUD-2026-07-2000015566 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015566 | 2026-09-29 17:00 | 20.0455 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | LOCATION VISIT AT GWALIOR IRD | 2026-03-13 | AUD-2026-03-2000010979 | 2026-03-12 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 1435 | GWALIOR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-03-2000010979 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010979 | 2026-08-22 19:00 | 57.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 2 | 2
[5 empty] | LOCATION VISIT-HMEL MKTG TML_16.06.26 | 2026-06-16 | AUD-2026-07-2000015565 | 2026-06-16 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 1187 | HMEL WHITE OIL TERMINAL |  | SOD | Marketing | NFZ | [7 empty] | AUD-2026-07-2000015565 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015565 | 2026-09-29 13:30 | 20.1913 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | AUDIT UPLOAD IN SAP | 2026-04-08 19:30 | AUD-2026-04-2000011323 | 2026-04-08 09:30 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1937 | SURYAPET TERMINAL |  | SOD | Marketing | SCR | [7 empty] | AUD-2026-04-2000011323 | TS | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-04-2000011323 | 2026-08-04 18:45 | 75.9726 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | MEERUT SR MANAGEMENT INSPECTION AUDIT | 2026-06-19 19:30 | AUD-2026-07-2000016217 | 2026-06-19 11:00 | Being Created | I1800 | PM - Senior Management Inspection | [8 empty] | 1146 | MEERUT DEPOT |  | SOD | Marketing | NUZ | [7 empty] | AUD-2026-07-2000016217 | UP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000016217 | 2026-09-25 19:00 | 23.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | Q2 BOKARO AUDIT SENIOR MANAGEMENT | 2026-09-19 | AUD-2026-09-2000017408 | 2026-09-18 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1742 | BOKARO DEPOT |  | SOD | Marketing | PZR | [7 empty] | AUD-2026-09-2000017408 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017408 | 2026-09-19 10:00 | 30.3372 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 1 | 1
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016268 | 2026-08-06 10:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-08-2000016268 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016268 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 4 | 2
[5 empty] | SR MANAGEMENT AUDIT SITARGANJ | 2026-05-20 15:00 | AUD-2026-08-2000016612 | 2026-05-19 10:30 | Being Created | I1800 | PM - Senior Management Inspection | [8 empty] | 1308 | SITARGANJ DEPOT |  | SOD | Marketing | NUZ | [7 empty] | AUD-2026-08-2000016612 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016612 | 2026-08-26 17:00 | 54.0455 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | LOCATION VISIT-HMEL BITUMEN TML_17.06.26 | 2026-06-18 | AUD-2026-07-2000015241 | 2026-06-17 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 3129 | BATHINDA BIT HMEL |  | SOD | Marketing | NFZ | [7 empty] | AUD-2026-07-2000015241 | [12 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-07-2000015241 | 2026-09-29 17:00 | 20.0455 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 0 | 0
[5 empty] | VISIT BY ZONAL O&D HEAD | 2026-01-13 | AUD-2026-03-2000010971 | 2026-01-12 | Confirmed | I1815 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-03-2000010971 | MP | [11 empty] | 2026 | 25-26 | 0 | Senior Management Inspection | AUD-2026-03-2000010971 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2025-26 | 0 | 21 | [6 empty] | 26 | 80 | 4 | 2
[5 empty] | SR MANAGEMENT INSPECTION-DIMAPUR | 2026-05-12 | AUD-2026-05-2000012302 | 2026-05-11 | Canceled | I1811 | PM - Senior Management Inspection | [8 empty] | 1708 | DIMAPUR DEPOT |  | SOD | Marketing | GZR | [7 empty] | AUD-2026-05-2000012302 | NL | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-05-2000012302 | 2026-09-12 | 37.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 7 | 7
[5 empty] | SENIOR MANAGEMENT AUDIT Q2 BOKARO | 2026-09-19 01:00 | AUD-2026-09-2000017505 | 2026-09-18 09:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1742 | BOKARO DEPOT |  | SOD | Marketing | PZR | [7 empty] | AUD-2026-09-2000017505 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017505 | 2026-09-19 10:00 | 30.3372 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 1 | 1
[5 empty] | SR MANAGEMENT AUDIT ROORKEE | 2026-05-16 14:00 | AUD-2026-08-2000016611 | 2026-05-15 11:45 | Being Created | I1800 | PM - Senior Management Inspection | [8 empty] | 1155 | ROORKEE DEPOT |  | SOD | Marketing | NUZ | [7 empty] | AUD-2026-08-2000016611 | UK | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016611 | 2026-09-03 | 46.7538 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 2 | 2
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016571 | 2026-08-06 10:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-08-2000016571 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016571 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 4 | 2
[5 empty] | LOCATION VISIT AT SAGAR IRD | 2026-08-07 19:00 | AUD-2026-08-2000016266 | 2026-08-06 10:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1436 | SAGAR DEPOT |  | SOD | Marketing | CEN | [7 empty] | AUD-2026-08-2000016266 | MP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016266 | 2026-08-07 19:00 | 72.9622 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 4 | 2
[5 empty] | Q2 BOKARO SENIOR MANAGEMENT INSPECTION | 2026-09-19 10:00 | AUD-2026-09-2000017409 | 2026-09-18 08:00 | Released | I1802 | PM - Senior Management Inspection | [8 empty] | 1742 | BOKARO DEPOT |  | SOD | Marketing | PZR | [7 empty] | AUD-2026-09-2000017409 | JH | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-09-2000017409 | 2026-09-19 10:00 | 30.3372 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 1 | 1
[5 empty] | SENIOR MANAGEMENT INSPECTION 26-27 Q1 | 2026-06-19 | AUD-2026-08-2000016625 | 2026-06-19 | Deletion Flag | I1810 | PM - Senior Management Inspection | [8 empty] | 1992 | VISAKH WHITE OIL TERMINAL |  | SOD | Marketing | SCR | [7 empty] | AUD-2026-08-2000016625 | AP | [11 empty] | 2026 | 26-27 | 0 | Senior Management Inspection | AUD-2026-08-2000016625 | 2026-09-17 20:00 | 31.9205 |  |  |  | 534 | 8294 |  |  |  |  | 2026-27 | 0 | 21 | [6 empty] | 27 | 80 | 3 | 2